## FIRE PUMP ROOM
Annexure I
P.O. No. 317047 Dt. 24.11.23
Scope of Supply & Erection :
Sr No | Description | Unit | Qty | Supply |  | Erection
|  |  |  | Rate | Amount | Rate | Amount
A. | FIRE PUMP ROOM
FIRE WATER PUMPING SYSTEM
1 | Supply, erection, testing & commissioning of Electrical Motor driven main pump, VERTICAL TURBINE type, capable of deliver 410 M3/HR at 105 MWC. The bowl assembly shall consist of suction bell, impellers, bowl shaft and column. Column depth shall be minimum 4.5 mtr. Pump shall be coupled with TEFC motor of suitable KW with speed of 1450 RPM with all accessories. The quoted rate shall include all fixing parts necessary to couple the pump with motor. Civil foundation like mounting base etc will be client's scope. (FOR HYDRANT SYSTEM) | Nos | R/O
2 | Supply, erection, testing & commissioning of Electrical Motor driven main pump, centrifugal horizontal type, with gland packing capable of deliver 410 M3/HR at 105 MWC. The pump shall be coupled with TEFC motor of suitable KW with speed of 1450 RPM with all accessories and complete set shall mounted on common base frame. The quoted rate shall include fixing of coupling, coupling guard and foudation bolts etc. Civil foundation will be client's scope.(FOR HYDRANT SYSTEM) | Nos | 1
3 | Supply, erection, testing & commissioning of Electrical Motor driven main pump, VERTICAL TURBINE type, capable of deliver 410 M3/HR at 105 MWC. The bowl assembly shall consists of suction bell, impellers, bowl shaft and column. Column depth shall be minimum 4.5 mtr. Pump shall be coupled with TEFC motor of suitable KW with speed of 1450 RPM with all accessories. The quoted rate shall include all fixing parts necessary to couple the pump with motor. Civil foundation like mounting base etc will be client's scope. (FOR SPRINKLER SYSTEM) | Nos | R/O
4 | Supply, erection, testing & commissioning of Electrical Motor driven main pump, centrifugal horizontal type, with gland packing capable of deliver 410 M3/HR at 105 MWC. The pump shall be coupled with TEFC motor of suitable KW with speed of 1450 RPM with all accessories and complete set shall mounted on common base frame. The quoted rate shall include fixing of coupling, coupling guard and foudation bolts etc. Civil foundation will be client's scope.(FOR SPRINKLER SYSTEM) | Nos | 1
5 | Supply, erection, testing & commissioning of diesel engine driven standby pump, VERTICAL TURBINE type, capable of deliver 410 M3/HR at 105 MWC. The bowl assembly shall consists of suction bell, impellers, bowl shaft and column. Column depth shall be minimum 4.5 mtr. Pump shall be coupled with diesel engine of suitable HP with speed of 1500 RPM with all accessories. The quoted rate shall include all fixing parts necessary to couple the pump with engine. Civil foundation like mounting base etc will be client's scope. | Nos | R/O
6 | Supply, erection,testing & commissioning of diesel engine driven stand by pump, centrifugal horizontal type with gland packing and capable of delivering 410 M3/HR at 105 MWC. The pump shall be coupled to suitable HP of Diesel Engine radiator water cooled type having speed of 1500 RPM with all accessories including diesel engine control panel and complete set shall be mounted on common base frame.Other accessories viz Batteries & battery leads with stand, fuel tank(for 4 hrs operation) with stand and gauge glass, fuel piping with valves etc to be supplied. The quoted rate shall include radiator water cooling piping(if required), coupling guard and other standard accessories, RCC foundation(as recommended by manufacturer) and foundation bolts, etc, complete ( civil foundation shall be client's scope). | Nos | 2
7 | Supply, erection, testing & commissioning of electric motor driven Jockey Pump,VERTICAL TURBINE type capable to deliver 25 M3/HR at 105 MWC. | Nos | R/O
8 | Supply, erection, testing & commissioning of electric motor driven Jockey Pump,centrifugal horizontal type capable to deliver 25 M3/HR at 105 MWC. The pump shall coupled to TEFC motor of suitable KW with speed of 2900 RPM with all accessories mounted on common base frame. | Nos | 2
9 | Supply, erection, testing & commissioning of compartmentalised common control panel for above pumps as per technical specification attached with this tender document. All components shall be housed in a common cubicals made of 16 swg. M.S. sheet with required stiffners(if required). The panel shall be powder coated of approved colour both inside and out side. The panel shall have both bottom and top cable entry provisions and panel shall be mounted on pedestal of 300mm height. | Nos | 1
10 | Supply, laying, testing & commissioning of FRLS, PVC outer sheath, steel armoured, aluminium / copper conductor, 1100 Volt Grade power cables with gland etc for above pumps. The cable shall be laid in tray / hume pipe / in trenches / on walls / floors etc as required. Cables laid out doors shall include the price of earth escavation providing brick and sand protection, refilling and compacting the earth. | Lot | 1
11 | GI earthing strips of 50mm x 6mm thick, strips shall run on floor / ceiling / walls, from pump to control panel with necessary accessories as required. | Mtr | 30
12 | 25 Sq.mm single core multistrand copper cable shall be run on floor / ceiling / walls, from the nearest earth bar to the pump control panel with necessary accessories as required. | Mtr | 40
13 | Supply and installation of pressure gauge, 1/2 inch bottom entry, of suitable range with ball valves and other accessories. | Nos | 8
14 | Supply and installation of Pressure switches, SPDT type, of suitable range for pump sets with ball valves and other accessories. | Nos | 8
15 | Supply and installation of double flanged vertical air vessel fabricated from M.S. Plate with dished ends (M.S. plate to be of required thickness to sustain the indicated test pressure), one standard pressure tight manhole, painted inside with bitumastic or anti-corrosive paint and outside with one coast of primer and two coats of synthetic enamel paint complete with approved quality of pressure switches, pressure gauge and all other required accessories to operate commonly main/sprinkler/diesel fire pump & jockey pump at drop of pressure, automatically at required pressure setting (Air vessel, pressure switch, pressure gauge, air release valve, piping and accessories to suit the pressure requirement of individual pressure zone) | Nos | 2
16 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600 with matching flanges complete with nuts & bolts. Pressure Class 150.
a | Size 300 mm NB | Nos | 1
b | Size 200 mm NB | Nos | 2
c | Size 250 mm NB | Nos | 4
d | Size 80 mm NB | Nos | 2
17 | Supply, installation, testing and commissioning of CS Non return valve as per BS 1868 with companion flanges,nuts & bolts and gaskets. Pressure Class 150.
a | Size 300 mm NB(Swing type) | Nos | 1
b | Size 250 mm NB(Swing type) | Nos | 4
c | Size 80 mm NB(Swing type) | Nos | 3
e | Size 50 mm NB(Swing type) | Nos | 6
18 | Supply, installation, testing and commissioning of Rubber bellow.
a | Size 80 mm NB | Nos | 2
b | Size 250 mm NB | Nos | 4
19 | Supply, Installation, testing & commissioning of CS Globe Valve as per IS:9338(PN16 rating) complete including matching flanges, nuts & bolts complete.
a | Size 150 mm NB | Nos | 4
b | Size 80 mm NB ( PRIMING LINE) | Nos | 1
c | Size 50 mm NB (PRIMING LINE) | Nos | 7
20 | Supply, installation of automatic 25 NB Air Release Valve | Nos | 2
21 | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor.
a | Size 150 mm NB | Nos | 2
22 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 & 7 mm Heavy grade conforming to IS : 3589 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope.
a | 350 mm NB x 7 mm thk | Mtr | 12
b | 300 mm NB x 7 mm thk | Mtr | 24
c | 250 mm NB x 7 mm thk | Mtr | 12
d | 200 mm NB x 7 mm thk | Mtr | 18
e | 150 mm NB | Mtr | 12
f | 100 mm NB | Mtr | 24
h | 80 mm NB | Mtr | 42
i | 50 mm NB | Mtr | 36
j | 25 mm NB | Mtr | 24
23 | Supply & installation of SS 4 way collecting head with 63 mm dia instantaneous type inlet 150 dia flanged outlet with built in check valve for fire brigade connection to fire reservoir (IS : 904). | Nos | 1
24 | Supply & installation of SS Fire Brigade Draw out connection with necessary foot valve (150NB) for reservoir. | Nos | 1
25 | Priming arrangement of 8000ltrs capacity for negative suction to be provided by the erection vendor including necessary tank and other structural support. Valves required are indicated elsewhere. | Nos | 1
26 | Supply,Installation, testing & commisssioning of CI Foot valve with Strainer
a | 100 mm NB | Nos | 2
b | 300 mm NB | Nos | 4
27 | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | Mtr | 400
Total

## EXTERNAL HYDRANT,SPRINKLER LINE
Annexure I
P.O. No. 317047 Dt. 24.11.23
Scope of Supply & Erection :
Sr No | Description | Unit | Qty | Supply |  | Erection
|  |  |  | Rate | Amount | Rate | Amount
B. | EXTERNAL HYDRANT, SPRINKLER LINE & FDA
1 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Loop cable) | Mtr | 1820
2 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Power cable) | Mtr | 1320
3 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 0.5 mm2 Armoured ( Telephone cable) | Mtr | 1200
4 | Supply, erection, fabrication, testing of MS black steel pipe of 7 mm Heavy grade conforming to IS : 3589 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipes shall be erected with grooved joints only. All sorts of escavation, pedestal support and structural support shall be of vendor's scope.
a | 200 NB(FOR REVAMPING OF HYDRANT LINE) | Mtr | 250
b | 200 NB(FOR EXTERNAL SPRINKLER LINE) | Mtr | 1040
5 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, Class 150, with matching flanges complete with nuts & bolts. (IN SPRINKLER LINE)
a | 200 mm NB | Nos | 3
6 | Supply, fabrication and erection of MS Structural material for various kind of supports consistes of angle, channels, I sections, plates etc including nuts, bolts and washers. | kg | 35000
7 | Supply, erection, testing & commissioning of analogue addressable outdoor type Manual Call point explosion proof complete with fittings and accessories. | Nos | 52
8 | Supply, erection, testing & commissioning of External Hooter cum strobe(IP 67 rating) complete with fittings and accessories. | Nos | 52
9 | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | Mtr | 1820
10 | Supply & installation of portable foam tank of 250 ltr. | Nos | R/O
11 | Supply & installation of FOAM WATER MONITOR 65NB water passage with 32nb Nozzle bore having 1750 lpm flow and 360 degree rotation with compaitable accessories. | Nos | R/O
12 | Supply, erection, testing & commissioning of Air Compressor with motor,mounted on a common base frame with air receiver tank. The set shall be fitted with dry suction filter, diaphragm,automatic venting device, safety valve, pressure gauge cooler, motor starter etc. The compressor shall be of capacity 25 M³/Hr( FAD), discharge pressure 10 bar, single stage, reciprocating type | Nos | 2
13 | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications
a | 50 NB | Mtr | 1800
B. | PA SYSTEM
1 | Main IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | Nos | 2
2 | High Efficiency SIREN with weather protection IP 21C (Weatherproof Type, Suitable for Outdoor Area), 3km range. | Nos | 2
3 | Supply, erection, testing & commissioning of 3 tone controller for high frequency siren. | Nos | 1
4 | Rack Mounted 125 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | Nos | 1
5 | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | Mtr | 2
6 | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | Nos | 2
7 | Paging Loudspeaker | Nos | 2
8 | Optical Fibre Cable (Armoured) with all accessories. | Nos | 1700
Total

## RESIN PLANT
Annexure I
P.O. No. 317047 Dt. 24.11.23
Scope of Supply & Erection :
Sr No | Description | Unit | Qty | Supply |  | Erection
|  |  |  | Rate | Amount | Rate | Amount
C | RESIN PLANT, RISHRA
C1 | HYDRANT SYSTEM
1 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Groove joints to be done for erection of pipes with proper couplings and fasteners. All escavations, pedestal supports, structural supports shall be of vendor's scope.
a | 150 mm NB | Mtr | 12
b | 80 mm NB | Mtr | 6
c | 25 mm NB | Mtr | 6
2 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, Class 150 with matching flanges, bolts, nuts and gaskets.
a | Size 150 mm NB | Nos | 1
3 | Supply, installation, testing and commissioning of CS Non return valve as per BS 1868, Class 150, with companion flanges,nuts & bolts and gaskets.
a | Size 150 mm NB | Nos | 1
4 | Supply & installation of SS oblique type single headed Landing valve with 80 mm inlet and 63 mm outlet SS instantaneous male coupling with rubber cap and chain conforming to IS : 5290 including matching flanges, gasket, nuts and bolts complete. | Nos | 3
5 | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor.
a | Size 80 mm NB | Nos | 3
6 | Supply & installation of SS branch pipe with 20 mm nozzle conforming to IS : 903 complete | Nos | 3
7 | Supply & installation of 63 mm dia rubberized reinforced rubber line hose pipe in 15 m length conforming to IS : 636 Type II ISI marked with gunmetal male and female instantaneous coupling conforming to IS 903 wounded with 18 SWG copper wire complete | Nos | 6
8 | Supply & installation of MS Hose Box of fabricated from 16 SWG CRCA sheet double door with lockable arrangements to accommodate 2 RRL hose of 15 m length and one branch pipe painted white inside and red outside with one key. (750X600X250 mm) | Nos | 3
9 | Supply & installation of swinging type hose reel drum fabricated from 14 SWG CRCA sheets painted with red colour stove paint 2 coats over 1 coat of primer with 30 m long 20 mm dia rubber hose pipe with with SS self closing shut – off nozzle of 5 mm outlet fixed on wall. | Nos | 3
10 | Supply and installation of pressure gauge, 1/2 inch bottom entry, of suitable range with ball valves and other accessories. | Nos | 1
11 | Supply, installation of automatic 25 NB Air Release Valve | Nos | 1
12 | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends
a | Size 25NB | Nos | 5
13 | Supply & installation of 250ltr portable foam tank filled with 3% ARFFF foam concentrate with foam making branch and pick up tube. | Nos | 1
C2 | FOAM WATER SPRAY SYSTEM
1 | Supply, erection , testing & commissioning of Deluge valve, with dry pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 2 way Solenoid Valve, and other accessories etc. & manual release unit.
a | 150 mm NB | Nos | 1
b | 80 mm NB | Nos | 2
2 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, Class 150 with matching flanges complete with nuts, bolts and gaskets.
a | 150 mm NB | Nos | 3
b | 80 mm NB | Nos | 6
3 | Supply, installation, testing and commissioning of Y-Strainer.
a | Size 150 mm NB | Nos | 1
b | Size 80 mm NB | Nos | 2
4 | Supply,installation,testing and commissioning of Foam Sprinkler nozzle with necessary threaded fittings as per drawing. The sprinkler shall be Open Aspiration, Pendent type, K-42 with standard spray angle.End connection 1/2" NPT/BSP.UL/FM Approved.
a | Spray nozzle K factor -42 | Nos | 123
5 | Supply,installation and commissioning of UL/FM approved Quartzoid Bulb Detector for K factor-80. Temp rating 68 deg C. | Nos | 123
6 | Supply, installation, testing and commissioning of Ratio Controller. | Nos
a | 150NB | Nos | 1
b | 80NB | Nos | 2
7 | Supply, installation, testing and commissioning of Foam bladder tank vertical type ,manufacturing as per ASME, section-VIII part- I. The bladder material shall be BUNA-N. The Bladder Tank shall be supplied along with all necessary valves, Hydraulically Operated Foam Concentrae Control Valve ,fittingss & instruments as per Technical data sheet attached with Tender documents.
a | Capacity of 2100 ltr. | Nos | 1
8 | Supply of AR-AFFF(3%) foam concentrate(PFOS/PFAS free) having sp. Gravity 1.0±.02 g/mlat 20⁰C , PH 7.0-8.5 & viscosity 1200 ±300 cps. | Ltr | 2100
9 | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications
a | 150 NB | Mtr | 32
b | 100 NB | Mtr | 16
c | 80 NB | Mtr | 92
d | 65 NB | Mtr | 36
e | 50 NB | Mtr | 46
f | 40NB | Mtr | 129
g | 25NB | Mtr | 952
10 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved red oxide primer and two coats of approved red enamel paint. Pipe joints shall be with grooved coupling. All escavation, pedestal supports, structural supports shall be of vendor's scope.
a | 150 mm NB | Mtr | 18
b | 100 mm NB | Mtr | 12
c | 80 mm NB | Mtr | 12
11 | Supply, erection, testing & commissioning of Air Buffer tank complete with necessary components. The compressor shall be of capacity 15 M³/Hr( FAD), discharge pressure 10 bar, single stage, reciprocating type. | Nos | 1
C3 | AUTOMATIC SPRINKLER SYSTEM
1 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved red oxide primer and two coats of approved red enamel paint. Pipe joints shall be with grooved couplings. All necessary supports shall be of vendor's scope.
a | 80 mm NB | Mtr | 18
b | 65 mm NB | Mtr | 6
c | 50 mm NB | Mtr | 6
d | 40 mm NB | Mtr | 6
e | 25 mm NB | Mtr | 65
2 | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor.
a | Size 80 mm NB | Nos | 1
b | Size 50 mm NB | Nos | 1
3 | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts confirming to API 594.
a | Size 80 mm NB | Nos | 1
b | Size 50 mm NB | Nos | 1
4 | Supply & fixing of Paddle type Flow Switch | Nos | 2
5 | Supply,Fixing of Sprinkler Head Pendent type for K factor-80. Temp rating 68 deg C.UL/FM Approved. | Nos | 37
6 | Supply, installation of automatic 25 NB Air Release Valve | Nos | 1
7 | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends
a | Size 25NB | Nos | 5
b | Size 40NB | Nos | 2
8 | Supply,Erection and testing of Installation Control Valve complete with trims & gong.
a | Size 80 mm NB | Nos | 1
9 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600 with matching flanges complete with nuts,bolts and gaskets.
a | Size 80 NB | Nos | 1
C4 | FDA SYSTEM
1 | Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | Nos | 9
2 | Supply, erection, testing & commissioning of analogue addressable Heat Detector | Nos | 2
3 | Supply, erection, testing & commissioning of IR Detector | Nos | 8
4 | Supply, erection, testing & commissioning of analogue addressable explosion proof Manual Call point | Nos | 6
5 | Supply, erection, testing & commissioning of explosion proo Hooter cum strobe | Nos | 10
6 | Supply, erction, testing & commissioning of analogue addressable Control Module | Nos | 8
7 | Supply, erection, testing & commissioning of analogue addressable Isolator Module | Nos | 3
8 | Supply, erection, testing & commissioning of analogue addressable Monitor module | Nos | 12
9 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Loop cable) | Mtr | 389
10 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Power cable) | Mtr | 297
11 | Supply, erection, fabrication, testing and commission of VOC detector with range of 1 – 1000 ppm isobutylene equivalent.and following accessoriesa) DigiPID internal dust filter (Pack of 5) b) Waterproof Filter Assy, RAEGuard2 PID, Pack of 5 c) DigiPID Teflon UV electrode shield pack of 10 d) DigiPID Dust Cover e) Air Drying Pre Filter Kit f) DigiPID external water trap filter (Pack of 5) | Nos | 11
12 | Supply, installation, testing and commissioning of aspiration detector with CMOS imager combined with multiple photodiode for reliable very early warning in a wide range of environments with minimal nuisance alarms. The detector should have 4 pipe inlet and min 100m pipelength support per inlet.The detector should have Smart on-board two stage filter retains dust count and remaining filter life for predictable maintenance& coverage area of min 2000 Sq.Mtr | Nos | 4
13 | Supply,Installation,Testing & Commissioning of UL/VDS listed CPVC Pipe 25 mm Dia & Pipe Accessories for the Aspiration detection. | Mtr | 304
14 | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | Mtr | 389
C5 | PA SYSTEM
1 | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | Nos | 1
2 | 6W Ceiling Mounted Speakers with excellent speech & (For False Ceiling Area). | Nos | 6
3 | 9 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | Nos | 2
4 | 15 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | Nos | 6
5 | Rack Mounted 200 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | Nos | 1
6 | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | Mtr | 260
7 | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | Nos | 1
8 | Paging Loudspeaker | Nos | 1
TOTAL

## SOLVENT PLANT
Annexure I
P.O. No. 317047 Dt. 24.11.23
Scope of Supply & Erection :
Sr No | Description | Unit | Qty | Supply |  | Erection
|  |  |  | Rate | Amount | Rate | Amount
D | SOLVENT PLANT
D1 | HYDRANT SYSTEM
1 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall of grooved with groove couplings. All escavations, pedestal supports, structural supports shall be of vendors scope.
a | 100 mm NB | Mtr | 166
b | 80 mm NB | Mtr | 56
c | 25 mm NB | Mtr | 12
2 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts.
a | Size 100 mm NB | Nos | 3
3 | Supply, installation, testing and commissioning of CS Non return valve as per BS 1868, Class 150 with companion flanges,nuts & bolts and gaskets.
a | Size 100 mm NB | Nos | 3
4 | Supply & installation of SS oblique type single headed Landing valve with 80 mm inlet and 63 mm outlet SS instantaneous male coupling with rubber cap and chain conforming to IS : 5290 including matching flanges, gasket, nuts and bolts complete. | Nos | 10
5 | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor.
a | Size 80 mm NB | Nos | 10
6 | Supply & installation of SS branch pipe with 20 mm nozzle conforming to IS : 903 complete | Nos | 10
7 | Supply & installation of 63 mm dia rubberized reinforced rubber line hose pipe in 15 m length conforming to IS : 636 Type II ISI marked with gunmetal male and female instantaneous coupling conforming to IS 903 wounded with 18 SWG copper wire complete | Nos | 20
8 | Supply & installation of MS Hose Box of fabricated from 16 SWG CRCA sheet double door with lockable arrangements to accommodate 2 RRL hose of 15 m length and one branch pipe painted white inside and red outside with one key. (750X600X250 mm) | Nos | 10
9 | Supply & installation of swinging type hose reel drum fabricated from 14 SWG CRCA sheets painted with red colour stove paint 2 coats over 1 coat of primer with 30 m long 20 mm dia rubber hose pipe with with SS self closing shut – off nozzle of 5 mm outlet fixed on wall. | Nos | 10
10 | Supply and installation of pressure gauge, 1/2 inch bottom entry, of suitable range with ball valves and other accessories. | Nos | 1
11 | Supply, installation of automatic 25 NB Air Release Valve | Nos | 3
12 | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends
a | Size 25NB | Nos | 16
13 | Supply & installation of 250ltr foam tank filled with 3% ARFFF foam concentrate with foam making branch and pick up tube. | Nos | 2
D2 | FOAM WATER SPRAY SYSTEM
1 | Supply, erection , testing & commissioning of Deluge valve with dry pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 2 way Solenoid Valve, etc. & manual release unit.
a | 150 mm NB | Nos | 5
b | 100 mm NB | Nos | 5
2 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, Class 150 with matching flanges complete with nuts & bolts.
a | 150 mm NB | Nos | 15
b | 100 mm NB | Nos | 15
3 | Supply, installation, testing and commissioning of Y-Strainer.
a | 150 mm NB | Nos | 5
b | 100 mm NB | Nos | 5
4 | Supply,installation,testing and commissioning of Foam Sprinkler nozzle with necessary threaded fittings as per drawing. The sprinkler shall be Open Aspiration, Pendent type, K-42 with standard spray angle.End connection 1/2" NPT/BSP.UL/FM Approved.
a | Spray nozzle K factor -42 | Nos | 517
5 | Supply,installation and commissioning of UL/FM approved Quartzoid Bulb Detector for K factor-80. Temp rating 68 deg C. | Nos | 517
6 | Supply, installation, testing and commissioning of Ratio Controller. | Nos
a | 150 mm NB | Nos | 5
b | 100 mm NB | Nos | 5
7 | Supply, installation, testing and commissioning of Foam bladder tank vertical type ,manufacturing as per ASME, section-VIII part- I. The bladder material shall be BUNA-N. The Bladder Tank shall be supplied along with all necessary valves, Hydraulically Operated Foam Concentrae Control Valve ,fittingss & instruments as per Technical data sheet attached with Tender documents.
a | Capacity of 1700 ltr. | Nos | 7
8 | Supply of AR-AFFF(3%) foam concentrate(PFOS/PFAS free) having sp. Gravity 1.0±.02 g/mlat 20⁰C , PH 7.0-8.5 & viscosity 1200 ±300 cps. | Ltr | 11900
9 | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee, reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications
a | 150 NB | Mtr | 371
b | 100 NB | Mtr | 280
c | 80 NB | Mtr | 182
d | 65 NB | Mtr | 227
e | 50 NB | Mtr | 120
f | 40NB | Mtr | 454
g | 25NB | Mtr | 2043
10 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall of grooved with groove couplings. All escavations, pedestal supports, structural supports shall be of vendor's scope.
a | 150 mm NB | Mtr | 46
b | 100 mm NB | Mtr | 75
11 | Supply, erection, testing & commissioning of Air Buffer tank complete with necessary components. The compressor shall be of capacity 15 M³/Hr( FAD), discharge pressure 10 bar, single stage, reciprocating type. | Nos | 1
D3 | WATER CURTAIN
1 | Supply, erection and testing of heavy grade(class-C) pipes conforming to IS-1239 including all fittings viz. tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer and structural steels for pipe supports. Hanger support with anchor fasteners and clamps shall be supplied to fix the pipes on ceiling wall etc. including supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners) as per specification. Cutting of floors, walls etc and making it good after erection of pipes shall be of vendor's scope. Necessary painting with 2 coats of primer and 2 coats of synthetic enamel paints to be done and supply of paints shall be with vendor's scope.
a | 50 NB | Mtr | 106
b | 65 NB | Mtr | 126
c | 80 NB | Mtr | 120
d | 100 NB | Mtr | 66
2 | Supply, erection , testing & commissioning of Deluge valve with wet pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 2 way Solenoid Valve, air filter regulator etc. & manual release unit.
a | Size 80 NB | Nos | 3
b | Size 100 NB | Nos | 5
3 | Providing & fixing Cast Iron Y Strainer.
a | Size 80 NB | Nos | 3
b | Size 100 NB | Nos | 5
4 | Supply & fixing of SS Water Curtain Nozzle with (K>=71). UL/FM Approved. | Nos | 119
5 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, Class 150 with matching flanges complete with nuts & bolts.
a | Size 80 NB | Nos | 9
b | Size 100 NB | Nos | 15
D4 | AUTOMATIC SPRINKLER SYSTEM
1 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be with grooved couplings. Necesary supports of all kind shall be of vendor's scope.
a | 80 mm NB | Mtr | 18
b | 65 mm NB | Mtr | 12
c | 50 mm NB | Mtr | 12
d | 40 mm NB | Mtr | 18
e | 25 mm NB | Mtr | 36
2 | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor.
a | Size 65 mm NB | Nos | 2
3 | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts.
a | Size 65 mm NB | Nos | 1
4 | Supply & fixing of Paddle type Flow Switch | Nos | 1
5 | Supply,Fixing of Sprinkler Head Pendent type for K factor-80. Temp rating 68 deg C. UL/FM Approved. | Nos | 16
6 | Supply, installation of automatic 25 NB Air Release Valve | Nos | 1
7 | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends
a | Size 25NB | Nos | 2
b | Size 40NB | Nos | 1
8 | Supply,Erection and testing of Installation Control Valve complete with trims & gong.
a | Size 80 mm NB | Nos | 1
9 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, Class 150 with matching flanges complete with nuts & bolts.
a | Size 80 NB | Nos | 1
D5 | FDA SYSTEM
1 | Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | Nos | 12
2 | Supply, erection, testing & commissioning of IR Detector | Nos | 15
3 | Supply, erection, testing & commissioning of analogue addressable explosion proof Manual Call point | Nos | 12
4 | Supply, erection, testing & commissioning of explosion proof Hooter | Nos | 12
5 | Supply, erction, testing & commissioning of analogue addressable Control Module | Nos | 26
6 | Supply, erection, testing & commissioning of analogue addressable Isolator Module | Nos | 4
7 | Supply, erection, testing & commissioning of analogue addressable Monitor module | Nos | 38
8 | Supply, erection, testing & commissioning of Telephone jack. | Nos | 2
9 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Loop cable) | Mtr | 690
10 | Providing & fixing FRLS CABLING complete with lugs, laying and termination of both ends.
a | 2C x 0.5 mm2 Armoured ( Telephone cable) | Mtr | 86
11 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Power cable) | Mtr | 620
12 | Supply, erection, fabrication, testing and commission of VOC detector with range of 1 – 1000 ppm isobutylene equivalent.and following accessoriesa) DigiPID internal dust filter (Pack of 5) b) Waterproof Filter Assy, RAEGuard2 PID, Pack of 5 c) DigiPID Teflon UV electrode shield pack of 10 d) DigiPID Dust Cover e) Air Drying Pre Filter Kit f) DigiPID external water trap filter (Pack of 5) | Nos | 16
13 | Supply, installation, testing and commissioning of aspiration detector with CMOS imager combined with multiple photodiode for reliable very early warning in a wide range of environments with minimal nuisance alarms. The detector should have 4 pipe inlet and min 100m pipelength support per inlet.The detector should have Smart on-board filter retains dust count and remaining filter life for predictable maintenance& coverage area of min 5000 Sq. | Nos | 4
14 | Supply,Installation,Testing & Commissioning of UL/VDS listed CPVC Pipe 25 mm Dia & Pipe Accessories for the Aspiration detection. | Mtr | 846
15 | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | Mtr | 894
D6 | PA SYSTEM
1 | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | Nos | 1
3 | 15 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | Nos | 8
4 | 30 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | Nos | 8
5 | Rack Mounted 500 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | Nos | 1
6 | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | Mtr | 440
7 | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | Nos | 1
8 | Paging Loudspeaker | Nos | 1
TOTAL

## ADMIN BUILDING
Annexure I
P.O. No. 317047 Dt. 24.11.23
Scope of Supply & Erection :
Sr No | Description | Unit | Qty | Supply |  | Erection
|  |  |  | Rate | Amount | Rate | Amount
E | ADMIN BUILDING
E1 | HYDRANT SYSTEM
1 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be of grooved with groove coupling. all escavation & back filling, pedestal support, structural support shall be of vendor's scope.
a. | 100 mm NB | Mtr | 36
b | 80 mm NB | Mtr | 36
c | 25 mm NB | Mtr | 18
2 | Supply & installation of swinging type hose reel drum fabricated from 14 SWG CRCA sheets painted with red colour stove paint 2 coats over 1 coat of primer with 30 m long 20 mm dia rubber hose pipe with with SS self closing shut – off nozzle of 5 mm outlet fixed on wall. | Nos | 3
3 | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends
a | Size 25NB | Nos | 3
4 | Supply & installation of SS oblique type single headed Landing valve with 80 mm inlet and 63 mm outlet SS instantaneous male coupling with rubber cap and chain conforming to IS : 5290 including matching flanges, gasket, nuts and bolts complete.
a | Size 80 mm NB | Nos | 3
5 | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. |  | 2
6 | Supply & installation of SS branch pipe with 20 mm nozzle conforming to IS : 903 complete | Nos | 2
7 | Supply & installation of 63 mm dia rubberized reinforced rubber line hose pipe in 15 m length conforming to IS : 636 Type II ISI marked with gunmetal male and female instantaneous coupling conforming to IS 903 wounded with 18 SWG copper wire complete | Nos | 4
8 | Supply & installation of MS Hose Box of fabricated from 16 SWG CRCA sheet double door with lockable arrangements to accommodate 2 RRL hose of 15 m length and one branch pipe painted white inside and red outside with one key. (750X600X250 mm) | Nos | 2
E2 | AUTOMATIC SPRINKLER SYSTEM
1 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be of grooved with groove couplings. All related civil work viz as wall cutting, structural supports etc for laying of sprinkler piping shall be vendor's scope.
a | 100 mm NB | Mtr | 12
b | 80 mm NB | Mtr | 18
c | 65 mm NB | Mtr | 30
d | 50 mm NB | Mtr | 18
e | 40 mm NB | Mtr | 18
f | 25 mm NB | Mtr | 72
2 | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor.
a | Size100 mm NB | Nos | 1
b | Size80 mm NB | Nos | 1
3 | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts confirming to API 594.
a | Size100 mm NB | Nos | 1
b | Size80 mm NB | Nos | 1
4 | Supply & fixing of paddle type Flow Switch | Nos | 2
5 | Supply,Fixing of Sprinkler Head Pendent type for K factor-80. Temp rating 68 deg C. UL/FM Approved. | Nos | 34
6 | Supply, installation of automatic 25 NB Air Release Valve | Nos | 1
7 | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends
a | Size 40NB | Nos | 2
b | Size 25NB | Nos | 2
8 | Supply,Erection and testing of Installation Control Valve complete with trims & gong.
a | Size 100 mm NB | Nos | 1
9 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, Class 150 with matching flanges complete with nuts & bolts.
a | Size 100 mm NB | Nos | 1
E3 | FDA SYSTEM
1 | Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | Nos | 25
2 | Supply, erection, testing & commissioning of analogue addressable Manual Call point | Nos | 4
3 | Supply, erection, testing & commissioning of Hooter cum strobe | Nos | 4
4 | Supply, erection, testing & commissioning of Telephone jack. | Nos | 2
5 | Supply, erction, testing & commissioning of analogue addressable Control Module | Nos | 2
6 | Supply, erection, testing & commissioning of analogue addressable Isolator Module | Nos | 2
7 | Supply, erection, testing & commissioning of analogue addressable Monitor module | Nos | 2
8 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Loop cable) | Mtr | 170
9 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Power cable) | Mtr | 104
10 | Providing & fixing FRLS CABLING complete with lugs, laying and termination of both ends.
a | 2C x 0.5 mm2 Armoured ( Telephone cable) | Mtr | 28
11 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Speaker cable) | Mtr | 164
12 | Supply, erection, testing & commissioning of Repeater Panel | Nos | 1
13 | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | Mtr | 170
E4 | PA SYSTEM
1 | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | Nos | 1
2 | 6 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | Nos | 21
3 | Rack Mounted 200 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | Nos | 1
4 | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | Mtr | 164
5 | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | Nos | 1
6 | Paging Loudspeaker | Nos | 1
TOTAL

## R&D BUILDING
Annexure I
P.O. No. 317047 Dt. 24.11.23
Scope of Supply & Erection :
Sr No | Description | Unit | Qty | Supply |  | Erection
|  |  |  | Rate | Amount | Rate | Amount
F | R & D BUILDING
F1 | HYDRANT SYSTEM
1 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be of groove with grooved coupling. All escavation, pedestal support, structural support shall be of vendor's scope.
a. | 100 mm NB | Mtr | 36
b | 80 mm NB | Mtr | 36
c | 25 mm NB | Mtr | 18
2 | Supply & installation of swinging type hose reel drum fabricated from 14 SWG CRCA sheets painted with red colour stove paint 2 coats over 1 coat of primer with 30 m long 20 mm dia rubber hose pipe with with SS self closing shut – off nozzle of 5 mm outlet fixed on wall. | Nos | 3
3 | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends
a | Size 25NB | Nos | 3
4 | Supply & installation of SS oblique type single headed Landing valve with 80 mm inlet and 63 mm outlet SS instantaneous male coupling with rubber cap and chain conforming to IS : 5290 including matching flanges, gasket, nuts and bolts complete. | Nos | 2
5 | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor.
a | Size 80 mm NB | Nos | 2
6 | Supply & installation of SS branch pipe with 20 mm nozzle conforming to IS : 903 complete | Nos | 2
7 | Supply & installation of 63 mm dia rubberized reinforced rubber line hose pipe in 15 m length conforming to IS : 636 Type II ISI marked with gunmetal male and female instantaneous coupling conforming to IS 903 wounded with 18 SWG copper wire complete | Nos | 4
8 | Supply & installation of MS Hose Box of fabricated from 16 SWG CRCA sheet double door with lockable arrangements to accommodate 2 RRL hose of 15 m length and one branch pipe painted white inside and red outside with one key. (750X600X250 mm) | Nos | 2
F2 | AUTOMATIC SPRINKLER SYSTEM
1 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope.
a | 150 mm NB | Mtr | 18
b | 100 mm NB | Mtr | 36
c | 80 mm NB | Mtr | 12
d | 65 mm NB | Mtr | 24
e | 50 mm NB | Mtr | 12
f | 40 mm NB | Mtr | 12
g | 25 mm NB | Mtr | 66
2 | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor.
a | Size150 mm NB | Nos | 2
b | Size50 mm NB | Nos | 1
3 | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts confirming to API 594.
a | Size150 mm NB | Nos | 2
b | Size50 mm NB | Nos | 1
4 | Supply & fixing of Paddle type Flow Switch | Nos | 2
5 | Supply,Fixing of Sprinkler Head Pendent type for K factor-80. Temp rating 68 deg C. UL/FM Approved. | Nos | 108
6 | Supply, installation of automatic 25 NB Air Release Valve | Nos | 1
7 | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends
a | Size 40NB | Nos | 2
b | Size 25NB | Nos | 2
8 | Supply,Erection and testing of Installation Control Valve complete with trims & gong.
a | Size 100 mm NB | Nos | 1
9 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts.
a | Size 100 mm NB | Nos | 1
F3 | FDA SYSTEM
1 | Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | Nos | 25
2 | Supply, erection, testing & commissioning of analogue addressable Manual Call point | Nos | 4
3 | Supply, erection, testing & commissioning of Hooter cum strobe | Nos | 4
4 | Supply, erection, testing & commissioning of Telephone jack. | Nos | 2
5 | Supply, erction, testing & commissioning of analogue addressable Control Module | Nos | 2
6 | Supply, erection, testing & commissioning of analogue addressable Isolator Module | Nos | 1
7 | Supply, erection, testing & commissioning of analogue addressable Monitor module | Nos | 3
8 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Loop cable) | Mtr | 170
9 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Power cable) | Mtr | 104
10 | Providing & fixing FRLS CABLING complete with lugs, laying and termination of both ends.
a | 2C x 0.5 mm2 Armoured ( Telephone cable) | Mtr | 28
11 | Providing & fixing 200Watt Amplifier with necessary accessories. | Nos | 1
12 | Supply, erection, testing & commissioning of Repeater Panel | Nos | 1
13 | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | Mtr | 170
F4 | PA SYSTEM
1 | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | Nos | 1
2 | 6 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | Nos | 21
3 | Rack Mounted 200 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | Nos | 1
4 | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | Mtr | 164
5 | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | Nos | 1
6 | Paging Loudspeaker | Nos | 1
Total

## MONOMER COLD ROOM
Annexure I
P.O. No. 317047 Dt. 24.11.23
Scope of Supply & Erection :
Sr No | Description | Unit | Qty | Supply |  | Erection
|  |  |  | Rate | Amount | Rate | Amount
G | MONOMER COLD ROOM
G1 | HIGH VELOCITY WATER SPRAY SYSTEM
1 | Supply, erection , testing & commissioning of Deluge valve with wet pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 3/2 way Solenoid Valve, air filter regulator etc. & manual release unit. The valve shall be electro-pneumatic type.
a | 80 mm NB | Nos | 1
2 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts.
a | 80 mm NB | Nos | 3
3 | Supply, installation, testing & commissioning of Y- Stainer
a | 80 mm NB | Nos | 1
4 | Supply,installation,testing and commissioning of HVWS NOZZLE with necessary threaded fittings as per drawing.
a | K26, SPRAY ANGLE=100° | Nos | 12
5 | Supply,installation and commissioning of UL/FM approved Quartzoid Bulb Detector for K factor-80. Temp rating 68 deg C | Nos | 12
6 | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications
a | 80 NB | Mtr | 9
b | 65 NB | Mtr | 6
c | 50 NB | Mtr | 6
d | 40NB | Mtr | 17
e | 25NB | Mtr | 56
7 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope.
a | 100 mm NB | Mtr | 12
b | 80 mm NB | Mtr | 12
G2 | FDA SYSTEM
1 | Supply, erection, testing & commissioning of analogue addressable ROR(Rate of Rise) type Heat Detector | Nos | 4
2 | Supply, erection, testing & commissioning of analogue addressable Manual Call point | Nos | 1
3 | Supply, erection, testing & commissioning of Hooter cum strobe | Nos | 1
4 | Supply, erction, testing & commissioning of analogue addressable Control Module | Nos | 2
5 | Supply, erection, testing & commissioning of analogue addressable Isolator Module | Nos | 1
6 | Supply, erection, testing & commissioning of analogue addressable Monitor module | Nos | 1
7 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Loop cable) | Mtr | 32
8 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Power cable) | Mtr | 12
9 | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | Mtr | 32
G3 | PA SYSTEM
1 | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | Nos | 1
2 | 6 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | Nos | 2
3 | Rack Mounted 125 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | Nos | 1
4 | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | Mtr | 18
5 | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | Nos | 1
6 | Paging Loudspeaker | Nos | 1
TOTAL

## MONOMER, STYRENE & SOLVENT PUMP
Annexure I
P.O. No. 317047 Dt. 24.11.23
Scope of Supply & Erection :
Sr No | Description | Unit | Qty | Supply |  | Erection
|  |  |  | Rate | Amount | Rate | Amount
H | MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK
H1 | FOAM WATER SPRAY SYSTEM
1 | Supply, erection , testing & commissioning of Deluge valve with dry pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 3/2 way Solenoid Valve, air filter regulator etc. & manual release unit. The valve shall be electro-pneumatic double inter lock system as per scheme drawing.
a | 80 mm NB | Nos | 3
2 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts.
a | 80 mm NB | Nos | 9
3 | Supply, installation, testing and commissioning of Y-Strainer..
a | Size 80 mm NB | Nos | 3
4 | Supply,installation,testing and commissioning of Foam Sprinkler nozzle with necessary threaded fittings as per drawing. The sprinkler shall be Open Aspiration, Pendent type, K-42 with standard spray angle.End connection 1/2" NPT/BSP.UL/FM Approved.
a | Spray nozzle K factor -42 | Nos | 17
5 | Supply,installation and commissioning of UL/FM approved Quartzoid Bulb Detector for K factor-80. Temp rating 68 deg C | Nos | 17
6 | Supply, installation, testing and commissioning of Ratio Controller. | Nos
a | 80NB | Nos | 3
7 | Supply, installation, testing and commissioning of Foam bladder tank vertical type ,manufacturing as per ASME, section-VIII part- I. The bladder material shall be BUNA-N. The Bladder Tank shall be supplied along with all necessary valves, Hydraulically Operated Foam Concentrae Control Valve ,fittingss & instruments as per Technical data sheet attached with Tender documents.
a | Capacity of 500 ltr. | Nos | 1
8 | Supply of AR-AFFF(3%) foam concentrate(PFOS/PFAS free) having sp. Gravity 1.0±.02 g/mlat 20⁰C , PH 7.0-8.5 & viscosity 1200 ±300 cps. | Ltr | 500
9 | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications
a | 50 NB | Mtr | 24
b | 40NB | Mtr | 52
c | 25NB | Mtr | 111
10 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope.
a | 100 mm NB | Mtr | 12
b | 80 mm NB | Mtr | 36
H2 | FOAM GENERATOR
1 | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications
a | 150 NB | Mtr | 34
b | 100 NB | Mtr | 89
2 | Supply, erection , testing & commissioning of Deluge valve with dry pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch,dry pilot actuator, air filter regulator etc. & manual release unit.
a | Size 150 NB | Nos | 2
3 | Providing & fixing Cast Iron Y Strainer.
a | Size 150 NB | Nos | 2
4 | Supply & fixing of SS-304 FOAM GENERATOR with Minimum flow 120lpm | Nos | 4
5 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts.
a | Size 150 NB | Nos | 6
6 | Supply, installation, testing and commissioning of Atmospheric Foam tank vertical type ,manufacturing as per ASME, section-VIII part- I. Tank shall be supplied along with all necessary valves, fittingss & instruments as per Technical data sheet attached with Tender documents.
a | Capacity of 250 ltr. | Nos | 2
7 | Supply of AR-AFFF(3%) foam concentrate (PFOS/PFAS free) having sp. Gravity 1.0±.02 g/mlat 20⁰C , pH 7.0-8.5 & viscosity 1200 ±300 cps. | Ltr | 500
8 | Supply, installation, testing and commissioning of Inline Inductor
a | 150NB | Nos | 2
H3 | FDA SYSTEM
1 | Supply, erection, testing & commissioning of analogue addressable Monitor module | Nos | 4
2 | Supply, erection, testing & commissioning of IR Detector | Nos | 4
3 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Loop cable) | Mtr | 106
4 | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | Mtr | 106
Total

## PAINTS CONTROL LAB
Annexure I
P.O. No. 317047 Dt. 24.11.23
Scope of Supply & Erection :
Sr No | Description | Unit | Qty | Supply |  | Erection
|  |  |  | Rate | Amount | Rate | Amount
I | PAINTS CONTROL LAB
I1 | HYDRANT SYSTEM
1 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope.
a | 100 mm NB | Mtr | 36
b | 80 mm NB | Mtr | 36
c | 25 mm NB | Mtr | 18
2 | Supply & installation of swinging type hose reel drum fabricated from 14 SWG CRCA sheets painted with red colour stove paint 2 coats over 1 coat of primer with 30 m long 20 mm dia rubber hose pipe with with SS self closing shut – off nozzle of 5 mm outlet fixed on wall. | Nos | 3
3 | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends
a | Size 25NB | Nos | 3
4 | Supply & installation of SS oblique type single headed Landing valve with 80 mm inlet and 63 mm outlet SS instantaneous male coupling with rubber cap and chain conforming to IS : 5290 including matching flanges, gasket, nuts and bolts complete. | Nos | 2
5 | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor.
a | Size 80 mm NB | Nos | 2
6 | Supply & installation of SS branch pipe with 20 mm nozzle conforming to IS : 903 complete | Nos | 2
7 | Supply & installation of 63 mm dia rubberized reinforced rubber line hose pipe in 15 m length conforming to IS : 636 Type II ISI marked with gunmetal male and female instantaneous coupling conforming to IS 903 wounded with 18 SWG copper wire complete | Nos | 4
8 | Supply & installation of MS Hose Box of fabricated from 16 SWG CRCA sheet double door with lockable arrangements to accommodate 2 RRL hose of 15 m length and one branch pipe painted white inside and red outside with one key. (750X600X250 mm) | Nos | 2
I2 | AUTOMATIC SPRINKLER SYSTEM
1 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope.
a | 100 mm NB | Mtr | 12
b | 80 mm NB | Mtr | 6
c | 65 mm NB | Mtr | 9
d | 50 mm NB | Mtr | 6
e | 40 mm NB | Mtr | 18
f | 25 mm NB | Mtr | 54
2 | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor.
a | Size80 mm NB | Nos | 1
b | Size40 mm NB | Nos | 1
3 | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts confirming IS:5312(PN16).
a | Size80 mm NB | Nos | 1
b | Size40 mm NB | Nos | 1
4 | Supply & fixing of paddle type Flow Switch | Nos | 2
5 | Supply,Fixing of Sprinkler Head Pendent type for K factor-80. Temp rating 68 deg C.UL/FM Approved. | Nos | 26
6 | Supply, installation of automatic 25 NB Air Release Valve | Nos | 1
7 | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends
a | Size 40NB | Nos | 2
b | Size 25NB | Nos | 2
8 | Supply,Erection and testing of Installation Control Valve complete with trims & gong.
a | Size 100 mm NB | Nos | 1
9 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts.
a | Size 100 mm NB | Nos | 1
I3 | FDA SYSTEM
1 | Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | Nos | 13
2 | Supply, erection, testing & commissioning of analogue addressable Manual Call point | Nos | 3
3 | Supply, erection, testing & commissioning of Hooter cum strobe | Nos | 3
4 | Supply, erection, testing & commissioning of Telephone jack. | Nos | 2
5 | Supply, erction, testing & commissioning of analogue addressable Control Module | Nos | 2
6 | Supply, erection, testing & commissioning of analogue addressable Isolator Module | Nos | 2
7 | Supply, erection, testing & commissioning of analogue addressable Monitor module | Nos | 2
8 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Loop cable) | Mtr | 125
9 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Power cable) | Mtr | 50
10 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 0.5 mm2 Armoured ( Telephone cable) | Mtr | 20
11 | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | Mtr | 131
I4 | PA SYSTEM
1 | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | Nos | 1
2 | 6 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | Nos | 11
3 | Rack Mounted 100 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | Nos | 1
4 | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | Mtr | 131
5 | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | Nos | 1
6 | Paging Loudspeaker | Nos | 1
Total

## WATER BASED PLANT
Annexure I
P.O. No. 317047 Dt. 24.11.23
Scope of Supply & Erection :
Sr No | Description | Unit | Qty | Supply |  | Erection
|  |  |  | Rate | Amount | Rate | Amount
J | WATER BASED PLANT
J1 | HYDRANT SYSTEM
1 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope.
a | 150 mm NB | Mtr | 12
b | 80 mm NB | Mtr | 24
c | 25 mm NB | Mtr | 6
2 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts.
a | Size 150 mm NB | Nos | 1
3 | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts confirming IS:5312(PN16).
a | Size 150 mm NB | Nos | 1
4 | Supply & installation of SS oblique type single headed Landing valve with 80 mm inlet and 63 mm outlet SS instantaneous male coupling with rubber cap and chain conforming to IS : 5290 including matching flanges, gasket, nuts and bolts complete. | Nos | 4
5 | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor.
a | Size 80 mm NB | Nos | 4
6 | Supply & installation of SS branch pipe with 20 mm nozzle conforming to IS : 903 complete | Nos | 4
7 | Supply & installation of 63 mm dia rubberized reinforced rubber line hose pipe in 15 m length conforming to IS : 636 Type II ISI marked with gunmetal male and female instantaneous coupling conforming to IS 903 wounded with 18 SWG copper wire complete | Nos | 8
8 | Supply & installation of MS Hose Box of fabricated from 16 SWG CRCA sheet double door with lockable arrangements to accommodate 2 RRL hose of 15 m length and one branch pipe painted white inside and red outside with one key. (750X600X250 mm) | Nos | 4
9 | Supply & installation of swinging type hose reel drum fabricated from 14 SWG CRCA sheets painted with red colour stove paint 2 coats over 1 coat of primer with 30 m long 20 mm dia rubber hose pipe with with SS self closing shut – off nozzle of 5 mm outlet fixed on wall. | Nos | 4
10 | Supply and installation of pressure gauge, 1/2 inch bottom entry, of suitable range with ball valves and other accessories. | Nos | 1
11 | Supply, installation of automatic 25 NB Air Release Valve | Nos | 1
12 | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends
a | Size 25NB | Nos | 6
J2 | AUTOMATIC SPRINKLER SYSTEM
1 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope.
a | 150 mm NB | Mtr | 121
b | 100 mm NB | Mtr | 101
c | 80 mm NB | Mtr | 66
d | 65 mm NB | Mtr | 286
e | 50 mm NB | Mtr | 386
f | 40 mm NB | Mtr | 602
2 | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor.
a | Size150 mm NB | Nos | 7
3 | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts confirming IS:5312(PN16).
a | Size150 mm NB | Nos | 7
4 | Supply & fixing of paddle type Flow Switch | Nos | 7
5 | Supply,Fixing of Sprinkler Head Pendent type for K factor-160. Temp rating 68 deg C.UL/FM Approved. | Nos | 540
6 | Supply, installation of automatic 25 NB Air Release Valve | Nos | 1
7 | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends
a | Size 40NB | Nos | 7
b | Size 25NB | Nos | 2
8 | Supply,Erection and testing of Installation Control Valve complete with trims & gong.
a | Size 150 mm NB | Nos | 1
9 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts.
a | Size 150 mm NB | Nos | 1
J3 | WATER CURTAIN
1 | Supply, erection and testing of heavy grade(class-C) pipes of thickness 5.4mm conforming to IS-1239 including all fittings viz. tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer and structural steels for pipe supports. Hanger support with anchor fasteners and clamps shall be supplied to fix the pipes on ceiling wall etc. including supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners) as per specification. Cutting of floors, walls etc and making it good after erection of pipes shall be of vendor's scope. Necessary painting with 2 coats of primer and 2 coats of synthetic enamel paints to be done and supply of paints shall be with vendor's scope.
a | 50 NB | Mtr | 56
b | 65 NB | Mtr | 52
c | 80 NB | Mtr | 66
d | 100 NB | Mtr | 36
2 | Supply, erection , testing & commissioning of Deluge valve with wet pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 2 way Solenoid Valve, air filter regulator etc. & manual release unit.
a | Size 80 NB | Nos | 1
b | Size 100 NB | Nos | 3
3 | Providing & fixing Cast Iron Y Strainer.
a | Size 80 NB | Nos | 1
b | Size 100 NB | Nos | 3
4 | Supply & fixing of SS Water Curtain Nozzle (K>=71)).UL/FM Approved. | Nos | 67
5 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts.
a | Size 80 NB | Nos | 3
b | Size 100 NB | Nos | 9
6 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope.
a | 150 mm NB | Mtr | 18
b | 100 mm NB | Mtr | 24
c | 80 mm NB | Mtr | 12
J4 | FDA SYSTEM
1 | Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | Nos | 15
2 | Supply, erection, testing & commissioning of analogue addressable Manual Call point | Nos | 12
3 | Supply, erection, testing & commissioning of Hooter cum strobe | Nos | 12
4 | Supply, erection, testing & commissioning of Telephone jack. | Nos | 2
5 | Supply, erction, testing & commissioning of analogue addressable Control Module | Nos | 4
6 | Supply, erection, testing & commissioning of analogue addressable Isolator Module | Nos | 2
7 | Supply, erection, testing & commissioning of analogue addressable Monitor module | Nos | 2
8 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Loop cable) | Mtr | 572
9 | Supply, installation, testing and commissioning of aspiration detector with CMOS imager combined with multiple photodiode for reliable very early warning in a wide range of environments with minimal nuisance alarms. The detector should have 4 pipe inlet and min 100m pipelength support per inlet.The detector should have Smart on-board filter retains dust count and remaining filter life for predictable maintenance& coverage area of min 5000 Sq. | Nos | 7
10 | Supply,Installation,Testing & Commissioning of UL/VDS listed CPVC Pipe 25 mm Dia & Pipe Accessories for the Aspiration detection. | Mtr | 980
11 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Power cable) | Mtr | 706
12 | Providing & fixing FRLS CABLING complete with lugs, laying and termination of both ends.
a | 2C x 0.5 mm2 Armoured ( Telephone cable) | Mtr | 60
13 | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | Mtr | 1158
J5 | PA SYSTEM
1 | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | Nos | 1
2 | 9 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | Nos | 5
3 | 30 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | Nos | 4
4 | Rack Mounted 200 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | Nos | 1
5 | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | Mtr | 350
6 | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | Nos | 1
7 | Paging Loudspeaker | Nos | 1
TOTAL

## RAW MATERIAL STORE
Annexure I
P.O. No. 317047 Dt. 24.11.23
Scope of Supply & Erection :
Sr No | Description | Unit | Qty | Supply |  | Erection
|  |  |  | Rate | Amount | Rate | Amount
K | RAW MATERIAL STORE
K1 | HYDRANT SYSTEM
1 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope.
a | 100 mm NB | Mtr | 36
b | 80 mm NB | Mtr | 12
c | 25 mm NB | Mtr | 6
2 | Supply & installation of SS oblique type single headed Landing valve with 80 mm inlet and 63 mm outlet SS instantaneous male coupling with rubber cap and chain conforming to IS : 5290 including matching flanges, gasket, nuts and bolts complete. | Nos | 4
3 | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor.
a | Size 80 mm NB | Nos | 4
4 | Supply & installation of SS branch pipe with 20 mm nozzle conforming to IS : 903 complete | Nos | 4
5 | Supply & installation of 63 mm dia rubberized reinforced rubber line hose pipe in 15 m length conforming to IS : 636 Type II ISI marked with gunmetal male and female instantaneous coupling conforming to IS 903 wounded with 18 SWG copper wire complete | Nos | 8
6 | Supply & installation of MS Hose Box of fabricated from 16 SWG CRCA sheet double door with lockable arrangements to accommodate 2 RRL hose of 15 m length and one branch pipe painted white inside and red outside with one key. (750X600X250 mm). | Nos | 4
7 | Supply & installation of swinging type hose reel drum fabricated from 14 SWG CRCA sheets painted with red colour stove paint 2 coats over 1 coat of primer with 30 m long 20 mm dia rubber hose pipe with with SS self closing shut – off nozzle of 5 mm outlet fixed on wall. | Nos | 4
8 | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends
a | Size 25NB | Nos | 4
K2 | AUTOMATIC SPRINKLER SYSTEM
1 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope.
a | 150 mm NB | Mtr | 122
b | 100 mm NB | Mtr | 76
c | 80 mm NB | Mtr | 64
d | 65 mm NB | Mtr | 101
e | 50 mm NB | Mtr | 293
f | 40 mm NB | Mtr | 384
2 | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor.
a | Size150 mm NB | Nos | 3
b | Size100 mm NB | Nos | 1
3 | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts confirming IS:5312(PN16).
a | Size150 mm NB | Nos | 3
b | Size100 mm NB | Nos | 1
4 | Supply & fixing of paddle type Flow Switch | Nos | 4
5 | Supply,Fixing of Sprinkler Head Pendent type for K factor-160 Temp rating 68 deg. CUL/FM Approved. | Nos | 316
6 | Supply, installation of automatic 25 NB Air Release Valve | Nos | 1
7 | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends
a | Size 40NB | Nos | 2
b | Size 25NB | Nos | 2
8 | Supply,Erection and testing of Installation Control Valve complete with trims & gong.
a | Size 150 mm NB | Nos | 1
9 | Supply, installation, testing & commissioning of CI Gate Valve as per IS:14846 (PN 16) with matching flanges complete with nuts & bolts.
a | Size 150 mm NB | Nos | 1
K3 | WATER CURTAIN
1 | Supply, erection and testing of heavy grade(class-C) pipes conforming to IS-1239 / IS-3589 including all fittings viz. tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer and structural steels for pipe supports. Hanger support with anchor fasteners and clamps shall be supplied to fix the pipes on ceiling wall etc. including supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners) as per specification. Cutting of floors, walls etc and making it good after erection of pipes shall be of vendor's scope. Necessary painting with 2 coats of primer and 2 coats of synthetic enamel paints to be done and supply of paints shall be with vendor's scope.
a | 50 NB | Mtr | 18
b | 65 NB | Mtr | 18
c | 80 NB | Mtr | 16
2 | Supply, erection , testing & commissioning of Deluge valve with wet pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 2 way Solenoid Valve, air filter regulator etc. & manual release unit.
a | Size 80 NB | Nos | 2
3 | Providing & fixing Cast Iron Y Strainer.
a | Size 80 NB | Nos | 2
4 | Supply & fixing of SS Water Curtain Nozzle (K>=71)).UL/FM Approved. | Nos | 20
5 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts.
a | Size 80 NB | Nos | 6
6 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope.
a | 150 mm NB | Mtr | 18
b | 100 mm NB | Mtr | 24
c | 80 mm NB | Mtr | 12
K4 | FDA SYSTEM
1 | Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | Nos | 89
2 | Supply, erection, testing & commissioning of analogue addressable Manual Call point | Nos | 7
3 | Supply, erection, testing & commissioning of Hooter cum strobe | Nos | 7
4 | Supply, erection, testing & commissioning of Telephone jack. | Nos | 2
5 | Supply, erction, testing & commissioning of analogue addressable Control Module | Nos | 3
6 | Supply, erection, testing & commissioning of analogue addressable Isolator Module | Nos | 2
7 | Supply, erection, testing & commissioning of analogue addressable Monitor module | Nos | 2
8 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Loop cable) | Mtr | 754
9 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Power cable) | Mtr | 297
10 | Providing & fixing FRLS CABLING complete with lugs, laying and termination of both ends.
a | 2C x 0.5 mm2 Armoured ( Telephone cable) | Mtr | 20
11 | Supply, installation, testing and commissioning of aspiration detector with CMOS imager combined with multiple photodiode for reliable very early warning in a wide range of environments with minimal nuisance alarms. The detector should have 4 pipe inlet and min 100m pipelength support per inlet.The detector should have Smart on-board filter retains dust count and remaining filter life for predictable maintenance& coverage area of min 5000 Sq. | Nos | 6
12 | Supply,Installation,Testing & Commissioning of UL/VDS listed CPVC Pipe 25 mm Dia & Pipe Accessories for the Aspiration detection. | Mtr | 441
13 | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | Mtr | 754
K5 | PA SYSTEM
1 | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | Nos | 1
2 | 30 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | Nos | 8
3 | 15 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | Nos | 1
4 | Rack Mounted 250 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | Nos | 1
5 | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | Mtr | 250
6 | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | Nos | 1
7 | Paging Loudspeaker | Nos | 1
TOTAL

## COLORANT STORE
Annexure I
P.O. No. 317047 Dt. 24.11.23
Scope of Supply & Erection :
Sr No | Description | Unit | Qty | Supply |  | Erection
|  |  |  | Rate | Amount | Rate | Amount
L | COLORANT STORE
L1 | HYDRANT SYSTEM
1 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope.
a | 150 mm NB | Mtr | 36
b | 80 mm NB | Mtr | 12
c | 25 mm NB | Mtr | 6
2 | Supply & installation of SS oblique type single headed Landing valve with 80 mm inlet and 63 mm outlet SS instantaneous male coupling with rubber cap and chain conforming to IS : 5290 including matching flanges, gasket, nuts and bolts complete. | Nos | 8
3 | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor.
a | Size 80 mm NB | Nos | 8
4 | Supply & installation of SS branch pipe with 20 mm nozzle conforming to IS : 903 complete | Nos | 8
5 | Supply & installation of 63 mm dia rubberized reinforced rubber line hose pipe in 15 m length conforming to IS : 636 Type II ISI marked with gunmetal male and female instantaneous coupling conforming to IS 903 wounded with 18 SWG copper wire complete | Nos | 16
6 | Supply & installation of MS Hose Box of fabricated from 16 SWG CRCA sheet double door with lockable arrangements to accommodate 2 RRL hose of 15 m length and one branch pipe painted white inside and red outside with one key. (750X600X250 mm) | Nos | 8
7 | Supply & installation of swinging type hose reel drum fabricated from 14 SWG CRCA sheets painted with red colour stove paint 2 coats over 1 coat of primer with 30 m long 20 mm dia rubber hose pipe with with SS self closing shut – off nozzle of 5 mm outlet fixed on wall. | Nos | 8
8 | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends
a | Size 25NB | Nos | 4
b | Size 40NB | Nos | 8
L2 | FDA SYSTEM
1 | Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | Nos | 141
2 | Supply, erection, testing & commissioning of analogue addressable Manual Call point | Nos | 15
3 | Supply, erection, testing & commissioning of Hooter cum strobe | Nos | 14
4 | Supply, erection, testing & commissioning of Telephone jack. | Nos | 8
5 | Supply, erction, testing & commissioning of analogue addressable Control Module | Nos | 5
6 | Supply, erection, testing & commissioning of analogue addressable Isolator Module | Nos | 4
7 | Supply, erection, testing & commissioning of analogue addressable Monitor module | Nos | 4
8 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Loop cable) | Mtr | 1170
9 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Power cable) | Mtr | 401
10 | Providing & fixing FRLS CABLING complete with lugs, laying and termination of both ends.
a | 2C x 0.5 mm2 Armoured ( Telephone cable) | Mtr | 327
11 | Supply, erection, testing & commissioning of 6 Watt Ceiling mounted Speakers | Nos | 80
12 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Speaker cable) | Mtr | 1027
13 | Providing & fixing 600Watt Amplifier with necessary accessories. | Nos | 1
14 | Supply, installation, testing and commissioning of aspiration detector with CMOS imager combined with multiple photodiode for reliable very early warning in a wide range of environments with minimal nuisance alarms. The detector should have 4 pipe inlet and min 100m pipelength support per inlet.The detector should have Smart on-board filter retains dust count and remaining filter life for predictable maintenance& coverage area of min 5000 Sq. | Nos | 4
15 | Supply,Installation,Testing & Commissioning of UL/VDS listed CPVC Pipe 25 mm Dia & Pipe Accessories for the Aspiration detection. | Mtr | 744
16 | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | Mtr | 1170
L3 | PA SYSTEM
1 | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | Nos | 1
2 | 30 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | Nos | 8
3 | 9 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | Nos | 1
4 | 6 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | Nos | 23
5 | Rack Mounted 400 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | Nos | 1
6 | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | Mtr | 541
7 | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | Nos | 1
8 | Paging Loudspeaker | Nos | 1
TOTAL

## SOFA TANK
Annexure I
P.O. No. 317047 Dt. 24.11.23
Scope of Supply & Erection :
Sr No | Description | Unit | Qty | Supply |  | Erection
|  |  |  | Rate | Amount | Rate | Amount
M | SOFA TANK
M1 | MEDIUM VELOCITY WATER SPRAY SYSTEM
1 | Supply, erection , testing & commissioning of Deluge valve with wet pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 3/2 way Solenoid Valve, air filter regulator etc. & manual release unit. The valve shall be electro-pneumatic type.
a | 150 mm NB | Nos | 1
2 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts.
a | 150 mm NB | Nos | 3
3 | Supply, installation, testing of Y- Stainer.
a | 150 mm NB | Nos | 1
4 | Supply,installation and commissioning of UL/FM approved Medium Velocity Water Spray Nozzle
a | MVWS nozzle K factor 18, spray angle 100⁰ | Nos | 66
5 | Supply,installation and commissioning of UL/FM approved Quartzoid Bulb Detector for K factor-80. Temp rating 68 deg C | Nos | 66
6 | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications
a | 150 NB | Mtr | 24
b | 100 NB | Mtr | 24
c | 80 NB | Mtr | 30
d | 65 NB | Mtr | 60
7 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope.
a | 150 NB | Mtr | 36
b | 25 NB | Mtr | 218
8 | Supply, erction, testing & commissioning of analogue addressable Control Module | Nos | 1
9 | Supply, erction, testing & commissioning of analogue addressable Monitor Module | Nos | 1
M2 | FOAM GENERATOR
1 | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications
a | 150 NB | Mtr | 66
b | 100 NB | Mtr | 140
2 | Supply, erection , testing & commissioning of Deluge valve with dry pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch,dry pilot actuator, air filter regulator etc. & manual release unit.
a | Size 150 NB | Nos | 4
3 | Providing & fixing Cast Iron Y Strainer.
a | Size 150 NB | Nos | 4
4 | Supply & fixing of SS-304 FOAM GENERATOR with Minimum flow 120lpm | Nos | 8
5 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts.
a | Size 150 NB | Nos | 12
6 | Supply, installation, testing and commissioning of Atmospheric Foam tank vertical type ,manufacturing as per ASME, section-VIII part- I. Tank shall be supplied along with all necessary valves, fittingss & instruments as per Technical data sheet attached with Tender documents.
a | Capacity of 250 ltr. | Nos | 4
7 | Supply of AR-AFFF(3%) foam concentrate (PFOS/PFAS free) having sp. Gravity 1.0±.02 g/mlat 20⁰C , pH 7.0-8.5 & viscosity 1200 ±300 cps. | Ltr | 1000
8 | Supply, installation, testing and commissioning of Inline Inductor
a | 150NB | Nos | 4
M3 | FDA SYSTEM
1 | Supply, erection, testing & commissioning of analogue addressable Monitor module | Nos | 5
2 | Supply, erection, testing & commissioning of IR Detector | Nos | 5
3 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Loop cable) | Mtr | 120
4 | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | Mtr | 120
TOTAL

## DEG & MEG TANK
Annexure I
P.O. No. 317047 Dt. 24.11.23
Scope of Supply & Erection :
Sr No | Description | Unit | Qty | Supply |  | Erection
|  |  |  | Rate | Amount | Rate | Amount
N | DEG & MEG TANK
N1 | MEDIUM VELOCITY WATER SPRAY SYSTEM
1 | Supply, erection , testing & commissioning of Deluge valve with wet pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 3/2 way Solenoid Valve, air filter regulator etc. & manual release unit. The valve shall be electro-pneumatic type.
a | 150 mm NB | Nos | 1
2 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts.
a | 150 mm NB | Nos | 3
3 | Supply, installation, testing of Y- Stainer
a | 150 mm NB | Nos | 1
4 | Supply,installation and commissioning of UL/FM approved Medium Velocity Water Spray Nozzle
a | MVWS nozzle K factor 18, spray angle 100⁰ | Nos | 90
5 | Supply,installation and commissioning of UL/FM approved Quartzoid Bulb Detector for K factor-80. Temp rating 68 deg C | Nos | 90
6 | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications
a | 150 NB | Mtr | 12
b | 100 NB | Mtr | 14
c | 80 NB | Mtr | 64
d | 65 NB | Mtr | 52
7 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope.
a | 150 mm NB | Mtr | 24
b | 25 NB | Mtr | 146
8 | Supply, erction, testing & commissioning of analogue addressable Control Module | Nos | 1
9 | Supply, erction, testing & commissioning of analogue addressable Monitor Module | Nos | 1
10 | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | Mtr | 24
N2 | FOAM GENERATOR
1 | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications
a | 150 NB | Mtr | 12
b | 100 NB | Mtr | 42
2 | Supply, erection , testing & commissioning of Deluge valve with dry pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch,dry pilot actuator, air filter regulator etc. & manual release unit.
a | Size 150 NB | Nos | 1
3 | Providing & fixing Cast Iron Y Strainer.
a | Size 150 NB | Nos | 1
4 | Supply & fixing of SS-304 FOAM GENERATOR with Minimum flow 120lpm | Nos | 2
5 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts.
a | Size 150 NB | Nos | 3
6 | Supply, installation, testing and commissioning of Atmospheric Foam tank vertical type ,manufacturing as per ASME, section-VIII part- I. Tank shall be supplied along with all necessary valves, fittingss & instruments as per Technical data sheet attached with Tender documents.
a | Capacity of 250 ltr. | Nos | 1
7 | Supply of AR-AFFF(3%) foam concentrate (PFOS/PFAS free) having sp. Gravity 1.0±.02 g/mlat 20⁰C , pH 7.0-8.5 & viscosity 1200 ±300 cps. | Ltr | 250
8 | Supply, installation, testing and commissioning of Inline Inductor
a | 150NB | Nos | 1
N3 | FDA SYSTEM
1 | Supply, erection, testing & commissioning of analogue addressable Monitor module | Nos | 4
2 | Supply, erection, testing & commissioning of IR Detector | Nos | 4
3 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Loop cable) | Mtr | 56
4 | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | Mtr | 56
TOTAL

## SECURITY ROOM
Annexure I
P.O. No. 317047 Dt. 24.11.23
Scope of Supply & Erection :
Sr No | Description | Unit | Qty | Supply |  | Erection
|  |  |  | Rate | Amount | Rate | Amount
O | SECURITY ROOM
O1 | FDA SYSTEM
1 | Supply, installation, testing and commissioning of Microprocessor based 6 Loop expandable upto 10 loops,Networkable analogue addressable type fire alarm control panel with 640 character LCD display.Detectors can be any mix of ion, photo, laser photo,thermal, or multi-sensor detectors; modules can be addressable pull stations, normally open contact devices,two-wire smoke, notification, or relay modules. Four access levels, Printer Port,RS-485 port for repeater/mimic panel communication,240 volts AC power supply, automatic battery charger, 24 volts sealed lead acid batteries sufficient for 24 hours normal working and then be capable of operating the system for 10 Min during an emergency conditions as required. The Panel shall have compatibility with BACKNET/MODBUS CARD for integration. | Nos | 1
2 | Providing & fixing of PA console with selector zone facility with necessary accessories. | Nos | 1
3 | Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | Nos | 6
4 | Supply, erection, testing & commissioning of analogue addressable Manual Call point | Nos | 2
5 | Supply, erection, testing & commissioning of Hooter cum strobe | Nos | 2
6 | Supply, erection, testing & commissioning of Telephone jack. | Nos | 1
7 | Supply, erction, testing & commissioning of analogue addressable Control Module | Nos | 1
8 | Supply, erection, testing & commissioning of analogue addressable Isolator Module | Nos | 2
9 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Loop cable) | Mtr | 38
10 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Power cable) | Mtr | 29
11 | Providing & fixing FRLS CABLING complete with lugs, laying and termination of both ends.
a | 2C x 0.5 mm2 Armoured ( Telephone cable) | Mtr | 12
12 | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | Mtr | 38
O2 | PA SYSTEM
1 | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | Nos | 1
2 | 6 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | Nos | 3
3 | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | Mtr | 19
4 | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | Nos | 1
5 | Paging Loudspeaker | Nos | 1
TOTAL

## BIOBRIQUETE STORE
Annexure I
P.O. No. 317047 Dt. 24.11.23
Scope of Supply & Erection :
Sr No | Description | Unit | Qty | Supply |  | Erection
|  |  |  | Rate | Amount | Rate | Amount
P | BIOBIQUETE STORE
P1 | AUTOMATIC SPRINKLER SYSTEM
1 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope.
a | 80 mm NB | Mtr | 12
b | 40 mm NB | Mtr | 18
c | 25 mm NB | Mtr | 12
2 | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor.
a | Size80 mm NB | Nos | 1
3 | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts.
a | Size80 mm NB | Nos | 1
4 | Supply & fixing of paddle type Flow Switch | Nos | 1
5 | Supply,Fixing of Sprinkler Head Pendent type for K factor-80. Temp rating 68 deg C.UL/FM Approved. | Nos | 3
6 | Supply, installation of automatic 25 NB Air Release Valve | Nos | 1
7 | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends
a | Size 40NB | Nos | 1
b | Size 25NB | Nos | 2
8 | Supply,Erection and testing of Installation Control Valve complete with trims & gong.
a | Size 80 mm NB | Nos | 1
9 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts.
a | Size 80 mm NB | Nos | 1
P2 | FDA SYSTEM
1 | Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | Nos | 3
2 | Supply, erection, testing & commissioning of analogue addressable Manual Call point | Nos | 1
3 | Supply, erection, testing & commissioning of Hooter cum strobe | Nos | 1
4 | Supply, erction, testing & commissioning of analogue addressable Control Module | Nos | 1
5 | Supply, erection, testing & commissioning of analogue addressable Isolator Module | Nos | 2
6 | Supply, erection, testing & commissioning of analogue addressable Monitor module | Nos | 1
7 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Loop cable) | Mtr | 36
8 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Power cable) | Mtr | 24
9 | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | Mtr | 36
P3 | PA SYSTEM
1 | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | Nos | 1
2 | 9 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | Nos | 1
3 | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | Mtr | 32
4 | Rack Mounted 125 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | Nos | 1
5 | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | Nos | 1
6 | Paging Loudspeaker | Nos | 1
TOTAL

## SUBSTATION BUILDING
Annexure I
P.O. No. 317047 Dt. 24.11.23
Scope of Supply & Erection :
Sr No | Description | Unit | Qty | Supply |  | Erection
|  |  |  | Rate | Amount | Rate | Amount
Q | SUBSTATION BUILDING
Q1 | HIGH VELOCITY WATER SPRAY SYSTEM
1 | Supply, erection , testing & commissioning of Deluge valve with wet pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 3/2 way Solenoid Valve, air filter regulator etc. & manual release unit. The valve shall be electro-pneumatic type.
a | 80 mm NB | Nos | 2
2 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts.
a | 80 mm NB | Nos | 6
3 | Supply, installation, testing of Y- Stainer .
a | 80 mm NB | Nos | 2
4 | Supply,installation,testing and commissioning of HVWS NOZZLE with necessary threaded fittings as per drawing.
a | K26, SPRAY ANGLE=100° | Nos | 32
5 | Supply,installation and commissioning of UL/FM approved Quartzoid Bulb Detector for K factor-80. Temp rating 68 deg C | Nos | 32
6 | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications
a | 80 NB | Mtr | 36
b | 65 NB | Mtr | 12
c | 50 NB | Mtr | 78
d | 40NB | Mtr | 42
e | 25NB | Mtr | 78
7 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope.
a | 150 mm NB | Mtr | 12
b | 80 mm NB | Mtr | 24
Q2 | FDA SYSTEM
1 | Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | Nos | 34
2 | Supply, erection, testing & commissioning of analogue addressable Manual Call point | Nos | 4
3 | Supply, erection, testing & commissioning of Hooter cum strobe | Nos | 4
4 | Supply, erction, testing & commissioning of analogue addressable Control Module | Nos | 4
5 | Supply, erection, testing & commissioning of analogue addressable Isolator Module | Nos | 2
6 | Supply, erection, testing & commissioning of analogue addressable Monitor module | Nos | 2
7 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Loop cable) | Mtr | 240
8 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Power cable) | Mtr | 110
9 | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | Mtr | 240
TOTAL

## PRE TREATMENT CHEMICAL(PTC)
Annexure I
P.O. No. 317047 Dt. 24.11.23
Scope of Supply & Erection :
Sr No | Description | Unit | Qty | Supply |  | Erection
|  |  |  | Rate | Amount | Rate | Amount
R | PRE TREATMENT CHEMICAL (PTC)
R1 | HYDRANT SYSTEM
1 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope.
a | 150 mm NB | Mtr | 18
b | 80 mm NB | Mtr | 12
c | 25 mm NB | Mtr | 12
2 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts.
a | Size 150 mm NB | Nos | 2
3 | Supply, installation, testing and commissioning of CS Non return valve with companion flanges,nuts & bolts and gaskets.
a | Size 150 mm NB | Nos | 1
4 | Supply & installation of SS oblique type single headed Landing valve with 80 mm inlet and 63 mm outlet SS instantaneous male coupling with rubber cap and chain conforming to IS : 5290 including matching flanges, gasket, nuts and bolts complete. | Nos | 3
5 | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor.
a | Size 80 mm NB | Nos | 3
6 | Supply & installation of SS branch pipe with 20 mm nozzle conforming to IS : 903 complete | Nos | 3
7 | Supply & installation of 63 mm dia rubberized reinforced rubber line hose pipe in 15 m length conforming to IS : 636 Type II ISI marked with gunmetal male and female instantaneous coupling conforming to IS 903 wounded with 18 SWG copper wire complete | Nos | 6
8 | Supply & installation of MS Hose Box of fabricated from 16 SWG CRCA sheet double door with lockable arrangements to accommodate 2 RRL hose of 15 m length and one branch pipe painted white inside and red outside with one key. (750X600X250 mm) | Nos | 3
8 | Supply & installation of swinging type hose reel drum fabricated from 14 SWG CRCA sheets painted with red colour stove paint 2 coats over 1 coat of primer with 30 m long 20 mm dia rubber hose pipe with with SS self closing shut – off nozzle of 5 mm outlet fixed on wall. | Nos | 3
9 | Supply and installation of pressure gauge, 1/2 inch bottom entry, of suitable range with ball valves and other accessories. | Nos | 1
10 | Supply, installation of automatic 25 NB Air Release Valve | Nos | 1
11 | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends
a | Size 25NB | Nos | 5
12 | Supply & installation of 250ltr foam tank filled with 3% AFFF foam concentrate with foam making branch and pick up tube. | Nos | 1
R2 | FOAM WATER SPRAY SYSTEM
1 | Supply, erection , testing & commissioning of Deluge valve with dry pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 3/2 way Solenoid Valve, air filter regulator etc. & manual release unit. The valve shall be electro-pneumatic double inter lock system as per scheme drawing.
a | 150 mm NB | Nos | 1
2 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts.
a | 150 mm NB | Nos | 3
3 | Supply, installation, testing of Y- Strainer.
a | Size 150 mm NB | Nos | 1
4 | Supply,installation,testing and commissioning of Foam Sprinkler nozzle with necessary threaded fittings as per drawing. The sprinkler shall be Open Aspiration, Pendent type, K-42 with standard spray angle.End connection 1/2" NPT/BSP.UL/FM Approved.
a | Spray nozzle K factor -42 | Nos | 59
5 | Supply,installation and commissioning of UL/FM approved Quartzoid Bulb Detector for K factor-80. Temp rating 68 deg C | Nos | 59
6 | Supply, installation, testing and commissioning of Ratio Controller. | Nos
a | 150NB | Nos | 1
7 | Supply, installation, testing and commissioning of Foam bladder tank vertical type ,manufacturing as per ASME, section-VIII part- I. The bladder material shall be BUNA-N. The Bladder Tank shall be supplied along with all necessary valves, Hydraulically Operated Foam Concentrae Control Valve ,fittingss & instruments as per Technical data sheet attached with Tender documents.
a | Capacity of 2100 ltr. | Nos | 1
8 | Supply of AR-AFFF(3%) foam concentrate(PFOS/PFAS free) having sp. Gravity 1.0±.02 g/mlat 20⁰C , PH 7.0-8.5 & viscosity 1200 ±300 cps. | Ltr | 2100
9 | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications
a | 150 NB | Mtr | 12
b | 100 NB | Mtr | 18
c | 80 NB | Mtr | 24
d | 65 NB | Mtr | 24
e | 50 NB | Mtr | 18
f | 40NB | Mtr | 66
g | 25NB | Mtr | 284
10 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope.
a | 80 mm NB | Mtr | 24
b | 65 mm NB | Mtr | 12
c | 50 mm NB | Mtr | 18
R3 | AUTOMATIC SPRINKLER SYSTEM
1 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved red oxide primer and two coats of approved red enamel paint and welded joints complete with cutting and making good the complete with cutting and making good the walls, floors or any other surface
a | 80 mm NB | Mtr | 24
b | 65 mm NB | Mtr | 12
c | 50 mm NB | Mtr | 18
d | 40 mm NB | Mtr | 12
e | 25 mm NB | Mtr | 24
2 | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor.
a | Size 80 mm NB | Nos | 1
3 | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts.
a | Size 80 mm NB | Nos | 1
4 | Supply & fixing of paddle type Flow Switch | Nos | 1
5 | Supply,Fixing of Sprinkler Head Pendent type for K factor-80. Temp rating 68 deg C. UL/FM Approved. | Nos | 18
6 | Supply, installation of automatic 25 NB Air Release Valve | Nos | 1
7 | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends
a | Size 25NB | Nos | 2
b | Size 40NB | Nos | 1
8 | Supply,Erection and testing of Installation Control Valve complete with trims & gong.
a | Size 80 mm NB | Nos | 1
R4 | FDA SYSTEM
1 | Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | Nos | 4
3 | Supply, erection, testing & commissioning of IR Detector | Nos | 7
4 | Supply, erection, testing & commissioning of analogue addressable Manual Call point | Nos | 4
5 | Supply, erection, testing & commissioning of Hooter cum strobe | Nos | 4
6 | Supply, erction, testing & commissioning of analogue addressable Control Module | Nos | 3
7 | Supply, erection, testing & commissioning of analogue addressable Isolator Module | Nos | 2
8 | Supply, erection, testing & commissioning of analogue addressable Monitor module | Nos | 9
9 | Supply, erection, testing & commissioning of 6 Watt Ceiling mounted Speakers | Nos | 9
10 | Providing & fixing 100Watt Amplifier with necessary accessories. | Nos | 1
11 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Loop cable) | Mtr | 256
12 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Power cable) | Mtr | 127
13 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Speaker cable) | Mtr | 140
14 | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | Mtr | 256
R5 | PA SYSTEM
1 | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | Nos | 1
2 | 15 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | Nos | 3
3 | Rack Mounted 125 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | Nos | 1
4 | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | Mtr | 90
5 | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | Nos | 1
6 | Paging Loudspeaker | Nos | 1
TOTAL

## FINISHED GOOD 1
Annexure I
P.O. No. 317047 Dt. 24.11.23
Scope of Supply & Erection :
Sr No | Description | Unit | Qty | Supply |  | Erection
|  |  |  | Rate | Amount | Rate | Amount
S | FINISH GODOWN 1
S1 | HYDRANT SYSTEM
1 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope.
a | 100 mm NB | Mtr | 120
b | 80 mm NB | Mtr | 30
c | 25 mm NB | Mtr | 12
2 | Supply & installation of SS oblique type single headed Landing valve with 80 mm inlet and 63 mm outlet SS instantaneous male coupling with rubber cap and chain conforming to IS : 5290 including matching flanges, gasket, nuts and bolts complete. | Nos | 6
3 | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor.
a | Size 80 mm NB | Nos | 6
4 | Supply & installation of SS branch pipe with 20 mm nozzle conforming to IS : 903 complete | Nos | 6
5 | Supply & installation of 63 mm dia rubberized reinforced rubber line hose pipe in 15 m length conforming to IS : 636 Type II ISI marked with gunmetal male and female instantaneous coupling conforming to IS 903 wounded with 18 SWG copper wire complete | Nos | 12
6 | Supply & installation of MS Hose Box of fabricated from 16 SWG CRCA sheet double door with lockable arrangements to accommodate 2 RRL hose of 15 m length and one branch pipe painted white inside and red outside with one key. (750X600X250 mm) | Nos | 6
7 | Supply & installation of swinging type hose reel drum fabricated from 14 SWG CRCA sheets painted with red colour stove paint 2 coats over 1 coat of primer with 30 m long 20 mm dia rubber hose pipe with with SS self closing shut – off nozzle of 5 mm outlet fixed on wall. | Nos | 6
8 | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends
a | Size 25NB | Nos | 6
S2 | FDA SYSTEM
1 | Supply, erection, testing & commissioning of analogue addressable Manual Call point | Nos | 8
2 | Supply, erection, testing & commissioning of Hooter cum strobe | Nos | 8
3 | Supply, erction, testing & commissioning of analogue addressable Control Module | Nos | 3
4 | Supply, erection, testing & commissioning of analogue addressable Isolator Module | Nos | 3
5 | Supply, erection, testing & commissioning of analogue addressable Monitor module | Nos | 2
6 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Loop cable) | Mtr | 330
7 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Power cable) | Mtr | 354
8 | Supply, erection, testing & commissioning of 6 Watt Ceiling mounted Speakers | Nos | 77
9 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Speaker cable) | Mtr | 640
10 | Supply, installation, testing and commissioning of aspiration detector with CMOS imager combined with multiple photodiode for reliable very early warning in a wide range of environments with minimal nuisance alarms. The detector should have 4 pipe inlet and min 100m pipelength support per inlet.The detector should have Smart on-board filter retains dust count and remaining filter life for predictable maintenance& coverage area of min 5000 Sq. | Nos | 4
11 | Supply,Installation,Testing & Commissioning of UL/VDS listed CPVC Pipe 25 mm Dia & Pipe Accessories for the Aspiration detection. | Mtr | 840
12 | Providing & fixing 600Watt Amplifier with necessary accessories. | Nos | 1
13 | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | Mtr | 640
S3 | WATER CURTAIN
1 | Supply, erection and testing of heavy grade(class-C) pipes conforming to IS-1239 / IS-3589 including all fittings viz. tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer and structural steels for pipe supports. Hanger support with anchor fasteners and clamps shall be supplied to fix the pipes on ceiling wall etc. including supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners) as per specification. Cutting of floors, walls etc and making it good after erection of pipes shall be of vendor's scope. Necessary painting with 2 coats of primer and 2 coats of synthetic enamel paints to be done and supply of paints shall be with vendor's scope.
a | 65 NB | Mtr | 384
b | 150 NB | Mtr | 130
(Make-TATA,JINDAL)
2 | Supply, erection , testing & commissioning of Deluge valve with wet pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 2 way Solenoid Valve, air filter regulator etc. & manual release unit.
a | Size 150 NB | Nos | 1
3 | Providing & fixing Cast Iron Y Strainer.
a | Size 150 NB | Nos | 1
4 | Supply & fixing of SS Water Curtain Nozzle (K>=71)UL/FM Approved. | Nos | 125
5 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts.
a | Size 150 NB | Nos | 3
S4 | PA SYSTEM
1 | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | Nos | 1
2 | 30 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | Nos | 6
3 | Rack Mounted 200 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | Nos | 1
4 | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | Mtr | 260
5 | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | Nos | 1
6 | Paging Loudspeaker | Nos | 1
TOTAL

## FINISHED GOOD 2
Annexure I
P.O. No. 317047 Dt. 24.11.23
Scope of Supply & Erection :
Sr No | Description | Unit | Qty | Supply |  | Erection
|  |  |  | Rate | Amount | Rate | Amount
T | FINISH GODOWN 2
T1 | FDA SYSTEM
1 | Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | Nos | 34
2 | Supply, erection, testing & commissioning of analogue addressable Manual Call point | Nos | 4
4 | Supply, erection, testing & commissioning of Hooter cum strobe | Nos | 4
5 | Supply, erction, testing & commissioning of analogue addressable Control Module | Nos | 4
6 | Supply, erection, testing & commissioning of analogue addressable Isolator Module | Nos | 1
7 | Supply, erection, testing & commissioning of analogue addressable Monitor module | Nos | 2
8 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Loop cable) | Mtr | 240
9 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Power cable) | Mtr | 110
10 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Speaker cable) | Mtr | 32
11 | Supply, installation, testing and commissioning of aspiration detector with CMOS imager combined with multiple photodiode for reliable very early warning in a wide range of environments with minimal nuisance alarms. The detector should have 4 pipe inlet and min 100m pipelength support per inlet.The detector should have Smart on-board filter retains dust count and remaining filter life for predictable maintenance& coverage area of min 5000 Sq. | Nos | 2
12 | Supply,Installation,Testing & Commissioning of UL/VDS listed CPVC Pipe 25 mm Dia & Pipe Accessories for the Aspiration detection. | Mtr | 270
13 | Providing & fixing 100Watt Amplifier with necessary accessories. | Nos | 1
14 | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | Mtr | 240
T2 | PA SYSTEM
1 | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | Nos | 1
2 | 15 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | Nos | 6
3 | Rack Mounted 125 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | Nos | 1
4 | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | Mtr | 140
5 | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | Nos | 1
6 | Paging Loudspeaker | Nos | 1
TOTAL

## GARBAGE YARD
Annexure I
P.O. No. 317047 Dt. 24.11.23
Scope of Supply & Erection :
Sr No | Description | Unit | Qty | Supply |  | Erection
|  |  |  | Rate | Amount | Rate | Amount
U | GARBAGE YARD
U1 | FOAM WATER SPRAY SYSTEM
1 | Supply, erection , testing & commissioning of Deluge valve with dry pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 3/2 way Solenoid Valve, air filter regulator etc. & manual release unit. The valve shall be electro-pneumatic double inter lock system as per scheme drawing.
a | 80 mm NB | Nos | 1
2 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts.
a | 80 mm NB | Nos | 3
3 | Supply, installation, testing and commissioning of Y-Strainer.
a | 80 mm NB | Nos | 1
4 | Supply,installation,testing and commissioning of Foam Sprinkler nozzle with necessary threaded fittings as per drawing. The sprinkler shall be Open Aspiration, Pendent type, K-42 with standard spray angle.End connection 1/2" NPT/BSP.UL/FM Approved.
a | Spray nozzle K factor -42 | Nos | 25
6 | Supply, installation, testing and commissioning of Ratio Controller. | Nos
a | 80 mm NB | Nos | 1
7 | Supply, installation, testing and commissioning of Foam bladder tank vertical type ,manufacturing as per ASME, section-VIII part- I. The bladder material shall be BUNA-N. The Bladder Tank shall be supplied along with all necessary valves, Hydraulically Operated Foam Concentrae Control Valve ,fittingss & instruments as per Technical data sheet attached with Tender documents.
a | Capacity of 500 ltr. | Nos | 1
8 | Supply of AR-AFFF(3%) foam concentrate(PFOS/PFAS free) having sp. Gravity 1.0±.02 g/mlat 20⁰C , PH 7.0-8.5 & viscosity 1200 ±300 cps. | Ltr | 500
9 | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications
a | 80 mm NB | Mtr | 12
b | 65 mm NB | Mtr | 6
c | 50 mm NB | Mtr | 6
d | 40 mm NB | Mtr | 18
e | 25 mm NB | Mtr | 66
10 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope.
a | 80 mm NB | Mtr | 45
U2 | FDA SYSTEM
1 | Supply, erection, testing & commissioning of IR Detector | Nos | 2
2 | Supply, erection, testing & commissioning of analogue addressable Manual Call point | Nos | 1
3 | Supply, erection, testing & commissioning of Hooter cum strobe | Nos | 1
5 | Supply, erction, testing & commissioning of analogue addressable Control Module | Nos | 1
6 | Supply, erection, testing & commissioning of analogue addressable Isolator Module | Nos | 2
7 | Supply, erection, testing & commissioning of analogue addressable Monitor module | Nos | 3
8 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Loop cable) | Mtr | 72
9 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Power cable) | Mtr | 26
10 | Supply, erection, testing & commissioning of 6 Watt Ceiling mounted Speakers | Nos | 4
11 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Speaker cable) | Mtr | 36
12 | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | Mtr | 72
U3 | PA SYSTEM
1 | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | Nos | 1
2 | 6 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | Nos | 4
3 | Rack Mounted 125 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | Nos | 1
4 | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | Mtr | 50
5 | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | Nos | 1
6 | Paging Loudspeaker | Nos | 1
TOTAL

## RESIN TANK
Annexure I
P.O. No. 317047 Dt. 24.11.23
Scope of Supply & Erection :
Sr No | Description | Unit | Qty | Supply |  | Erection
|  |  |  | Rate | Amount | Rate | Amount
V | RESIN TANK
V1 | FOAM GENERATOR
1 | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications
a | 150 NB | Mtr | 75
b | 100 NB | Mtr | 106
2 | Supply, erection , testing & commissioning of Deluge valve with dry pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch,dry pilot actuator, air filter regulator etc. & manual release unit.
a | Size 150 NB | Nos | 2
b | Size 100 NB | Nos | 2
3 | Providing & fixing Cast Iron Y Strainer.
a | Size 150 NB | Nos | 2
b | Size 100 NB | Nos | 2
4 | Supply & fixing of SS-304 FOAM GENERATOR with Minimum flow 120lpm | Nos | 6
5 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts.
a | Size 150 NB | Nos | 6
b | Size 100 NB | Nos | 6
6 | Supply, installation, testing and commissioning of Atmospheric Foam tank vertical type ,manufacturing as per ASME, section-VIII part- I. Tank shall be supplied along with all necessary valves, fittingss & instruments as per Technical data sheet attached with Tender documents.
a | Capacity of 250 ltr. | Nos | 2
b | Capacity of 150 ltr. | Nos | 2
7 | Supply of AR-AFFF(3%) foam concentrate (PFOS/PFAS free) having sp. Gravity 1.0±.02 g/mlat 20⁰C , pH 7.0-8.5 & viscosity 1200 ±300 cps. | Ltr | 800
8 | Supply, installation, testing and commissioning of Inline Inductor
a | 150NB | Nos | 2
b | 100 NB | Nos | 2
V2 | MEDIUM VELOCITY WATER SPRAY SYSTEM
1 | Supply, erection , testing & commissioning of Deluge valve with wet pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 3/2 way Solenoid Valve, air filter regulator etc. & manual release unit. The valve shall be electro-pneumatic type.
a | 100 NB | Mtr | 1
b | 80 NB | Mtr | 3
2 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts.
a | 100 NB | Mtr | 3
b | 80 NB | Mtr | 9
3 | Y- Strainer
a | 100 NB | Mtr | 1
b | 80 NB | Mtr | 3
4 | Supply,installation and commissioning of UL/FM approved Medium Velocity Water Spray Nozzle. UL/FM Approved.
a | MVWS nozzle K factor 18, spray angle 100⁰ | Nos | 91
5 | Supply,installation and commissioning of UL/FM approved Quartzoid Bulb Detector for K factor-80. Temp rating 68 deg C | Nos | 91
6 | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications
a | 100 NB | Mtr | 14
b | 80 NB | Mtr | 60
c | 65 NB | Mtr | 210
7 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope.
a | 100 mm NB | Mtr | 24
b | 80 mm NB | Mtr | 86
c | 25 mm NB | Mtr | 230
8 | Supply, erction, testing & commissioning of analogue addressable Control Module | Nos | 4
9 | Supply, erction, testing & commissioning of analogue addressable Monitor Module | Nos | 4
V3 | FDA SYSTEM
1 | Supply, erection, testing & commissioning of analogue addressable Monitor module | Nos | 9
2 | Supply, erection, testing & commissioning of IR Detector | Nos | 9
3 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Loop cable) | Mtr | 60
4 | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | Mtr | 62
TOTAL

## EMULSION PLANT
Annexure I
P.O. No. 317047 Dt. 24.11.23
Scope of Supply & Erection :
Sr No | Description | Unit | Qty | Supply |  | Erection
|  |  |  | Rate | Amount | Rate | Amount
W | EMULSION PLANT
W1 | FDA SYSTEM
1 | Supply, installation, testing and commissioning of aspiration detector with CMOS imager combined with multiple photodiode for reliable very early warning in a wide range of environments with minimal nuisance alarms. The detector should have 4 pipe inlet and min 100m pipelength support per inlet.The detector should have Smart on-board filter retains dust count and remaining filter life for predictable maintenance& coverage area of min 5000 Sq. | Nos | 2
2 | Supply,Installation,Testing & Commissioning of UL/VDS listed CPVC Pipe 25 mm Dia & Pipe Accessories for the Aspiration detection. | Mtr | 212
3 | Supply, erection, fabrication, testing and commission of VOC detector with range of 1 – 1000 ppm isobutylene equivalent.and following accessoriesa) DigiPID internal dust filter (Pack of 5) b) Waterproof Filter Assy, RAEGuard2 PID, Pack of 5 c) DigiPID Teflon UV electrode shield pack of 10 d) DigiPID Dust Cover e) Air Drying Pre Filter Kit f) DigiPID external water trap filter (Pack of 5) | Nos | 3
4 | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | Mtr | 18
W2 | PA SYSTEM
1 | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | Nos | 1
2 | 30 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | Nos | 4
3 | Rack Mounted 125 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | Nos | 1
4 | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | Mtr | 150
5 | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | Nos | 1
6 | Paging Loudspeaker | Nos | 1
TOTAL

## PLC AUTOMATION
Annexure I
P.O. No. 317047 Dt. 24.11.23
Scope of Supply & Erection :
Sr No | Description | Unit | Qty | Supply |  | Erection
|  |  |  | Rate | Amount | Rate | Amount
X | PLC AUTOMATION
1 | SUPPLY & INSTALLATION OF PLC BASED DV CONTROL PANEL FOR FOAM SPRINKLER SYSTEM AND FIRE WATER PUMPING SYSTEM INTERGRATION PANEL WITH PLC.
Supply,Installation,Termination of cable,Testing and Commissioning of PLC Based Deluge Valve Control Panel with accessories. The panel should have local push botton switched for emergency operation from panel.Panel and associated accessories shall be designed to withstand environmental conditions at site.Panel in open areas shall be weatherproof to IP-65 as per IS/ IEC-60529. Canopy/Shed of adequate sizes shall be provided for each panel to protect from weather, the cost of the same shall be included in the panel cost.No extra payment shall be made for providing fixture , fittings & accessories.
PLC Based DELUGE VALVE CONTROL PANEL should contain the following:- 1. Programmable Logic Controller. 2.Solid State type or microprocessor based programmable type Alarm Annunciator with sounder. 3.UPS. 4.Cables (Power & Control)
Specification of Programmable Logic Controller (PLC) : 1.Input Power: 24vdc,Redundant Supply. 2.Application capabilities with up to 7 expansion I/O modules for a maximum of 256 discrete I/O. 3.Up to 6 embedded 100 kHz highspeed counters (on controllers with dc inputs) 4.2 Serial ports with DF1/ DH485/Modbus RTU/DNP3/ASCII protocol support. 5.Ethernet port provides you with EtherNet/IP, DNP3 over IP and Modbus TCP/IP protocol support as well as web server and email capabilities. 6.Built-in LCD with backlight allows you to view controller and I/O status, and provides a simple interface for messages, bit / integer monitoring and manipulation. 9.Memory:non-volatile battery backed RAM. 10.online editing:yes. 11.Operating Temp.:-20°C...+60°C. 12.Storage Temp:-40°C (or -30°C)...+85°C.
Specification of Solid State type or microprocessor based programmable type Alarm Annunciator with sounder: Window display shall be back lighted incandescent lamps or cluster LED type integral power supply.
Specification of UPS: 1.Alarm Condition: 1 hours. 2.Standalone Condition: 4 Hours.
a | For 22 nos. Deluge Valve IO point 3 nos (22 W + 3 S)-SOLVENT PLANT | Set | 2
b | For 3 nos. Deluge Valve IO point 1 nos (3 W + 1 S)-RESIN PLANT | Set | 1
c | For 2 nos. Deluge Valve IO point 1 nos (2 W + 1 S) -,MONOMER & STYRENE | Set | 1
d | For 4 nos. Deluge Valve IO point 1 nos(4 W + 1 S) -WATER BASED PLANT | Sets | 2
e | For 2 nos. Deluge Valve IO point 1 nos (2 W + 1 S)-SUBSTATION BUILDING | Set | 1
f | For 1 nos. Deluge Valve IO point 1 nos (1 W + 1 S) -,SOFA AREA | Set | 1
g | For 1 nos. Deluge Valve IO point 1 nos (1 W + 1 S)-PTC | Set | 1
h | For 1 nos. Deluge Valve IO point 1 nos (1 W + 1 S) -,FG-1 | Set | 1
i | For 1 nos. Deluge Valve IO point 1 nos(1 W + 1 S) -,MONOMER COLD ROOM | Set | 1
j | For 2 nos. Deluge Valve IO point 1 nos (2 W + 1 S) - DEG & MEG TANK FIRM | Set | 1
k | For 8 nos. Deluge Valve IO point 1 nos (8 W + 1 S) - resin TANK FIRM foam generator & MVWS. | Set | 1
l | For 4 nos. Deluge Valve IO point 1 nos(4 W + 1 S) - SOFA TANK area foam generator. | Set | 1
m | For 2 nos. Deluge Valve IO point 1 nos(2 W + 1 S) - styrene & monomer tank area foam generator. | Set | 1
n | For 2 nos. Deluge Valve IO point 1 nos (2 W + 1 S) - raw material curtain. | Set | 1
o | For 2 Nos. Electric Motor driven Pump,2 Nos. of Diesel Engine driven Pump,2 nos. of Jockey Pumps, Air Compressor running-"ON" & "OFF" Condition. | Set | 1
2 | SUPPLY & ERECTION OF HMI PC
| Supply,Installation and Commissioning of HMI PC with all accessories complete in all respect and UPS of suitable capacity capable supply power for atleast 1 hour in Alarm Condition & 4 hours in Standalone Condition. (Two Sets of HMI PC shall be provided in two different Locations, one at Control Room/Security Cabin and another at Admin Block) | Sets | 2
Specification of HMI PC: 1.Site specific HMI software and provision for stimulation DV System. 2.HMI Software for one user with paper licence. 3.Harddisk:1TB. 4.RAM: 8 GB. 5.Display:21" LED. 6.OS: windows lateset professional version. 7.DVD drive ± R/RW 16X. 8.Processor 32 bit Intel Xeon Quad Core Processor with 2.8 GHz. 9.Graphics NVIDIA Quadro 600 with 1GB video memory. 10.event history:min 1 month.
3 | Optical Fiber Cable (OFC)
| Specification of OFC Cable : Cable Description : 6F LT-SM/MM Single sheath armoured O.F. cable with HDPE encasing pipe. | RM | 1400
4 | Supply, Installation and commissioning of SCADA (Supervisory Control & Data Acquisition) based PLC Panel for integrating with various PLCs and other automations, | SET | 1
TOTAL

## PANEL SUPPRESSION SYSTEM
Annexure I
P.O. No. 317047 Dt. 24.11.23
Scope of Supply & Erection :
Sr No | Description | Unit | Qty | Supply |  | Erection
|  |  |  | Rate | Amount | Rate | Amount
Y | PANEL SUPPRESSION SYSTEM
1 | FIRETRACE Direct Low Pressure (DLP) Novec 1230 4 Kgs. System, supplied complete with differential pressure valve, Novec 1230, Pressure Gauage,with panel mounting bracket. (CE Approved) | Nos | 32
2 | FIRETRACE Direct Low Pressure (DLP) Novec 1230 2 Kgs. System, supplied complete with differential pressure valve, Novec 1230, Pressure Gauage,with panel mounting bracket. (CE Approved) | Nos | 7
3 | FIRETRACE Direct Low Pressure (DLP) Novec 1230 1 Kgs. System, supplied complete with differential pressure valve, Novec 1230, Pressure Gauage,with panel mounting bracket. (CE Approved) | Nos | 3
4 | Pressure Switch | Nos | 42
5 | End of line Adaptor with pressure Gauge | Nos | 42
6 | Firetrace 4/6 Linear Pneumatic Heat detection tube kit, (Standard) | Mtr | 610
7 | 6mm End Plug | Nos | 84
8 | 6mm Equal TEE | Nos | 84
9 | Master Control Unit | Nos | 42
10 | Supply, erection, testing & commissioning of analogue addressable Monitor module | Nos | 42
11 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Loop cable) | Mtr | 3200
12 | Providing & fixing of modular type clean agent extinguisher.
a | 10 KG Extinguisher | Nos | 6
b | 5 KG Extinguisher | Nos | 4
TOTAL

## GAS LEAK DETECTION
Annexure I
P.O. No. 317047 Dt. 24.11.23
Scope of Supply & Erection :
Sr No | Description | Unit | Qty | Supply |  | Erection
|  |  |  | Rate | Amount | Rate | Amount
Z | GAS LEAK DETECTION
Z1
1 | Supply, erection, fabrication, testing and commission of VOC detector with range of 1 – 1000 ppm isobutylene equivalent.and following accessoriesa) DigiPID internal dust filter (Pack of 5) b) Waterproof Filter Assy, RAEGuard2 PID, Pack of 5 c) DigiPID Teflon UV electrode shield pack of 10 d) DigiPID Dust Cover e) Air Drying Pre Filter Kit f) DigiPID external water trap filter (Pack of 5) | Nos | 5
2 | Supply, erection, fabrication, testing and commission of IR based LEL Detector, includes nylon weather protection. | Nos | 4
3 | Supply, erection, fabrication, testing and commission of Ex proof Hooter & Beacon. | Nos | 5
4 | Supply, erection, fabrication, testing and commission of Local Display (VOC monitoring) unit. | Nos | 1
5 | Supply, erection, fabrication, testing and commission of Micro-controller based, multi-channel monitoring and control of Gas Sensors 39 channel. | Nos | 1
6 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 3C x 2.5 mm2 Armoured | Mtr | 1600
TOTAL