## FIRE PUMP ROOM
BILL OF MATERIALS FOR BERGER PLANT, GOA
Date.-11.09.2023
SL NO | DESCRIPTION | UNIT | QTY | UNIT RATE | TOTAL RATE
A. | FIRE PUMP ROOM
FIRE WATER PUMPING SYSTEM
1 | Supply, erection, testing & commissioning of Electrical Motor driven main pump, centrifugal horizontal type, with gland packing capable of deliver 410 M3/HR at 110 MWC. The pump shall be coupled with TEFC motor of suitable KW with speed of 1450 RPM with all accessories and complete set shall mounted on common base frame. The quoted rate shall include fixing of coupling, coupling guard and foudation bolts etc. Civil foundation will be client's scope.(FOR HYDRANT SYSTEM) | Nos | 1 |  | 0
2 | Supply, erection, testing & commissioning of Electrical Motor driven main pump, centrifugal horizontal type, with gland packing capable of deliver 410 M3/HR at 110 MWC. The pump shall be coupled with TEFC motor of suitable KW with speed of 1450 RPM with all accessories and complete set shall mounted on common base frame. The quoted rate shall include fixing of coupling, coupling guard and foudation bolts etc. Civil foundation will be client's scope.(FOR SPRINKLER SYSTEM) | Nos | 1 |  | 0
3 | Supply, erection,testing & commissioning of diesel engine driven stand by pump, centrifugal horizontal type with gland packing and capable of delivering 410 M3/HR at 110 MWC. The pump shall be coupled to suitable HP of Diesel Engine radiator water cooled type having speed of 1500 RPM with all accessories including diesel engine control panel and complete set shall be mounted on common base frame.Other accessories viz Batteries & battery leads with stand, fuel tank(for 4 hrs operation) with stand and gauge glass, fuel piping with valves etc to be supplied. The quoted rate shall include radiator water cooling piping(if required), coupling guard and other standard accessories, RCC foundation(as recommended by manufacturer) and foundation bolts, etc, complete ( civil foundation shall be client's scope). | Nos | 2 |  | 0
4 | Supply, erection, testing & commissioning of electric motor driven Jockey Pump,centrifugal horizontal type capable to deliver 25 M3/HR at 110 MWC. The pump shall coupled to TEFC motor of suitable KW with speed of 2900 RPM with all accessories mounted on common base frame. | Nos | 2 |  | 0
0
5 | Supply, erection, testing & commissioning of compartmentalised common control panel for above pumps as per technical specification attached with this tender document. All components shall be housed in a common cubicals made of 16 swg. M.S. sheet with required stiffners(if required). The panel shall be powder coated of approved colour both inside and out side. The panel shall have both bottom and top cable entry provisions and panel shall be mounted on pedestal of 300mm height. | Nos | 1 |  | 0
0
6 | Supply, laying, testing & commissioning of FRLS, PVC outer sheath, steel armoured, aluminium / copper conductor, 1100 Volt Grade power cables with gland etc for above pumps. The cable shall be laid in tray / hume pipe / in trenches / on walls / floors etc as required. Cables laid out doors shall include the price of earth escavation providing brick and sand protection, refilling and compacting the earth. | Lot | 1 |  | 0
0
7 | GI earthing strips of 50mm x 6mm thick, strips shall run on floor / ceiling / walls, from pump to control panel with necessary accessories as required. | Mtr | 30 |  | 0
0
8 | 25 Sq.mm single core multistrand copper cable shall be run on floor / ceiling / walls, from the nearest earth bar to the pump control panel with necessary accessories as required. | Mtr | 40 |  | 0
0
9 | Supply & installation of dial type Pressure Gauge of suitable pressure range, fitted with dampner arrangement and isolation ball valve as shown in respective drawing. The diameter of dial shall be 150 mm preferably filled up with glyserine. All other necessary fittings to be supplied to erect the gauge on top of the riser. | Nos | 6 |  | 0
0
10 | Supply and installation of Pressure switches, SPDT type, of suitable range for pump sets with ball valves and other accessories. | Nos | 8 |  | 0
0
11 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600 with matching flanges complete with nuts & bolts. Pressure Class 150. |  |  |  | 0
a | Size 300 mm NB | Nos | 8 |  | 0
b | Size 250 mm NB | Nos | 4 |  | 0
c | Size 100 mm NB | Nos | 2 |  | 0
d | Size 80 mm NB | Nos | 2 |  | 0
0
12 | Supply, installation, testing and commissioning of CS Non return valve as per BS 1868 with companion flanges,nuts & bolts and gaskets. Pressure Class 150. |  |  |  | 0
a | Size 300 mm NB(Swing type) | Nos | 1 |  | 0
b | Size 250 mm NB(Swing type) | Nos | 4 |  | 0
c | Size 80 mm NB(Swing type) | Nos | 2 |  | 0
0
13 | Supply, installation, testing and commissioning of Rubber bellow. |  |  |  | 0
a | Size 300 mm NB | Nos | 3 |  | 0
b | Size 100 mm NB | Nos | 2 |  | 0
0
14 | Supply, installation, testing and commissioning of Bucket Strainer |  |  |  | 0
a | Size 300 mm NB | Nos | 2 |  | 0
0
15 | Supply, Installation, testing & commissioning of CS Globe Valve as per IS:9338(PN16 rating) complete including matching flanges, nuts & bolts complete. |  |  |  | 0
a | Size 150 mm NB | Nos | 2 |  | 0
0
16 | Supply, installation of automatic 25 NB Air Release Valve | Nos | 2 |  | 0
0
17 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. |  |  |  | 0
a | 350 mm NB x 7 mm thk | Mtr | 12 |  | 0
b | 300 mm NB x 7 mm thk | Mtr | 24 |  | 0
c | 250 mm NB x 7 mm thk | Mtr | 30 |  | 0
d | 200 mm NB x 7 mm thk | Mtr | 18 |  | 0
e | 150 mm NB | Mtr | 24 |  | 0
f | 100 mm NB | Mtr | 12 |  | 0
g | 80 mm NB | Mtr | 12 |  | 0
h | 25 mm NB | Mtr | 24 |  | 0
0
18 | Supply & installation of SS 4 way collecting head with 63 mm dia instantaneous type inlet 150 dia flanged outlet with built in check valve for fire brigade connection to fire reservoir (IS : 904). | Nos | 1 |  | 0
0
19 | Supply & installation of SS Fire Brigade Draw out connection with necessary foot valve (150NB) for reservoir. | Nos | 1 |  | 0
0
20 | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications |  |  |  | 0
a | 50 NB | Mtr | 800 |  | 0
0
21 | Supply and installation of double flanged vertical air vessel fabricated from M.S. Plate with dished ends (M.S. plate to be of required thickness to sustain the indicated test pressure), one standard pressure tight manhole, painted inside with bitumastic or anti-corrosive paint and outside with one coast of primer and two coats of synthetic enamel paint complete with approved quality of pressure switches, pressure gauge and all other required accessories to operate commonly main/sprinkler/diesel fire pump & jockey pump at drop of pressure, automatically at required pressure setting (Air vessel, pressure switch, pressure gauge, air release valve, piping and accessories to suit the pressure requirement of individual pressure zone) | nos. | 2 |  | 0
0
22 | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | Mtr | 500 |  | 0
| TOTAL= |  |  |  | 0