## Table 1
MIRAJ ENGINEERING SERVICES PVT. LTD.
BOQ - ELECTRICAL AND INSTRUMENTATION WORKS FOR IOCL MEGHALAYA
SL. NO. | DESCRIPTION | UNIT | QTY.
ELE | PART A - SUPPLY OF ELECTRICAL ITEMS
1 | H POLE STRUCTURE
1.1 | Design and supply of H-pole Structure for 11 KV Incoming Power Supply with Gang operated isolator, D.O. fuse with base, lightning arrestors, Insulator, earthing, construction of earth Pits, fencing, gate, gravel laying, padlocking, signages including all civil works for 11 KV Supply. The design shall be in line with Electricity board guidelines. | Set | 1
2 | 11 KV indoor VCB Panel
2.1 | 11 KV, 630 A, VCB panel indoor type comprising of metering and protection system including numerical relay, auxiliary relay, CTs, PTs , indication lamp, switches along with Weather proof double compression Ni plated brass cable gland and crimping type cable lugs for all incoming and outgoing cables and as per specfication.. | No. | 1
3 | POWER TRANSFORMER AND LIGHTING TRANSFORMER
3.1 | 500 KVA, 11KV/433V, Dyn11, AN type with off load tap changer power transformer complete with all accessories as per attached specifications & DS. | No. | 1
3.2 | 200KVA, 415V/433V, Dyn1, natural air cooled Dry type Lighting transformer as per attached specifications & DS. | No. | 1
4 | MV/LV SWITCH BOARDS/ PANELS
4.1 | PMCC: 415V, 3phase, 4 wire, 50 Hz, 800A, 50 KA for 1second, double front fully draw out type PMCC comprising of ACBs, CTs/PTs, relays, indicating lamps etc. as per attached SLDs, specifications & DS. | No. | 1
4.2 | MLDB: 415V, 3phase, 4 wire, 50 Hz, 400A, 25KA for 1second MLDB including as per attached SLD, specifications & DS. | No. | 1
4.3 | Fire water MCC: 415V, 3phase, 4 wire, 50 Hz, 400A, 50KA for 1second MCC including as per attached SLD, specifications & DS. | No. | 1
4.4 | CAPACITOR PANEL : 415V, 3Ph-N, 50Hz, 50KA for 1second, 250KVAR capacitor panel with capacitors 2X75, 1X50, 2X25 KVAR) and APFC relay, protections, filters etc. as per attached SLD, specifications & DS including weather proof double compression Ni plated brass cable glands and lugs for all incoming and outgoing feeders. | No. | 1
5 | LDB and SUB-LDB
5.1 | LDB / LP, W eatherproof, IP 65, incomer 63A, 3 Phase, 4 wire, 3 Way LDB, 10kA for 1 sec with RCBO | No. | 1
5.2 | LDB / LP, W eatherproof, IP 65, incomer 63A, 3 Phase, 4 wire, 6 Way LDB, 10kA for 1 sec with RCBO | No. | 1
5.3 | LDB / LP, Outdoor type, Flame proof (FLP) Type, IP class suitable for FLP and minimum protection shall be IP-65, incomer 63A, 3 Phase, 4 wire, 3 Way LDB, 10kA for 1 sec with RCBO | No. | 5
5.4 | LDB / LP, Outdoor type, Flame proof (FLP) Type, IP class suitable for FLP and minimum protection shall be IP-65 , incomer 63A, 3 Phase, 4 wire, 6 Way LDB, 10kA for 1 sec with RCBO | No. | 1
5.5 | UPS DB - 230V, 50Hz,Outdoor type, Flame proof (FLP) Type, IP class suitable for FLP and minimum protection shall be IP-65, incomer 63A, 3 Phase, 4 wire, 3 Way LDB, 10kA for 1 sec with RCBO | No. | 1
5.6 | Feeder Pillar for street Lighting . 415V, 3Ph, 50Hz, Flame proof (IP class suitable for FLP and minimum protection shall be IP-65) sheet steel enclosure column/structural mounted, with photovoltic cell based control with A/M selector switch, start/stop PB, indicating lamps etc. with 3mm thick FRP canopy and side cover of the following incoming and outgoing feeders: i) 1no.-Incomer 63A, 3 phase RCBO 30 mA ii) 3nos.-O/G 16A TPN MCB | No. | 1
5.7 | PDB at outdoor location . 415V, 3Ph, 50Hz, W eatherproof and Flame proof (IP class suitable for FLP and minimum protection shall be IP-65) sheet steel enclosure column/structural mounted, start/stop PB, indicating lamps etc. with 3mm thick FRP canopy and side cover of the following incoming and outgoing feeders: i) 1no.-Incomer 100A TPN MCCB ii) 5nos.-O/G 32A TPN MCCB One outgoing shall be provided with photovoltic cell based control with A/M selector switch, start/stop PB, indicating lamps etc to feed the street light. | No. | 1
6 | BATTERY CHARGER WITH BATTERY & DC DB
6.1 | 110V, 10A BATTERY CHARGER consisting of dual float cum boost charger and Ni-Cd type battery (43AH) with two hour back up capacity as per attached specifications & DS. | No. | 1
6.2 | DC DISTRIBUTION BOARD: 110V DC, 2 wire 63A DC Distribution Board fed by duel float cum boost charger as per attached SLD, specifications & DS. Incomer: 63A DP MCB Outgoing: 15nos. 16A DP MCB | No. | 1
7 | LIGHTING FIXTURES & ACCESSORIES
7.1 | Supply of Flameproof lighting fixtures, Lamps & Accessories as per attached specification. (All Lighting fixtures shall be provided with required no. of FLP double compression stainless steel cable glands and FLP stopping plug and control gear boxes etc. All fixtures shall have inbuilt JBs for loop in loop out facility of 3Cx2.5 sqmm Cu lighting cables)
| 230 Volt AC, 40W Well glass Flameproof Ex'd',LED lighting fixtures and all other accessories | Nos. | 135
7.2 | Supply of weatherproof lighting fixtures, Lamps & Accessories as per attached specification. (All Lighting fixtures shall be provided with required no. of double compression stainless steel cable glands and stopping plug. All control gear boxes shall be provided with 3mm thick FRP canopy with side cover. .All fixtures shall have inbuilt JBs for loop in loop out facility of 3Cx2.5 sqmm Cu lighting cables)
| 230 Volt AC, 40W Well glass weatherproof ,LED lighting fixtures and all other accessories | Nos. | 22
8 | JUNCTION BOX
8.1 | 240 Volt AC, 16 A, Cast Aluminium Flameproof Ex'd' (Zone-1, IIA / IIB) 4-way, 125 mm (minimum) internal dimensions junction box with terminals block suitable for 2.5 sq.mm along with flameproof double compression Ni plated brass cables glands for all incoming and outgoing cables,PVC shroud and other accessories. | Nos. | 45
8.2 | 240 Volt AC, 16 A, Cast Aluminium weatherproof 4-way, 125 mm (minimum) internal dimensions junction box with terminals block suitable for 2.5 sq.mm along with weatherproof double compression Ni plated brass cables glands for all incoming and outgoing cables,PVC shroud and other accessories. | Nos. | 18
8.3 | JUNCTION BOXES FOR PUMP MOTOR (WEATHER PROOF, FLAME PROOF): Design, Supply, Installation, Testing and Commissionong of following 415V, 3P, Industrial type, W eatherproof, Flame proof “Ex-d” (suitable for hazardous area of gas group IIA/IIB, temperature class T3 and Zone-1), IP 65 suitable for Wall / Column / Structure mounting Including cabling from JB to terminal box for Star-Delta pump motor having different terminal for star and delta connection. All JBs shall be made up of cast Aluminium alloy (LM6 grade) with Canopy of 14 gauge CRCA sheet with side cover. JBs shall confirm to specification/data sheet of tender document. Junction Boxes shall be complete with busbar of suitable rating, support insulator, suitable for 2 nos. of 1RX 3.5 C X 150 Sqmm of Incoming cable size and 2 nos. of 1RX 3.5 C X 95 Sqmm of outgoing cable size XLPE insulated, extruded PVC inner & outer sheathed, FRLS, Armoured cables & shall be supplied along with FLP type double compression, Ni plated brass cable glands, lugs & plugs. However, exact cable sizes shall be indicated during drawing approval only. | Nos. | 1
9 | RECEPTACLES
9.1 | Supply of flameproof Interlocking type switch sockets and plugs of following ratings as per attached specifications. All switch sockets shall be provided with 3mm thick FRP canopy with side cover and required no. of FLP double compression stainless steel cable glands and FLP stopping plug.
| i) 415V, 5-pin, 63A flame proof switch socket and plug | Nos. | 4
| ii) 240V, 3-pin, 16A/5A flame proof switch socket and plug | Nos. | 6
9.2 | Supply of weatherproof Interlocking type switch sockets and plugs of following ratings as per attached specifications. All switch sockets shall be provided with 3mm thick FRP canopy with side cover and required no. of double compression stainless steel cable glands and stopping plug.
| i) 415V, 5-pin, 63A weatherproof switch socket and plug | Nos. | 2
| ii) 240V, 3-pin, 16A/5A weatherproof switch socket and plug | Nos. | 2
10 | RIGID/ FLEXIBLE CONDUIT
Supply of PVC rigid conduit of min. 2mm thick wall, heavy duty type as per IS (with bends, reducers, couplers etc.) of following sizes:-
10.1 | 25 mm Dia. PVC Rigid Conduit | m | 50
10.2 | 50 mm Dia. PVC Rigid Conduit | m | 150
10.3 | 75 mm Dia. PVC Rigid Conduit | m | 50
Supply of following PVC flexible conduit of min. 2mm thick wall, heavy duty type & as per IS: 2509.
10.4 | 25 mm Dia PVC Flexible Conduit | m | 425
11 | Lighting Cable
| 0.6/1 kV grade 3C X 2.5 Sqmm Cu XLPE insulated FRLS PVC sheathed Lighting Cable | m | 1800
12 | LIGHTING POLES
| Supply of 9.5 Mtr lighting pole (polygonal type) for base mounting complete with all accessories like MCB & terminal block, JB (as applicable), Zinc passivated hardware for fixtures support & pole support, cable protection pipe with earthing rod/ wire as applicable, clamps, nuts, bolts, etc. | Nos. | 6
13 | HIGH MAST LIGHTING TOWER
| Civil & Structural design, engineering & supply of hot dip galvanised High Mast lighting tower (30 m height) including all accessories for High Mast like 24 nos. of High mast lantern Carraige, 16 nos. of 350 watt LED fixture with lamp, head frame, stainless steel rope, double drum winch, Flameproof junction boxes, Flameproof plugs and sockets, Flameproof feeder pillar, galvanised lantern carrier arrangement, cables and cable accessories control panel for feeder pillar etc. as per specification, data sheet and direction of Engineer- in-charge ingincluding supply of commissioning and 2 years O&M spares. | Nos. | 4
14 | SUPPLY OF HT/ LT CABLES AS PER ENCLOSED SPECIFICATION
11 KV(UE) Grade Cables as per typical specifications ; XLPE insulated; PVC Sheathed; Armoured Aluminium Conductor Cables of Following Sizes As Per Is:1554 (Part-I), IS 7098 Part I & IS 1225-Latest Version and Sealed properly with Pvc Caps of following size:-
14.1 | 3C x 240 sqmm (AL) | m | 250
1.1KV(E) XLPE insulated, FRLS, PVC sheathed aluminium/copper conductor, 1.1 kV grade armoured cable conforming to IS:7098, as per approved make AS PER ENCLOSED SPECIFICATIONS
14.2 | 1C x 400, Sqmm XLPE AL | m | 1010
14.3 | 3.5C x 150, Sqmm XLPE AL | m | 100
14.4 | 3.5C x 95, Sqmm XLPE AL | m | 500
14.5 | 3.5C X 50, Sqmm XLPE AL | m | 3000
14.6 | 4C X 25, Sqmm XLPE AL | m | 6800
14.7 | 4C X 16, Sqmm XLPE AL | m | 600
14.8 | 4C X 10, Sqmm XLPE AL | m | 100
14.9 | 4C X 6, Sqmm XLPE AL | m | 8000
14.1 | 4C X 4, Sqmm XLPE AL | m | 3100
14.11 | 4C X 2.5, Sqmm XLPE AL | m | 2200
14.12 | 3C X 6, Sqmm XLPE AL | m | 400
14.13 | 3C X 2.5, Sqmm XLPE AL | m | 100
14.14 | 2C X 4, Sqmm XLPE AL | m | 200
14.15 | 2C X 16, Sqmm XLPE AL | m | 900
1.1KV(E) armoured XLPE, FRLS Control Cable of following size:-
14.16 | 7C x 2.5 SQMM CU | m | 27000
14.17 | 3C x 2.5 SQMM CU | m | 800
15 | CABLE GLANDS
Supply of Flameproof double compression stainless steel cable gland suitable for following XLPE , FRLS cable sizes & as per relevant IS for hazardous area.
15.1 | 3.5C x 150, Sqmm XLPE AL | Nos. | 5
15.2 | 3.5C x 95, Sqmm XLPE AL | Nos. | 5
15.3 | 3.5C X 50, Sqmm XLPE AL | Nos. | 20
15.4 | 4C X 25, Sqmm XLPE AL | Nos. | 50
15.5 | 4C X 16, Sqmm XLPE AL | Nos. | 50
15.6 | 4C X 10, Sqmm XLPE AL | Nos. | 4
15.7 | 4C X 6, Sqmm XLPE AL | Nos. | 60
15.8 | 4C X 4, Sqmm XLPE AL | Nos. | 15
15.9 | 4C X 2.5, Sqmm XLPE AL | Nos. | 16
15.1 | 3C X 2.5, Sqmm XLPE AL | Nos. | 5
15.11 | 3C X 6, Sqmm XLPE AL | Nos. | 10
15.12 | 2C X 4, Sqmm XLPE AL | Nos. | 4
15.13 | 2C X 16, Sqmm XLPE AL | Nos. | 4
15.14 | 7C x 2.5 SQMM CU | Nos. | 70
15.15 | 3C x 2.5 SQMM CU | Nos. | 10
Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use.
15.16 | 1C x 400, Sqmm XLPE AL | Nos. | 60
15.17 | 3.5C x 150, Sqmm XLPE AL | Nos. | 6
15.18 | 3.5C x 95, Sqmm XLPE AL | Nos. | 5
15.19 | 3.5C X 50, Sqmm XLPE AL | Nos. | 22
15.2 | 4C X 25, Sqmm XLPE AL | Nos. | 50
15.21 | 4C X 16, Sqmm XLPE AL | Nos. | 50
15.22 | 4C X 10, Sqmm XLPE AL | Nos. | 4
15.23 | 4C X 6, Sqmm XLPE AL | Nos. | 60
15.24 | 4C X 4, Sqmm XLPE AL | Nos. | 15
15.25 | 4C X 2.5, Sqmm XLPE AL | Nos. | 16
15.26 | 3C X 2.5, Sqmm XLPE AL | Nos. | 5
15.27 | 3C X 6, Sqmm XLPE AL | Nos. | 10
15.28 | 2C X 4, Sqmm XLPE AL | Nos. | 4
15.29 | 2C X 16, Sqmm XLPE AL | Nos. | 4
15.3 | 7C x 2.5 SQMM CU | Nos. | 70
15.31 | 3C x 2.5 SQMM CU | Nos. | 10
END TERMINATION KIT
15.32 | Supply of Raychem make heat shrinkable end termination kit suitable for 11 KV (UE) XLPE, FRLS cables of following sizes.
15.33 | 3C x 240 sqmm (AL) ( suitable for outdoor purpose) | Nos. | 1
15.34 | 3C x 240 sqmm (AL) ( suitable for indoor purpose) | Nos. | 3
16 | CABLE LUGS
Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:-
16.1 | 3.5C x 150, Sqmm XLPE AL | Nos. | 25
16.2 | 3.5C x 95, Sqmm XLPE AL | Nos. | 20
16.3 | 3.5C X 50, Sqmm XLPE AL | Nos. | 80
16.4 | 4C X 25, Sqmm XLPE AL | Nos. | 200
16.5 | 4C X 16, Sqmm XLPE AL | Nos. | 200
16.6 | 4C X 10, Sqmm XLPE AL | Nos. | 8
16.7 | 4C X 6, Sqmm XLPE AL | Nos. | 240
16.8 | 4C X 4, Sqmm XLPE AL | Nos. | 60
16.8 | 4C X 2.5, Sqmm XLPE AL | Nos. | 64
16.9 | 3C X 2.5, Sqmm XLPE AL | Nos. | 12
16.1 | 3C X 6, Sqmm XLPE AL | Nos. | 15
16.11 | 2C X 4, Sqmm XLPE AL | Nos. | 8
16.12 | 2C X 16, Sqmm XLPE AL | Nos. | 16
16.13 | 7C x 2.5 SQMM CU | Nos. | 500
16.14 | 3C x 2.5 SQMM CU | Nos. | 100
Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:-
16.15 | 1C x 400, Sqmm XLPE AL | Nos. | 60
16.16 | 3.5C x 150, Sqmm XLPE AL | Nos. | 25
16.17 | 3.5C x 95, Sqmm XLPE AL | Nos. | 20
16.18 | 3.5C X 50, Sqmm XLPE AL | Nos. | 80
16.19 | 4C X 25, Sqmm XLPE AL | Nos. | 200
16.2 | 4C X 16, Sqmm XLPE AL | Nos. | 200
16.21 | 4C X 10, Sqmm XLPE AL | Nos. | 8
16.22 | 4C X 6, Sqmm XLPE AL | Nos. | 240
16.23 | 4C X 4, Sqmm XLPE AL | Nos. | 60
16.24 | 4C X 2.5, Sqmm XLPE AL | Nos. | 64
16.25 | 3C X 2.5, Sqmm XLPE AL | Nos. | 12
16.26 | 3C X 6, Sqmm XLPE AL | Nos. | 15
16.27 | 2C X 4, Sqmm XLPE AL | Nos. | 8
16.28 | 2C X 16, Sqmm XLPE AL | Nos. | 16
16.29 | 7C x 2.5 SQMM CU | Nos. | 500
16.3 | 3C x 2.5 SQMM CU | Nos. | 100
17 | Cable Trays
17.1 | Ladder type GI cable tray (100mmx2mm, 3 Meter length) with minimum hot dip zinc coating 75 micron with accessories like coupler plates,bends, Stainless steels hardwares like nuts & bolts , bends, washers etc and as per IS & ES:8161.
a. | 750mm Wide | m | 40
b. | 600mm Wide | m | 300
c. | 300mm Wide | m | 200
d. | 150mm Wide | m | 228
e. | 50mm Wide | m | 100
17.2 | 90 deg Horizontal Bend Ladder type (shall be decided as per detail engineering)
a. | 750mm Wide | Nos. | 4
b. | 600mm Wide | Nos. | 16
c. | 300mm Wide | Nos. | 8
d. | 150mm Wide | Nos. | 5
17.3 | TEE Connection Ladder type (shall be decided as per detail engineering)
a. | 600mm Wide | Nos. | 16
b. | 300mm Wide | Nos. | 5
17.4 | 90 deg Vertical Bend (inside) Ladder (shall be decided as per detail engineering)
a. | 600mm Wide | Nos. | 10
b. | 300mm Wide | Nos. | 2
17.5 | 90 deg Vertical Bend (outside) Perforated (shall be decided as per detail engineering)
a. | 600mm Wide | Nos. | 10
b. | 300mm Wide | Nos. | 2
17.6 | G.I. Perforated Cable Trays , 100 mm deep, 3 mm thick G.I. perforated cable trays (Min. coating 100 microns of zinc) with bend, reducer, coupler plate and other hardware.
a. | 750mm Wide | m | 10
b. | 600mm Wide | m | 550
c. | 300mm Wide | m | 175
d. | 150mm Wide | m | 350
e. | 50mm Wide | m | 100
17.7 | 90 deg Horizontal Bend Perforated (shall be decided as per detail engineering)
a. | 750mm Wide | Nos. | 3
b. | 600mm Wide | Nos. | 20
c. | 300mm Wide | Nos. | 20
17.8 | 90 deg Vertical Bend (Inside) Perforated (shall be decided as per detail engineering)
a. | 600mm Wide | Nos. | 10
b. | 300mm Wide | Nos. | 4
c. | 150mm Wide | Nos. | 20
17.9 | 90 deg Vertical Bend (outside) Perforated (shall be decided as per detail engineering)
a. | 600mm Wide | Nos. | 10
b. | 300mm Wide | Nos. | 4
c. | 150mm Wide | Nos. | 20
17.1 | TEE Connection Perforated type (shall be decided as per detail engineering)
a. | 600mm Wide | Nos. | 8
18 | STEEL STRUCTURAL/ MS PLATE/ MS CHEQUARD PLATE
18.1 | Supply and Erection of MS Structural Steel: MS structural steel like ISMC , angles, flats etc conforming to IS-2062. : Structural steel work riveted,bolted or welded in built up sections, trusses & framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete: | Ton | 7
18.2 | Supplying and fixing of 6 mm thick chequered plate on cable trench inside swtich room, DG room, earthing pit including cutting, painting, lifting hooks, etc conforming to IS-3502. | Sqm | 100
18.3 | 3mm to 10mm thick MS plate conforming to IS-2062 | Ton | 1.5
19 | EARTHING & LIGHTNING
Supply of following Hot dip Galvanized earthing and lightning protection materials along with the accessories conforming to IS & drg. Attachment no.-29 (LPG.ENG.117.06.03.2001) of contract specification Specifications and .(Galvanisation is 910gms/sq. mtr)
19.1 | 50 x 6 mm GI Strip | m | 4400
19.2 | 35 x 6 mm GI Strip | m | 2400
19.3 | 25 x 6 mm GI Strip | m | 1100
19.4 | 1C x 150 mm2 PVC (Al) cable Green colour | m | 560
19.5 | 1C x 95 mm2 PVC (Al) cable Green colour | m | 670
19.6 | 1C x 35 mm2 PVC (Al) cable Green colour | m | 330
19.7 | 1C x 16 mm2 PVC (Al) cable Green colour | m | 850
19.8 | 1C x 2.5 mm2 PVC (Cul) cable Green colour | m | 150
19.8 | Hot dip Galvanized 10 Holes ∅13mm ground plate 550mmx50mmx6mm earth connection bar with fixing materials/ accessories , SS hardware etc. (min. coating 120 microns of zinc). | Nos | 70
19.9 | Flexible earth provision inclusive of flexible cable, hanger, grounding clip etc for LPG unloading tanker | Nos | 3
19.1 | 1000mm long,20 dia. Hot dipped GI air termination rod(lightning rod-120 Micron coating) with all fixing material,accessories as per IS:2309 | Nos | 3
20 | Earthing Lug
20.1 | 1C x 150 mm2 PVC (Al) cable Green colour | Nos | 60
20.2 | 1C x 95 mm2 PVC (Al) cable Green colour | Nos | 80
20.3 | 1C x 35 mm2 PVC (Al) cable Green colour | Nos | 65
20.4 | 1C x 16 mm2 PVC (Al) cable Green colour | Nos | 300
20.5 | 1C x 2.5 mm2 PVC (Cul) cable Green colour | Nos. | 850
20.5 | SQUARE TAPE CLAMP | Nos | 40
20.6 | TEST LINK | Nos | 10
20.7 | TAPE CLIP | Nos | 1000
20.8 | TEE JOINT | Nos | 700
20.9 | Earth Pit: Supply of Maintanance Free (chemical) Earth electrode with all parts including required hardware for earth pit (equipment earthing, Neutral earthing and for lightning protection) and required test link for checking earth connectivity.as per specification,Attachment-29 LPG.ENG.117.06.03.2001, IS and direction of Engineer-in-charge icludingincluding supply of commissioning and 2 years O&M spares.
a. | Earth pit for Body Earthing ( BEP) | Nos | 23
b. | Earth pit for Lightning Earthing ( LEP) | Nos | 31
c. | Earth pit for Neutral Earthing ( NEP) | Nos | 8
d. | Instrument earth pit (IEP) | Nos | 27
21 | Earth Pit: Supply of Maintanance Free (chemical) Earth electrode 4 mtr long, 100 mm dia suitable for rocky area with all parts including required hardware for earth pit as required as per IS 3043. The pipe shall be embedded as far as possible vertically into the ground, except when hard rock is encountered, where it may be burled inclined to the vertical, the inclination being limited to 30 degree from the vertical. The connection of MS flat to each electrode shall be made through MS links by bolted joints to enable isolation of the electrode for testing purposes. . This is included with excavation, restoration and removal extra earth/rock. and required test link for checking earth connectivity.as per specification,Attachment-29 LPG.ENG.117.06.03.2001, IS and direction of Engineer-in-charge icludingincluding supply of commissioning and 2 years O&M spares. | Nos | 8
22 | GENERAL SAFETY EQUIPMENT
22.1 | 11 kV, 900mm wide, electric grade floor rubber mat conforming to relevant IS. ISI mark shall be there on rubber mat. | m | 5
22.2 | 1.1 kV, 900mm wide, electric grade floor rubber mat (in pieces of length not less than 2 mtrs.) conforming to relevant IS. ISI mark shall be there on rubber mat. | m | 60
22.3 | Rubber Hand Gloves of 11 KV grade. | Pair | 4
22.4 | Rubber Hand Gloves of 415V grade. | Pair | 6
22.5 | First aid box of GI, 18 SWG sheet with necessary items. | No. | 8
22.6 | DANGER PLATE (As per IS 2551) | Nos. | 30
22.7 | CABLE ROUTE MARKER | Nos. | 200
22.8 | CO2 fire extinguishers 5kg with fixing bracket | Nos. | 18
22.9 | ABC Dry chemical powder (DCP) fire extinguishers 5kg with fixing bracket | Nos. | 18
21.1 | Shock treatment chart | Nos. | 40
21.11 | Fire buckets (4nos.) with sand & M.S. Hooks / stand | Set | 10
INST | CONTROL & INSTRUMENTATION WORKS
PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)
Note: 1. All items under this section shall be quoted for supply to site including charges towards packing and forwarding, loading, unloading, transportation, insurance etc. Third party inspection for the supply items shall be in tenderer's scope. Approval of TPI agency shall be obtained from IOCL/EPMC on award of contract & engaged for inspection & clearance of all materials as per agreed QAP to be firmed up after placement of order by IOCL/EPMC.
1 | FIRE DETECTION SYSTEM
1.1 | Presssure Transmitter & solenoid valve for Deluge valve
1.1.1 | Supply of pressure transmitter (24 V DC) Exd type, 2 nos. with each DV (1 nos. for air line & 1 no. for water line) Description:IP-66, EExia IIA IIB, T3 (ATEX /CENELEC),CCOE 4 ~ 20 mA +HART, Range: 0~7kg/cm2 (11 nos.) & 0~15kg/cm2 (11 Nos ), Acuracy:0.075% of span. Rangeability – 1:100 , service: water & Air, SS316 cable gland. refer tender specification for detail. | Nos. | 22
1.1.2 | Supply flameproof solenoid valve (24V DC) suitable for Hazardous area zone-1, IIA/IIB T3, 1/2" NPT connection as per specification (9 nos for DV+2 Nos spares) | Nos. | 9
1.2 | ESD PUSH BUTTON STATION
1.2.1 | Supply of ESD Push button station with all accessories like cables , glanding & termination etc. mounted on Exd JBs located at different areas - a)Filling Shed, b)Pump house, c)LPG Bullets, d)TLD , e)Central Monitoring Hub f) plant manager room g) Filled Cylinder Area | Nos. | 7
1.3 | SIREN
1.3.1 | Supply of electric siren at pump house/PMCC/Security room. Scope also includes: a) supply of necessory equipments/component/ accessories including siren controller required to complete system as per tender document. b) supply of any support required for siren & it's panel | Nos. | 1
1.3.2 | Supply of Hand operated siren for the location of LPG pump house, security room, TLD bay & Empty cum filling shed. | Nos. | 4
1.4 | Fire detection system & integrated local panels
1.4.1 | Supply of Fire Alarm System panel along with electronic card and other electrical accessories. All hardware and software to integrate all devices for successful functioning of the system included in the scope. All Fire Alarm Panel Panels shall be integrated through MODBUS / PROFIBUS / OEM RECOMMENDED SERIAL LINK COMMUNICATION. Common Fault Alarm shall be generated in Fire Alarm Panel to hook up through hardware cable to PLC / ESD located at CR. Associated electrical or electronics circuit connecting with the field devices of detection system requires high availability and reliability in confirmation to tender drawings and specification. Fire alarm system shall be UL listed. Fire Detection System Panel shall include below mentioned items: 1. Intelligent Analogue Addressable type non-ex-proof type Manual Call point (06 Nos), to be hooked up with Fire Alarm Panel at CMH, 2. Intelligent Analogue Addressable type Flame proof type Manual Call point (07 Nos), to be hooked up with Fire Alarm Panel at CMH, 3. Isolator Modules (03 Nos), to be hooked up with Fire Alarm Panel at CMH. 4. Control Modules (05 Nos), to be hooked up with Fire Alarm Panel at CMH. 5. Intelligent Analogue Addressable type Multi Criteria Detector (05 Nos) to be hooked up in Fire Alarm Panel of CMH). 6. Response Indicators (05 Nos), 7 Audio Visual Fire Alarm Siren (05 Nos). Above items shall be read in conjuction with Fire Detection drawing & ILSD drawing. | Lot | 1
1.4.2 | SUPPLY of DV Operation Panel integrating with PLC and with PB (with operation indicating lamp for "DV on Fire" and "DV Operated") for opening of Deluge Valve (09 nos+ 1 spare) . All hardware as required and software included. (1 No. DV panel shall be installed at fire water pump house, 1 No. at main gate security room.) | Lot | 2
2 | GAS MONITORING SYSTEM
2.1 | Gas detectors
2.1.1 | Supply of flameproof/EX -proof , IP-66 IR gas detector suitable to hazardous area Zone-1, IIA/B T3 . Canopy & any otther acessories required is included in scope | Nos. | 28
2.2 | Gas monitoring system
2.2.1 | Gas monitoring system: Supply of Dual redundant (Parallel/ Hot Standby) wall mounted Programmable Logic Controller (Process PLC) along with PLC Panels, Input Output modules, Power supply units, Relays with base, barriers, TBs, Dual Ethernet ports per processors, Serial Interface Modules, wirings, glands, plugs, other modules/ hardwares required for interfacing all the required field and Central Monitoring Hub (CMH) equipments including spare requirements, licenses, tags, softwares etc complete as per specification and tender document. AI -28 Nos DI -12 Nos DO -04 Nos Serial Interface Ports: 04 Additional 20% spare (min 1) qty to be supplied over the above mentioned I/O quantity.Size of the PLC panel shall be optimized mode to accomodate all the signals in wall mounted panel only. Gas monitoring system at Central Monitoring Hub (CMH) as per tender documents. the scope also includes supply of all componennt, accessories required for complete the system and customization of reports as detailed in specifications and tender documents. | Lot | 1
2.2.2 | Supply of weather proof Repeater panel at security room alongwith hooter & indication of Fault & LEL Alarm as per tender secifications. Panel to be hooked up with GMS at CMH. | Nos. | 1
2.2.3 | Supply of Flameproof/Ex-Proof cum weatherproof Repeater Panel alongwith Flameproof/Ex-proof Hooter & indication of Fault & LEL Alarm as per tender secifications. same to be hooked up with GMS at CR , All cabling & hardware included (Common repeater panel 1 no. in LPG Pump House room for TLD, LPG P/H & MSV's area gas detectors; 1 no for Filling shed & filled cylinder shed. ) | Nos. | 2
2.2.4 | Supply of sample gas cylinder for gas detectors sufficient to calibrate min. 21 nos. Gas detectors at a time. All asscessories needed for calibration are included in scope | Lot | 4
3 | TANK FARM MANAGEMENT SYSTEM
3.1 | Supply of Tank farm management (TFM) - accessories , all required components as per ITB Specifications and Documents/ Drg ,Technical discussions , correspondences , including Documentation , Testing, Inspection, packing , transportation to site, guarantee etc. - Radar gauges, Servo gauges, Pressure Transmitter, temperature transmitter, multi point TE RTD type on all MSV tank, backend system along with computer terminal, TFM (CIU), TFM panels, Redundant Server along with software, facility for printing in common network printer, communication system Ethernet base (TFM side) with communication cable to interface with PLC as per the quantities mentioned in tender documents/ drawings, Electrical accessories if required and any other modification, painting etc. All other hardware and software as per Specifications and drawings in tender documents.
3.1.1 | The followings shall be considered for above - i) Servo Gauge with Display , Accuracy +-1mm LAB conditions,Density Measurement - 1 no. for each MSV | Nos | 3
3.1.2 | ii) Pressure Tx with 2 valve manifold for vapour pressure measurement Range 0 -15 Kg/CM2 - 2 nos. for each MSV | Nos | 3
3.1.3 | iii) Radar Gauge with Display and - +/-1mm LAB condition with Display (Smart typeTank Side Indicator),Temperature sensor interface, Suitable for 6" Sch 10 Stilling pipe,1 Nos. SIL3 Relay Output & Analog Output - 1 no. for each MSV | Nos | 3
3.1.4 | iv) Vibration Fork type level switch with HH/LL set points - 1no. For each MSV | Nos | 3
3.1.5 | v) Smart type tank side indicator for Radar gauge at LPG pump house & interfacing with Radar gauge & Process PLC /safety PLC - 1 no. for each MSV | Nos | 3
3.1.6 | vi) Smart type tank side indicator for servo Gauge at LPG pump house & interfacing with servo gauge & Process PLC /safety PLC 1 no. for each MSV | Nos | 3
3.1.7 | vii) local indicator for pressure transmitter at LPG pump house - 1 no. for each MSV | Nos | 6
3.1.8 | viii) Interface (Radar & Servo) | Nos | 6
3.1.9 | ix) 9 Point temperature probe ( to be interface with Radar & Servo) | Nos | 3
2010-01-03 | x) Redundant CIU/FCU with all interfacing , 2 nos of Modbus ports for Process PLC and 2 nos of Modbus ports for TFMS connectivity as required - 1 set | Set | 1
2011-01-03 | xii) Verification pin set | Nos | 20
2012-01-03 | xiii)TFMS Software supplied by bidder shall be same make as radar manufacturer and compatible with servo gauges. Licence shall be 12 nos min. | Lot | 1
2013-01-03 | xiv) Junction Boxes - | Nos | 4
2014-01-03 | xv) PDB Panel for TFMS. | Nos | 2
2015-01-03 | xvi) Communication cable, RTD cable, Power cable for TFMS | Lot | 1
2016-01-03 | xvIi) Audio-Visual Annunciation Panel for annunciation at LPG Pump House, integrated with all Level Switches of MSVs (Single common Panel for all level switches) | Nos | 1
3.2 | Tank Farm Management Servers - Commodity Grade, working on redundant (Primary and Secondary) hot standby mode with software, including backlit LED Monitor, key board and mouse. Supply , Installation, erection and commissioning of Operator Interface Console Computer (OIC) with 22" colour LED monitor, standard keyboard etc. complete as per specifications at Central Monitoring Hub (CMH). | Lot | 1
3.3 | Other items for above - FLP Double compression type SS cable glands - As required , Adaptor Plate for Radar Gauge 4"/6",300# (SS316) for Radar tags - 1 no , Adaptor Plate for Temperature Probes 2",300# (SS316) - 4 nos , Fabricated Adaptor Chamber for Servo Gauge 2"X 4" X 6"300# (MOC CS) with pressure gauge, needle valve & pressure relief valve for Servo Tags , Studs as per SA 320 Gr. L7 & Bolts Nuts as per SA 194 Gr. 7 , Gaskets ( 6",4", 2") Spiral wound Metallic AISI 304, asbestos filled as per API 601 , fabricated cable for CIU & PC - As required ,fabrication of manifold for ionstllation of local indicator (radar /servo)- as required, Cables for communication of Servo , Radar / Servo / field Instruments to CIU (FRLS Cable for data communicatin) - As required , All software and Hardware shall be included as required , Bidder shall consider Process PLC & Tank Gauging system interface on redundant Modbus Communication , Any other item to achieve complete system to successful functioning and integration with other system as required are included. | Lot | 1
4 | AUTOMATION SYSTEM
4.1 | TLF/TLD GANTRY
4.1.1 | Supply of Flameproof cum weather proof smart type Grounding unit with one green indicating lamp and dual output for safety earthing of tank trucks, suitable for giving safety interlocking signal to PLC all complete as per specifications | Nos. | 2
4.2 | Central Monitoring Hub (CMH) INSTRUMENTATION
4.2.1 | Supply of Dual redundant (Parallel/ Hot Standby) Programmable Logic Controller (Process PLC) along with PLC Panels, Marshalling Panels, Input Output modules, Power supply units, Relays with base, barriers, TBs, Dual Ethernet ports per processors, Serial Interface Modules, HMI console, wirings, glands, plugs, other modules/ hardwares required for interfacing all the required field and Central Monitoring Hub (CMH) equipments including spare requirements, licenses, tags, GUI, softwares etc complete as per specification and tender document. AI -25 Nos DI -96 Nos DO -80 Nos Serial Interface Ports: 28 Minimum 20% spare IO to be supplied as per tender specification. Count of PLC panel shall be optimized to accomodate all the signals in one panel only. | Lot | 1

## Table 2
4.2.2 | Supply of Terminal Automation Software for Operator Stations with dongle/key, licenses, media, documentation etc., complete as per specifications / documents. TAS is the front end for all sub systems, hence below subsystems shall be interfaced with TAS for Monitoring, Logging, Reporting and Controls-Interlocks etc. System Interfaces: (Based on functional requirement for interfacing of the available sub systems at the Locations).System stated below with TAS & its commissioning with TAS for Alarms,archiving & events logging - SAP for TAS (TT & packed truck loading & unloading & sub systems covered in the work) - MCC, VFD, DG Sets, UPS etc. Interface - PLC & ESD ROV etc. - TFMS Interface including SAP - SAP-TFMS Interface - PAGA Interface - FAS Interface, - Fire Fighting System, - CCTV systems - DV Operational Panel - GMS Repeater Panel | Lot | 1
4.2.3 | Supply of SCADA Software with 100% spare tags alongwith dongle/key, licenses, media, documentation etc. complete as per specifications / documents. | Lot | 1
4.2.4 | Supply of Operator Interface Console Computer (OIC)/EWS with 22" colour LED monitor , standard keyboard etc. complete as per specifications and tender drawing: -CAROUSAL -EWS/OWS -GMS -WEIGH BRIDGE -CYLINDER INVENTORY | Nos. | 5
4.2.5 | Supply of computer with 22" LED colour monitor, standard keyboard for SAP terminal for generating printing invoice, complete as per specifications. | Nos. | 1
4.2.6 | Supply of 24 port Redundant Managed L2 Ethernet Switch (10/100/1000 MBPS) for connecting LED Display etc. complete as per specification. [Number of Port shall be as per site Requirment with 20% spare ports] | Set | 4
4.2.7 | Supply of color laser printer of approved make (latest model with added feature is also acceptable) complete as per specifications. A- 4 size @ Security Room. | Nos. | 1
4.2.8 | Supply of color laser printer of approved make (latest model with added feature is also acceptable) complete as per specifications. A- 3 size @ Central Monitoring Hub (CMH. | Nos. | 1
4.2.9 | Supply of heavy duty high speed dot matrix network printer with minimum 550 CPS at 10 CPI for invoice printing in 01 Nos Security room & 01 Nos in CHM Room, complete as per specifications and tender document. | Nos. | 2
2010-02-04 | Supply of GSM modem for auto SMS for transmission after each stage of loading process for ESD as per specification. | Lot | 2
2011-02-04 | Supply of 65" LED monitor of reputated make to be installed at driver rest room for display of safety videos & slogans. | Nos. | 1
2012-02-04 | Supply of 55" LED monitor of reputated make to be installed at admistrative building Lobby area for plant & safety monitoring & instruction shall be in scope. Scope also includes interfacing with OIC, PAGA & TAS server including cable supply,laying and termination as needed. | Nos. | 1
2013-02-04 | Supply of UPS Power Distribution Panel for powering PLC Panel, ESD System Panel, LRCS, OIC & EWS stations, TFMS System, TTES, Bay Instruments , Tank Farm Instruments , CCTV system , local control panels, Fire Detection System,fire alarm panels, Access control system, pnuematic, header line instruments and other TAS equipments where UPS power are required for smooth un- interrupted operation as per OEMs recommendation. Miscellaneous Instrumentation comprising of suitable MCCBs for Isolation etc to be provided. The panel shall be complete in all respects with necessary indication lamps for powering, necessary control wiring voltmeter, ammeter etc & as per specifications and tender document. Note: Minimum 20% spare power points to be made available for future use. | Lot | 1
2014-02-04 | Supply of Open desk operator consoles in CMH room: -CAROUSAL -SAP -ACS -EWS/OWS -TFMS -GMS -CCTV Supply of Open desk operator consoles in Security Room: -WEIGH BRIDGE -CYLINDER INVETORY -CCTV Each console will consists of nessary electrical wirring, 2 Nos. Sockets, 2 Nos. buttons, MCBs as required, LIght, Louvers & FAN number as required.) | Nos. | 10
2015-02-04 | Supply of Computer chairs (Make: Godrej or equivalent) - -03 Nos for Central Monitoring Hub (CMH) -02 Nos for Security Room | Nos. | 5
2016-02-04 | Supply of Table (Make: Godrej or equivalent) for printer in security room/ Central Monitoring Hub (CMH) - 1 nos. for security room (main gate) & 1no.in CMH Room. | Nos. | 2
5 | SECURITY GATES & TRUCK PARKING AREA
5.1 | Supply of electrically operated barrier gates(boom length to sute the site requirement, approx. 4 mtr.) with detection mechanism, manual bypass control with EX-proof motor, Exproof Traffic lamp & electronics etc. with configurable closing & opening time with sensors for detection of vehicle crossing the barrier etc. complete with supporting structure, fittings, cable supports complete as per specification. The gates are required for Security Entry and exit at licence area. 1 set. for packed truck Entry (4 m), 1 set for packed truck Exit (4 m). | Set | 2
5.2 | Supply of electrically operated barrier gates(boom length to sute the site requirement, approx. 7 mtr.) with detection mechanism, manual bypass control with EX-proof motor, Exproof Traffic lamp & electronics etc. with configurable closing & opening time with sensors for detection of vehicle crossing the barrier etc. complete with supporting structure, fittings, cable supports complete as per specification. The gates are required for Security Entry and exit at licence area. 1 no. at bulk truck Entry/EXIT (7 m). | Set | 1
6 | ACCESS CONTROL SYSTEM:
6.1 | Supply of Biometric fingerprint cum contactless type smart card reader (entry side, inside Central Monitoring Hub (CMH)) along with ectromagnetic door lock 600 lb, panic bar for fire exit doors, door position magnetic contact with buzzer as per specifications. One more magnetic latch along with push button shall be provided for emergency exit door, Main security room. | Nos. | 1
6.2 | Supply of Biometric fingerprint cum contactless type smart card reader (Outdoor) along with accessories including controller, software and programming kit as per specification. (Entry & Exit both side) | Nos. | 3
6.3 | Supply of Access Control System Software for setup, configuration, operation, events, history and archiving, alarm monitoring, recording, printing, time and attendance etc. complete as per specification and tender specifications including ESD input from PLC. | LS | 1
6.4 | Supply of Visitor Management Software complete as per specificationand tender specifications. | Set | 1
6.5 | Supply of ACS server computer with 22"color led monitor , standard keyboard, video camera loaded with ACS software for CMH room etc. complete as per specifications. | Set | 1
6.6 | Supply of Client Computer of ACS / Visitor Management with 22"color led monitor, standardkeyboard, OS, Antivirus, video camera etc including installation of ACS software for ID badging & issuing of Visitor pass at security Room etc. complete as per specifications. | Set | 1
6.7 | Supply of the multizone door frame metallic detector as per specification. | Nos. | 2
6.8 | Supply of smart cards for Biometric fingerprint cum contactless type smart card reader as per the specification and tender document. | Nos. | 50
6.9 | Supply of half height turnstile (tripod) as per specification. | Nos. | 3
6.1 | Supply of SS 304 guiding rail as per specification. | RM | 30
7 | WEIGHING BRIDGE SYSTEM
7.1 | Supply of Static Weighing bridge (50 MT) located at near to Central Monitoring Hub (CMH) with load cells with all accessories (load cells, like cable from field to Central Monitoring Hub (CMH), JB, instruments, Jumbo Display for TT etc.) The rate shall include Static weighing bridges local marshalling / control panel . Vendor to provide Static Weighing bridge local marshalling/ control panel protocol free of cost to M/s IOCL. Supply & installation of Jumbo display for TTs is also included. | Set | 1
8 | FIELD INSTRUMENTS
8.1 | Pressure gauge- IP-66 , SS316 bourdon,zero adjustment facility, micrometer screw type pointer, ±1% accuracy with all accessories.
8.1.1 | supply of bourdon type pressure gauge with range 0~ 25kg/cm2. | Nos. | 4
8.1.2 | supply of bourdon type pressure gauge with range 0~ 16kg/cm2. | Nos. | 24
8.1.3 | supply of bourdon type pressure gauge with range 0~ 10kg/cm2. | Nos. | 21
8.1.4 | supply of bourdon type pressure gauge with range 0~ 6kg/cm2. | Nos. | 4
8.2 | Pressure & Differential pressure transmitter
8.2.1 | Supply of presssure transmitter with calibration range 0~ 25 kg/cm2. | Nos. | 6
8.3 | Tempreture Transmitter
8.3.1 | Supply of tempreture transmitter with calibration range 0~ 100°C alonge with tempreture elements & cable from element to transmitter. | Nos. | 3
8.4 | level gauge- Description:-Transperent Type,IP-66, C To C distance: HOLD, SS float, Vent & Drain Plug: 3/4 " NPT , Flange:1 1/2" 300# RF, Zone-1 IIA/IIB
8.4.1 | Supply of level gauge. | Nos. | 2
8.5 | Temprature gauge: all angle type, 1.5" 300# RF well connection, 1/2" NPT gauge,150mm dial size, SS316 material, shatterproof glass
8.5.1 | Supply of tempreture gauge with range 0 ~ 100°C. | Nos. | 5
8.6 | Electromagnetic Flow meter: For water line of 100mm.
8.6.1. | Supply of Electromagnetic Flow meter with range 0 ~ 50 m3/hr. | Nos. | 1
8.7 | Flow Switch: For Water application and line size is 25mm.
8.8.1 | Supply of Magnetic Flow Switch with range 0 ~ 15m3/hr. | Nos. | 4
8.8 | Level Switch: Level Switch for waste water in plant Sumps.
8.8.1 | Supply of Float type level switch with range of 0 ~ 3 mtr. | Nos. | 3
9 | JUNCTION BOXES WITH SPARES ACCESSORIES, ALL REQUIRED COMPONENTS AS PER ITB SPECIFICATIONS AND DOCUMENTS/ DRAWINGS INCLUDING DOCUMENTATION, TECHNICAL DISCUSSIONS, CORRESPONDENCES, TESTING, INSPECTION, PACKING, TRANSPORTATION TO SITE, GUARANTEE ETC.
9.1 | Junction for Field Instruments
9.1.1 | Supply of Signal Junction Box (BLUE) : Flame proof /ex-proof, Die cast AL LM6 body, 12 inlet+2 outlet as per specification suitable for hazardous area of zone 1, group IIA/IIB, T3 ,having PESO/CMIFR approval. It shall be complete in all respect. Accessories like certified flameproof /exproof SS316 double compression cable glands with PVC shrouds & SS plugs for excess entries, SS 316 engraved tag plate, mounting clamp & SS 316 fasteners. Complete as per specifications / documents. | Nos. | 2
9.1.2 | Supply of Signal Junction Box (BLUE) : Flame proof /ex-proof, Die cast AL LM6 body, 6 inlet+2 outlet as per specification suitable for hazardous area of zone 1, group IIA/IIB, T3 ,having PESO/CMIFR approval. It shall be complete in all respect. Accessories like certified flameproof /exproof SS316 double compression cable glands with PVC shrouds & SS plugs for excess entries, SS 316 engraved tag plate, mounting clamp & SS 316 fasteners. Complete as per specifications / documents. | Nos. | 2
9.1.3 | Control Junction Box(GREY):Flame proof /ex-proof, Die cast AL LM6 body, 12 inlet+2 outlet as per specification suitable for hazardous area of zone 1, group IIA/IIB, T3 or better having PESO/CMIFR approval. It shall be complete in all respect. Accessories like certified flameproof /exproof SS316 double compression cable glands with PVC shrouds & SS plugs for excess entries, SS 316 engraved tag plate, mounting clamp & SS 316 fasteners. Complete as per specifications / documents. | Nos. | 6
9.1.4 | Supply of Power Junction Box (GREY): Flame proof /ex-proof, Die cast AL LM6 body, 12 inlet+2 outlet as per specification suitable for hazardous area of zone 1, group IIA/IIB, T3 or better having PESO/CMIFR approval. It shall be complete in all respect. Accessories like certified double compression cable glands with PVC shrouds & plugs for excess entries, SS 316 engraved tag plate, mounting clamp & SS 316 fasteners. Complete as per specifications / documents. | Nos. | 7
9.1.5 | Junction Boxes Ex proof-EExd (JBP ) Terminals for LINE, NEUTRAL, shall be isolation breakers : All terminals suitable for 240 V AC , Exd type 12 nos. ½” NPTF cable entries at sides + 2 Nos. cable entries at bottom ; complete with suitable size double compressor SS316 Flame proof Glands with Check Nuts & gaskets. | Nos. | 1
9.2 | Junction box for DELUGE VALVE instruments & GAS DETECTORS
9.2.1 | Supply of Signal Junction Box (BLUE) : Flame proof /ex-proof, Die cast AL LM6 body, 12 inlet+2 outlet as per specification suitable for hazardous area of zone 1, group IIA/IIB, T3 ,having PESO/CMIFR approval. It shall be complete in all respect. Accessories like certified flameproof /exproof SS316 double compression cable glands with PVC shrouds & SS plugs for excess entries, SS 316 engraved tag plate, mounting clamp & SS 316 fasteners. Complete as per specifications / documents. | Nos. | 3
9.2.2 | Control Junction Box(GREY):Flame proof /ex-proof, Die cast AL LM6 body, 12 inlet+2 outlet as per specification suitable for hazardous area of zone 1, group IIA/IIB, T3 or better having PESO/CMIFR approval. It shall be complete in all respect. Accessories like certified flameproof /exproof SS316 double compression cable glands with PVC shrouds & SS plugs for excess entries, SS 316 engraved tag plate, mounting clamp & SS 316 fasteners. Complete as per specifications / documents. | Nos. | 2
9.2.3 | Supply of Junction Box(blue) for spot type IR gas detectors:Flame proof /ex-proof, Die cast AL LM6 body, 12 inlet+2 outlet as per specification suitable for hazardous area of zone 1, group IIA/IIB, T3 or better having PESO/CMIFR approval. It shall be complete in all respect. Accessories like certified flameproof /exproof SS316 double compression cable glands with PVC shrouds & SS plugs for excess entries, SS 316 engraved tag plate, mounting clamp & SS 316 fasteners. Complete as per specifications / documents. | Nos. | 4
10 | ESD PUSH BUTTON STATION FOR ESD-ROV
10.1 | Supply of EX-proof/flameproof ESD Push button station with all accessories mounted at local nearby of ROV (as per IOCL instruction) for Emergecy shut down of ROV . 1 PB station shall be used for 1 no. ESD ROV closed only. | Nos. | 10
11 | INSTRUMENT CABLES
11.01 | 01P X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , OVERALL SHIELDED , SIGNAL CABLE | Mtrs | 1101.9
11.02 | 01T X 2.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , OVERALL SHIELDED , SIGNAL CABLE | Mtrs | 571.2
11.03 | 02C X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , CONTROL CABLE | Mtrs | 7286.6
11.04 | 02P X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , OVERALL SHIELDED , SIGNAL CABLE | Mtrs | 538.02
11.05 | 03C X 2.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , CONTROL CABLE | Mtrs | 3625
11.06 | 03C X 4.0 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , CONTROL CABLE | Mtrs | 250
11.07 | 03C X 6.0 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , CONTROL CABLE | Mtrs | 200
11.08 | 04C X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , CONTROL CABLE | Mtrs | 1669.44
11.09 | 04C X 2.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , CONTROL CABLE | Mtrs | 1094.46
11.1 | 04P X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , OVERALL SHIELDED , SIGNAL CABLE | Mtrs | 350
11.11 | 05C X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , CONTROL CABLE | Mtrs | 1496.34
11.12 | 06P X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , OVERALL SHIELDED , SIGNAL CABLE | Mtrs | 539.58
11.13 | 06T X 2.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , OVERALL SHIELDED , SIGNAL CABLE | Mtrs | 211.14
11.14 | 12C X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , CONTROL CABLE | Mtrs | 1644.62
11.15 | 12C X 2.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , CONTROL CABLE | Mtrs | 211.14
11.16 | 12P X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , OVERALL SHIELDED , SIGNAL CABLE | Mtrs | 234.6
11.17 | 10T X 2.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , OVERALL SHIELDED , SIGNAL CABLE | Mtrs | 758.88
11.18 | 24C X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , CONTROL CABLE | Mtrs | 1149.54
11.19 | 24C X 2.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , CONTROL CABLE | Mtrs | 744.6
11.2 | 36C X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , CONTROL CABLE | Mtrs | 298.86
11.21 | RS485 CABLE | Mtrs | 4279.92
11.22 | Supply of Cat 6 cable.accessories like lugs, adapter, blank plate & patch cord etc as required is included | Mtrs | 590
11.23 | Supply of 24 core OF armod cable in HDPE duct .OFC accessories like 12/24 port LIU, splice tray, loaded adapter, blank plate & patch cord etc as required is included | Mtrs | 2205
11.24 | 04P X 0.8 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , OVERALL SHIELDED , SIGNAL CABLE | Mtrs | 2010
12 | ERECTION MATERIAL AS PER TENDER
12.1 | FIELD INSTRUMENTS
12.1.1 | BALL VALVE -1/4'' NPTF 800# - -A-182 F304 | NOS. | 4
12.1.2 | CAP -1/2"NPTF -3000# -A105 | NOS. | 70
12.1.3 | ELBOW -1/2"SW -6000# -A105 | NOS. | 112
12.1.4 | EQUAL TEE -1/2"SW -3000# -A105 | NOS. | 84
12.1.5 | FEMALE CONNECTOR -1/2"NPTF x 1/2"OD TUBE -3000# -SS316 | NOS. | 36
12.1.6 | FEMALE CONNECTOR -1/2"NPTF x 1/2"OD TUBE -6000# -SS316 | NOS. | 15
12.1.7 | FLANGE -1/2"SW WITH STUDS, NUTS & GASKET -300#RF -A105 | NOS. | 250
12.1.8 | GLOBE VALVE -1/2"SW -800# -A105 | NOS. | 98
12.1.9 | MALE CONNECTOR -1/2"NPTM x 1/2"OD TUBE -3000# -SS316 | NOS. | 60
2010-01-12 | MALE CONNECTOR -1/2"NPTM x 1/2"OD TUBE -6000# -SS316 | NOS. | 15
2011-01-12 | MALE CONNECTOR -1/4'' NPTM x 1/4'' O.D. - -AISI-316 | NOS. | 8
2012-01-12 | NIPPLE L=100 mm -1/2"NPTM x 1/2"PL -HEAVY -IS1239 | NOS. | 168
2013-01-12 | NIPPLE L=100 mm -1/2"NPTM x 1/2"PL -SCH.160 -A106 GR.B | NOS. | 50
2014-01-12 | NIPPLE L=50 mm -1/4'' NPTM x 1/4'' NPTM SCH.XS - -A-312 TP 304 | NOS. | 4
2015-01-12 | PLUG -1/2"NPTM -3000# -SS316 | NOS. | 84
2016-01-12 | PLUG -1/2"NPTM -6000# -SS316 | NOS. | 50
2017-01-12 | REDUCER -3/4"NPTF x 1/2"SW -3000# -A105 | NOS. | 84
2018-01-12 | REDUCER -3/4"NPTF x 1/2"SW -6000# -A105 | NOS. | 100
2019-01-12 | SEAMLESS PIPE -1/2" PL. -HEAVY -IS1239 | MTR. | 168
2020-01-12 | SEAMLESS PIPE -1/2" PL. -SCH.160 -A106 GR.B | MTR. | 200
2021-01-12 | STUD BOLT -3/4"D 140MM L - -ASTM A193-B16 / ASTM A194-4 | NOS. | 48
2022-01-12 | STUD BOLT -3/4"D 160MM L - -ASTM A193-B16 / ASTM A194-4 | NOS. | 108
2023-01-12 | STUD BOLT -5/8"D 120MM L - -ASTM A193-B16 / ASTM A194-4 | NOS. | 24
2024-01-12 | TUBE -1/2"OD -0.065"THK -A269 TP316 | MTR. | 135
2025-01-12 | TUBE -1/4'' O D 1mm THICK - -A-269 TP304 | MTR. | 20
2026-01-12 | TWO-WAY MANIFOLD -1/2"NPTFX1/2"NPTF -3000# -SS316 | NOS. | 56
2027-01-12 | TWO-WAY MANIFOLD -1/2"NPTFX1/2"NPTF -6000# -SS316 | NOS. | 25
2028-01-12 | FLANGE -1/2"NPTF -300#RF -A105 | NOS. | 8
2029-01-12 | CAP -1/2"NPTF -3000# -A105 | NOS. | 70
2030-01-12 | GASKET -1/2" -150# -SS316 GRAPHITE WITH SPIRAL WOUND | NOS. | 21
2031-01-12 | GASKET -1/2" -150# -SS316 GRAPHITE WITH SPIRAL WOUND | NOS. | 21
2032-01-12 | GASKET -4"D -300# -SS316 GRAPHITE WITH SPIRAL WOUND | NOS. | 3
2033-01-12 | GASKET -2"D -150# -SS316 GRAPHITE WITH SPIRAL WOUND | NOS. | 3
2034-01-12 | GASKET -6"D -300# -SS316 GRAPHITE WITH SPIRAL WOUND | NOS. | 9
2035-01-12 | GASKET -2"D -150# -SS316 GRAPHITE WITH SPIRAL WOUND | NOS. | 3
2036-01-12 | STUDS AND NUTS -1/2" x 75MM -300# -SS316 GRAPHITE WITH SPIRAL WOUND | NOS. | 84
2037-01-12 | STUDS AND NUTS -1/2" x 75MM -300# -SS316 GRAPHITE WITH SPIRAL WOUND | NOS. | 84
12.2 | FRP CANOPY
12.2.1 | Supply FRP canopy as per drawing attached with SOR for pressure transmitters, pressure switch & level switch (suitable for vertical as well as horizontal mounting) | Nos. | 6
12.2.2 | Supply of Maintenance Free CPRI approved Earth Pit (Ashlok /Equivalent make) of minimum 3.8 mtr length T45 model/equivalent safe earthing electrode with Pipe-in-pipe technology consisting of two mild steel pipes one inside the other, hot dip galvanized (80-100 microns), filled with high conductive & corrosion resistance crystalline mixture and backfilling compound around electrode, 25 mm dia G.I. watering pipe with funnel, test link, brick masonry earth pit including plastering in CM 1:4, 600x600 mm C.I. Manhole chamber etc. Equivalent make shall be approved by client / consultants. Procedure recommended by chemical earth supplier and IS code to be finally adopted. Item also includes provision of earth station flags with pit nos and date of inspection and the next due date of inspection. Job also includes provision of test certificate of earthing station from a licensed electrician as per the format of the Corporation | Nos. | 1
12.3 | SUPPLY & ERECTION OF STRUCTURALS STEEL: Structural steel work riveted,bolted or welded in built up sections, trusses & framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete: | MT | 2
13 | TOOL & TACKLES FOR SITE (REPUTATED MAKE)
13.01 | TONG TESTER | Nos. | 1
13.02 | MEGGER TESTER | Nos. | 1
13.03 | EARTH TESTER | Nos. | 1
13.04 | PRESSURE GAUGE & TRANSMITTER TEST BENCH SET WITH OIL + 2 LITER OIL AS SPARE | Nos. | 1
13.05 | HAND HELD CALIBRATOR /HART CALIBRATOR (UNIVERSAL TYPE ) | Nos. | 1
13.06 | TEMPRETURE BATH SET FOR RANGE 0~ 200°C | Nos. | 1
13.07 | VIBRATION METER | Nos. | 1
13.08 | GAS SENSOR CALIBRATOR CYLINDER | Set | 1
13.09 | LEL METER , IR TYPE , 0~100 VOL% , RESPONSE TIME - BELOW 20 SEC. | Nos. | 1
13.1 | OXYGEN METER | Nos. | 1
13.11 | ELCOMETER | Nos. | 1
13.12 | DIGITAL LUX METER | Nos. | 1
14 | CCTV SYSTEM
14.1 | CCTV Cameras
14.1.1 | Supply of UL listed HD IP Fixed Dome Camera with IR and MFZ (Motorized Focus & Zoom) Lens 2MP, 1/3'' or better Prograsive scan Cmos sensor , 32GB SD card, multi streaming , H.264, PoE, DC12V/AC24V, IP 66 & IK 10 rated ,ONVIF with with features like Camera tampering, Network loss detectionand all accessories etc. complete as required. for weather proof application including all the wall Mount accessories & pole mounting or accesories as per site requirement. -Wall Mounting Quantity - 12 Nos -Pole Mounting Camera Quantity - 01 Nos Camera shall be installed under driver rest roo, cylinder counting, central monitoring hub room, security path, bulk truck safety, PMCC Panel Room, Fire water pump house, Entrance of admin office, canteen, store, incharge room, training hall/conference room. Below mentioned items to be provide along with cameras: -Surge Protectors -Mounting Bracket same make as Camera | Nos. | 13
14.1.2 | Supply of UL listed IP Fixed Bullet Camera with MFZ (Motorized Focus Zoom) lens of 8MP, 4k resolution , better Progresive scan CMOS sensor, 32GB SD card, WDR, multi streaming , H.264, PoE, DC12V/AC24V, IP 67 ,ONVIF with Pole Mount accessories or accesory as per site requirement Cameras shall be installed under licensed entry & exit gate both for bulk and packed trucks, Main entry/Exit gate both for bul and packed trucs, external road at plant entry and exit. Below mentioned items to be provide along with cameras: -Surge Protectors -Mounting Bracket same make as Camera | Nos. | 6
14.1.3 | Supply of UL listed IP Fixed Box Camera , 8MP lens, with 1/2.5'' or better Progresive scan CMOS sensor ,Varifocal lens (8MP) of 2.8 to 8.5mm, #4k Resolution, 32GB SD card, WDR,multi streaming , H.264, PoE, DC12V/AC24V, IP 67 ,ONVIF with Pole Mount accessories or accesory as per site requirement. Cameras shall be installed over perimeter at 65 M gap (max). | Nos. | 15
14.1.4 | Supply of Full HD , 2MP, IP PTZ Camera (for peripheral survilience in auto mode) with 30X HD optical zoom, IP 66 Day/Night CCD/CMOS, 4.8 to 120 mm Lens, motorised varifocal , progressive scan, Wide Dynamic Range, Dual H.264 and M-JPEG simultaneously, digital signal processing, both PoE and 12 VDC/24 VAC, ONVIF conformant, UL Listed, POE enabled, complete with IP 66 Connectors, Lens, Camera Mounts, Power Supply & all accessories complete as per specifiocation. Cameras shall be installed over perimeter in pair with Manual mode PTZ camera. Below mentioned items to be provide along with cameras: -Surge Protectors -Mounting Bracket same make as Camera | Nos. | 6
14.1.5 | Supply of Full HD , 2MP, IP PTZ Camera (for peripheral survilience in manual mode) with 30X HD optical zoom, IP 66 Day/Night CCD/CMOS, 4.8 to 120 mm Lens, motorised varifocal , progressive scan, Wide Dynamic Range, Dual H.264 and M-JPEG simultaneously, digital signal processing, both PoE and 12 VDC/24 VAC, ONVIF conformant, UL Listed, POE enabled, complete with IP 66 Connectors, Lens, Camera Mounts, Power Supply & all accessories complete as per specifiocation. Cameras shall be installed over perimeter in pair with Auto mode PTZ camera. Below mentioned items to be provide along with cameras: -Surge Protectors -Mounting Bracket same make as Camera | Nos. | 6
14.1.6 | Supply of Full HD , 2MP, IP PTZ Camera with 30X HD optical zoom, IP 66 Day/Night CCD/CMOS, 4.8 to 120 mm Lens, motorised varifocal , progressive scan, Wide Dynamic Range, Dual H.264 and M-JPEG simultaneously, digital signal processing, both PoE and 12 VDC/24 VAC, ONVIF conformant, UL Listed, POE enabled, complete with IP 66 Connectors, Lens, Camera Mounts, Power Supply & all accessories complete as per specifiocation. Cameras shall be installed in bulk storage area including manifold area, complete location of plant. Below mentioned items to be provide along with cameras: -Surge Protectors -Mounting Bracket same make as Camera | Nos. | 2
14.1.7 | Supply of Fixed Ultra High Definition Panoramic camera not less than 8 MP with H.264 with high profile H.264 compression, constant 360 degee recording along with simultaneous multiple angles of view using one sensor, ONVIF, 3D client side Dewarping with no blind spots, POE enabled, UL certified as per tender specification. Camera shall be installed in TT Parking area. Below mentioned items to be provide along with cameras: -Surge Protectors -Mounting Bracket same make as Camera | Nos. | 1
14.1.8 | Supply of Explosion proof ATEX Certified Fixed camera , MFZ Lens of 2MP, resolution of 1920x1080 pixels camera with progresive scan, with H.264 with high profile H.264 compression, lens of 3 - 9 mm Lens,DC-Iris, Day-Night 32 GB MicroSD/SDHC card Slot, 30fps, Multi streams, POE enabled, UL certified. Camera shall be installed in hazardous areas such as LPG Pump House, LPG Compressor House, Empty Cum Filling SHed, Loading- unloading shed, TLD bays. Below mentioned items to be provide along with cameras: -Surge Protectors -Mounting Bracket same make as Camera | Nos. | 5
14.2 | NEWTORK SERVER & VIDEO MANAGEMENT SOFTWARE
14.2.1 | Recording Server(s) with the following minimum configuration Intel Xeon Quad Core Server 32 GB RAM 2 Gigabit NICs Windows Server 2012 R2 x64 Standard/Data Center OS and Application Volume - Disk Configuration: 2 x 300 GB minimum RAID 5 (with server redundancy) Live Database Disk Configuration: Connectivity Internal or Direct Attached 10 x 15K RPM 600GB RAID 1 / RAID10 | Nos. | 1
14.2.2 | Supply of NAS based CCTV storage array (Cumulative 220 TB minimum) for NETWORK SERVER with centralized, scalable video storage, ideal for small to medium setups. The storage shall delivers total available throughput of 350 Mbps / 120 Streams for recording of IP video streams as well as playback and export through the client machine .It should have following hardware fetaure as minimum Processor Intel® Xeon E3-1276 v3 or better, Operating System Microsoft® Windows®Server 2012 . It should have 1TB SSD storage for Operating system.It should gave Internal Memory 32 GB DDR3 ECC or better. It should support RAID 6 feature for HDD redundancy and NVR should be UL listed. It should have Internal, RedundantcPower Supply.build up hard disk for min. 90 days recording. Supply of Dual Redundant Network Video Recorder(NVR) Server with min 21" widescreen LED monitor(One no) with KVM switch complete as per specifications and Tender Document. | Nos. | 3
14.2.3 | Supply of Video Management software licesnes | Nos. | 54
14.2.4 | Supply of Advanced Analytics Software for all fixed cameras (including varifocal, Panoramic, MFZ fixed cameras) alongwith compatible Analytics Server with OS, Antivirus etc including analytic license for each camera complete as per specifications and Tender Document. | Lot | 1
14.3 | WORKSTATION WITH CLIENT LINSENCE
14.3.1 | Supply of workstation. The workstation shall have the following specifications:- Processor – Intel Core i7-4790 @ 3.60GHz Intel® HD Graphics 4600,Memory – Minimum 16 GB,Hard disks – 2TB SATA at 7200 rpms,OS- Windows 8.1/10, 64bit,Network Card – 1Gbit/s network card, Graphic card of minimum 2 GB memory. Location as mentioned below: -Central Monitoring Hub Room -Security Room -Admin Building Plant Manager Room | Nos. | 3
14.4 | CCTV Central Monitoring Hub (CMH) /SECURITY ROOM
14.4.1 | Supply of 55" Flat LED 4K Colour Monitors installed -Security Room -Admin Building (PM cabin) | Nos. | 2
14.4.2 | Supply of 42 U Enclosure cabinet/panel along with all accessories/component for switches and server installation. | Lot | 1
14.5 | CABLE, SWITCHES AND ERECTION MATERIAL
14.5.1 | 4 port Industrial grade layer 2 Managed POE/POE+ Ethernet Switch for connecting Cameras with 4 No. RJ copper port and 2 Nos. optical fiber ports and surge protector as per specifications and Tender Document. | Nos. | 28
14.5.2 | Supply of Layer 3 8 Port SFP , 2SFP+ Ports Managed Switch with Dual internal Power Supply. To be installed in CR | Nos. | 2
14.5.3 | Supply of Explosion Proof junction box for field switches in licsence area | Nos. | 6
14.5.4 | Supply of Layer 3 24 Port SFP , 2SFP+ Ports Managed Switch with Dual internal Power Supply. | Nos. | 1
14.5.5 | Supply of IP 65 junction box Box for keeping the field switches in non licsence area | Nos. | 22
14.5.6 | Supply of 8 M with cantilever of 3 meter (Above ground) Hot Dip Galvanized Poles along with foundation & painting as per the tender specifications. This scope also includes supply, erection & fabrication of structural steel work for installation of JB & camera with industrial grade painting | Nos. | 7
14.5.7 | Supply of 8 M with cantilever of 1.5 meter (Above ground) Hot Dip Galvanized Poles along with foundation & painting as per the tender specifications. This scope also includes supply, erection & fabrication of structural steel work for installation of JB & camera with industrial grade painting | Nos. | 1
14.5.8 | Supply of 8 M with 2 cantilevers (one at 8 m & second at 1.5 M) of 1.5 meter (Above ground) Hot Dip Galvanized Poles along with foundation & painting as per the tender specifications. This scope also includes supply, erection & fabrication of structural steel work for installation of JB & camera with industrial grade painting | Nos. | 1
14.5.9 | Supply of 6 M with cantilever of 3 meter (Above ground) Hot Dip Galvanized Poles along with foundation & painting as per the tender specifications. This scope also includes supply, erection & fabrication of structural steel work for installation of JB & camera with industrial grade painting | Nos. | 8
2010-05-14 | Supply of 6 M with cantilever of 1.5 meter (Above ground) Hot Dip Galvanized Poles along with foundation & painting as per the tender specifications. This scope also includes supply, erection & fabrication of structural steel work for installation of JB & camera with industrial grade painting | Nos. | 1
2011-05-14 | Supply of 6 M with 2 cantilevers (one at 8 m & second at 1.5 M) of 2.5 meter (Above ground) Hot Dip Galvanized Poles along with foundation & painting as per the tender specifications. This scope also includes supply, erection & fabrication of structural steel work for installation of JB & camera with industrial grade painting | Nos. | 1
2012-05-14 | Supply of 10 M with cantilever of 1.5 meter (Above ground) Hot Dip Galvanized Poles along with foundation & painting as per the tender specifications. This scope also includes supply, erection & fabrication of structural steel work for installation of JB & camera with industrial grade painting | Nos. | 1
2013-05-14 | Supply of approx. 15 M (Above ground) Hot Dip Galvanized Poles along with foundation & painting as per the tender specifications. This scope also includes supply of structural steel work for installation of JB & camera with industrial grade painting | Nos. | 1
2014-05-14 | Supply of approx. 30 M (Above ground) Hot Dip Galvanized Poles as per the tender specifications. This scope also includes supply of structural steel work for installation of JB & camera with industrial grade painting (foundation design shall be provided by E & I vendor, foundation construction shall be in IOCL scope) | Nos. | 1
2015-05-14 | suppy of 2'' GI Pipe | Mtrs | 1000
15 | UPS SYSTEM
15.01 | 230V, 1-ph,2-wire- 2X25 kVA Parallel redundant, UPS system with static bypass supply along with suitable Ahrs. rating of Ni-Cd batteries for half hour backup, battery stands, Weatherproof double compression Ni plated brass cable glands and cable lugs for all incoming and outgoing cables etc and as per specification. The UPS shall have two numbers of 230 V output. One 230 V output shall feed to the 230/110 V, 2 kVA, control transformer, the secondary of which will feed to 110 V ACDB (as per SLD). | No. | 1
15.02 | 230V, 1-ph,2-wire- 250A, Cu-Busbar,UPS distribution board (ACDB) as per attached specification and single line diagram PC00128- 1221 along with Weather proof double compression Ni plated brass cable glands and cable lugs for all incoming and outgoing cables. | No. | 1
16 | PLANT COMMUNICATION SYSTEM
16.01 | Supply of Plant Communication system along with Cable gland and lugs etc complete .The system shall comprise of following items as per latest IS/IEC. -Digital central exchange unit with power supply unit and battery back up - 1 set. -Desktop master call station- 1 No. -Weather proof field call station including amplifier with full keypad (12 keys) along with the functional keys- 05 Nos. -Explosion proof field call station including amplifier with full keypad (12 keys) along with the functional keys- 06 Nos -Explosion proof field call station including amplifier with full keypad (12 keys) along with the functional keys & Beacon- 01 Nos. -Weather proof loudspeaker 25W- 08 Nos. -Explosion proof loudspeaker 25W- 02 Nos. -Provision for interfacing with fire alarm and gas detection system. -Basic software and programming. Any other item not specifically mentioned but requireed for the completeness of the system shall be provided. Above shall be checked and read in conjuction with tender drawing. | LOT | 1
17 | EPABX & TELEPHONE
17.01 | Supply of EPABX System along with operator console, Battery, Battery Charger, junction boxes etc and required accessories including supply of suitbale size cable glands, cable lugs, as per scope of supply. EPABX shall be placed in CHM Room and telephone system cables shall be hooked between telephone system from CHM rooom to all telephone (hardwares to fulfill the system requirement) locations. | Lot. | 1
17.02 | Analog telephone with LCD display, incoming call memory, outgoing call memory, Redial & pause function, 5 types of ringing tone for selection of intercom & parallel call transfer, volume control, caller ID Instrument and other standard features. | No. | 1
17.03 | Analog telephone with Redial , recall & pause function, intercom parallel call transfer facility, volume control etc and other standard features. | No. | 1
17.04 | Roset box with voice tag & face plate | No. | 1
17.05 | Supply of armoured communication cable, junction boxes with suitable cable glands & lugs & associated PVC slotted channel with cover with structured cable laying - Lot. Quanteties shown hear are estimated only. Vendor shall provide actual quanties as per site requirement. This item is to be cosider as lumsum only.
17.05.1 | 1) 2Px 0.5 mm dia. | Mtrs. | 100
17.05.2 | 2) 4P x 0.5 mm dia. | Mtrs. | 300
17.05.3 | 3) 10Px 0.5 mm dia. | Mtrs. | 300
14.1.6 | PVC conduit casing pipe | Mtrs. | 300
18 | INTRINSCIALLY SAFE (IP55)WALKIE-TALKIE SUITABLE FOR HAZARDOUS AREA DEFINED AS ZONE1, GAS GROUP IIA/IIB,TEMPERATURE CLASS T3 OF MOTOROLA MAKE INCLUDING LISONING AND OBTAINING LICENSE FROM DOT. (OFFICIAL FEE FOR LICENSE IF ANY SHALL BE PAID BY IOCL)
18.1 | Motorola GP 328 Intrinsically safe VHF handheld radio with 1800 mAh battery Tri Chemistry Charger with Adapter & Antenna-Genuine Motorola make | Nos. | 6
18.2 | Motorola GM 338 Fixed Station with Fist Mic,12V/10A Power supply unit cum battery charger with all accessories (maintenance free) (Base Station) | No. | 1
18.3 | Motorola GP 328 spare battery with 1800 mAh capacity of Genuine Motorola Make | Nos. | 3
19 | CABLE GLANDS
19.1 | Supply of weather proof double compression Ni plated brass cable gland of the following sizes of XLPE,Arm. FRLS cables.
19.1.1 | 01P X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , OVERALL SHIELDED , SIGNAL CABLE | Nos. | 54
19.1.2 | 02C X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , CONTROL CABLE | Nos. | 48
19.1.3 | 02P X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , OVERALL SHIELDED , SIGNAL CABLE | Nos. | 3
19.1.4 | 04C X 2.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , CONTROL CABLE | Nos. | 31
19.1.5 | 05C X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , CONTROL CABLE | Nos. | 19
19.1.6 | 12C X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , CONTROL CABLE | Nos. | 11
19.2 | Supply of Flameproof double compression nickel plated brass cable gland suitable for following XLPE , FRLS cable sizes & as per relevant IS for hazardous area Zone-1,IIA/IIB,T3.
19.2.1 | 01P X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , OVERALL SHIELDED , SIGNAL CABLE | Nos. | 54
19.2.2 | 01T X 2.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , OVERALL SHIELDED , SIGNAL CABLE | Nos. | 62
19.2.3 | 02C X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , CONTROL CABLE | Nos. | 48
19.2.4 | 04P X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , OVERALL SHIELDED , SIGNAL CABLE | Nos. | 2
19.2.5 | 06P X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , OVERALL SHIELDED , SIGNAL CABLE | Nos. | 8
19.2.6 | 06T X 2.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , OVERALL SHIELDED , SIGNAL CABLE | Nos. | 8
19.2.7 | 12P X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , OVERALL SHIELDED , SIGNAL CABLE | Nos. | 10
19.2.8 | 12T X 2.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , OVERALL SHIELDED , SIGNAL CABLE | Nos. | 2
20 | SPARES
20.1 | Plant Communication System, Similar as supplied.
20.2 | Flameproof Field Call Station. | Nos. | 1
20.3 | Weatherproof Field Call Station. | Nos. | 1
20.4 | Flameproof Loudspeaker. | Nos. | 1
20.5 | Weatherproof Loudspeaker. | No. | 1
20.6 | Local Control Station (LCS) Similar as Supplied.
20.7 | Flameproof Local control station with Start/Stop Push Button, FRP Canopy with Ammeter. | Nos. | 1
20.8 | Flameproof Local control station,Start/Stop Push Button, FRP Canopy without ammeter. | Nos. | 1
20.9 | Weatherproof Local control station with Start/Stop Push Button, FRP Canopy with Ammeter. | Nos. | 1
20.1 | Weatherproof Local control station,Start/Stop Push Button, FRP Canopy without ammeter. | Nos. | 1
20.11 | Junction Box Similar as Supplied.
20.12 | Digital Meggar (make FLUKE / YAKOGAWA) | Set. | 1
20.13 | Tongue Tester (make FLUKE / YAKOGAWA) | No. | 1
20.14 | Digital Multimeter (make FLUKE / YAKOGAWA) | No. | 1
21 | CABLE TRAYS
21.1 | G.I. Perforated Cable Trays , 100 mm deep, 3 mm thick G.I. perforated cable trays (Min. coating 100 microns of zinc) with bend, reducer, coupler plate and other hardware.
b. | 600mm Wide | m | 140
c. | 300mm Wide | m | 60
d. | 150mm Wide | m | 200
e. | 50mm Wide | m | 75
21.2 | 90 deg Horizontal Bend Perforated
b. | 600mm Wide | Nos. | 4
c. | 300mm Wide | Nos. | 6
21.3 | 90 deg Vertical Bend (Inside) Perforated
a. | 600mm Wide | Nos. | 4
b. | 300mm Wide | Nos. | 4
c. | 150mm Wide | Nos. | 12
21.4 | 90 deg Vertical Bend (outside) Perforated
a. | 600mm Wide | Nos. | 4
b. | 300mm Wide | Nos. | 4
c. | 150mm Wide | Nos. | 20
21.5 | TEE Connection Perforated type
a. | 600mm Wide | Nos. | 4
22 | EARTHING ITEMS FOR INSTRUMENTATION
22.1 | Supply of Hot dip Galvanized 10 Holes ∅13mm ground plate 550mmx50mmx6mm earth connection bar with fixing materials/ accessories , SS hardware etc. (min. coating 120 microns of zinc). | Nos. | 12
22.2 | Supply of following Hot dip Galvanized earthing and lightning protection materials along with the accessories conforming to IS & drg. Attachment no.-29 (LPG.ENG.117.06.03.2001) of contract specification Specifications and .(Galvanisation is 910gms/sq. mtr) - 1C x 6 mm2 PVC (Al) cable Green colour | Mtr | 2400
22.3 | Supply of Earthing Lug 1C x 6 mm2 PVC (Al) cable Green colour | Nos. | 250