## Table 1
MIRAJ ENGINEERING SERVICES PVT. LTD.
BOQ-Supply for Electrical work of 2x800MW MEL Ph-II at Singrauli, Madhya Pradesh
Sl. No. | Items Description |  | UOM | Sub summary | QTY
Supply of following items
A | UPS
1 | 5kVA Stand-Alone UPS with SCVS Bypass, battery bank (1X 100%) having 1hr backup along with it's mounting Stainless Steel rack, Battery isolation box & Intercell connectors suitable for batteries and along with required cable & cablibg accessories for UPS, battery bank, UPS ACDB. (For Raw Water reservoir Control room) 5 KVA UPS DB shall have below feeders Incoming : 63 A DP MCCB : 2 nos Outgoing : 16A DP MCB (12 Nos) : 32A DP MCB (4 Nos) : 6A DP MCB (4 Nos) |  | Set | DC system | 1
B | DC System 220 Volt (Battery Charger & Battery Bank)
1 | 50AH, 220V DC Battery (1x100%) & 25A Battery Charger (Dual Float cum boost battery charger) complete with Rack, accessories etc. & 220V DC distribution board. Intercoinnecting DC cable between battery, battery cherger, Battery isolation box and 220V DC distribuion board. 220V DCDB Incoming : 63 A DP MCCB : 1 nos Outgoing : 16A DP MCB (6 Nos) : 32A DP MCB (6 Nos) |  | Set | DC system | 1
C | 11 KV (UE) & 6.6 KV (UE) HT Cable Jointing & End Termination
1 | 11 KV (UE) Heat Shrinkable Indoor End Termination With Double Compression Gland | 1C x 400 sqmm AL | No's | Termination Kit | 270
2 |  | 1C x 300 sqmm AL | No's | Termination Kit | 40
3 |  | 3C x 240 sqmm AL | No's | Termination Kit | 150
4 |  | 3C x 300 sqmm AL | No's | Termination Kit | 10
5 | 11 KV (UE) Heat Shrinkable Outdoor Straight Through Termination | 1C x 400 sqmm AL | No's | Termination Kit | 160
6 |  | 1C x 300 sqmm AL | No's | Termination Kit | 30
7 |  | 3C x 240 sqmm AL | No's | Termination Kit | 90
8 |  | 3C x 300 sqmm AL | No's | Termination Kit | 6
9 | 6.6 KV (UE) Heat Shrinkable Indoor End Termination With Double Compression Gland | 1C x 185 sqmm AL | No's | Termination Kit | 24
10 |  | 3C x 185 sqmm AL | No's | Termination Kit | 100
11 |  | 3C x 300 sqmm AL | No's | Termination Kit | 20
12 | 6.6 KV (UE) Heat Shrinkable Outdoor Straight Through Termination | 1C x 185 sqmm AL | No's | Termination Kit | 2
13 |  | 3C x 185 sqmm AL | No's | Termination Kit | 76
14 |  | 3C x 300 sqmm AL | No's | Termination Kit | 2
15 | 11 KV (UE) Heat Shrinkable Outdoor End Termination Kit for NGR | 1C x 300 sqmm AL | No's | Termination Kit | 16
16 | 6.6 KV (UE) Heat Shrinkable Outdoor End Termination Kit for NGR | 1C x 185 sqmm AL | No's | Termination Kit | 24
17 | 19/33 KV (E)Heat Shrinkable Indoor End Termination With Double Compression Gland | 1C x 400 sqmm AL | No's | Termination Kit | 6
D | Trefoil Cable Clamps (Material PVC)
1 | 11 KV (UE) grade, Aluminium conductor, XLPE insulated, FRLS PVC | 1Cx400 mm2 (Dia - 55mm) | Nos. | Misc | 12000
| sheathed armoured cables | 1Cx300 mm2 (Dia - 45mm) | Nos. | Misc | 2000
2 | 6.6 KV (UE) grade, Aluminium conductor, XLPE insulated, FRLS PVC sheathed armoured cables | 1Cx185 mm2 (Dia - 40mm) | Nos. | Misc | 20
3 | 1,1 KV (UE) grade, Aluminium conductor, XLPE insulated, FRLS PVC sheathed armoured cables | 1Cx630 mm2 (Dia - 45mm) | Nos. | Misc | 5000
4 | 1,1 KV (UE) grade, Aluminium conductor, XLPE insulated, FRLS PVC sheathed armoured cables | 1Cx400 mm2 (Dia - 65mm) | Nos. | Misc | 4000
E | POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule
1 | 1.1kV, 90 Deg.C rating, heavy duty power cables with stranded Copper conductor, extruded XLPE insulation, extruded PVC, FRLS inner sheath (Type-ST2), aluminium round wire armour for single core cables and galvanized steel strip /wire armour for Multi core cables, and extruded PVC, FR-LSH (Type-ST2) overall sheath. | 2Cx2.5 sqmm Cu | Set | Termination Kit | 500
2 |  | 3Cx2.5 sqmm Cu | Set | Termination Kit | 3500
3 |  | 4Cx2.5 sqmm Cu | Set | Termination Kit | 20
4 |  | 2Cx4 sqmm Cu | Set | Termination Kit | 120
5 |  | 3Cx4 sqmm Cu | Set | Termination Kit | 100
6 |  | 4Cx4 sqmm Cu | Set | Termination Kit | 100
7 | 1.1kV, 90 Deg.C rating, heavy duty power cables with stranded Aluminium conductor, extruded XLPE insulation, extruded PVC, FRLS inner sheath (Type-ST2), aluminium round wire armour for single core cables and galvanized steel strip /wire armour for Multi core cables, and extruded PVC, FR-LSH (Type-ST2) overall sheath. | 1Cx630 sqmm Al | Set | Termination Kit | 1100
8 |  | 2CX120 sqmm Al | Set | Termination Kit | 950
9 |  | 2CX16 sqmm Al | Set | Termination Kit | 250
10 |  | 2CX185 sqmm Al | Set | Termination Kit | 100
11 |  | 2CX35 sqmm Al | Set | Termination Kit | 80
12 |  | 2CX50 sqmm Al | Set | Termination Kit | 80
13 |  | 3.5CX50 sqmm Al | Set | Termination Kit | 50
14 |  | 3.5CX70 sqmm Al | Set | Termination Kit | 280
15 |  | 3.5CX95 sqmm Al | Set | Termination Kit | 400
16 |  | 3.5CX150 sqmm Al | Set | Termination Kit | 40
17 |  | 3.5CX185 sqmm Al | Set | Termination Kit | 80
18 |  | 3.5CX240 sqmm Al | Set | Termination Kit | 40
19 |  | 3.5CX300 sqmm Al | Set | Termination Kit | 160
20 |  | 3CX16 sqmm Al | Set | Termination Kit | 600
21 |  | 3CX35 sqmm Al | Set | Termination Kit | 1100
22 |  | 3CX50 sqmm Al | Set | Termination Kit | 40
23 |  | 3CX70 sqmm Al | Set | Termination Kit | 100
24 |  | 3CX95 sqmm Al | Set | Termination Kit | 150
25 |  | 3CX150 sqmm Al | Set | Termination Kit | 30
26 |  | 3CX185 sqmm Al | Set | Termination Kit | 50
27 |  | 3CX240 sqmm Al | Set | Termination Kit | 200
28 |  | 4CX16 sqmm Al | Set | Termination Kit | 200
29 |  | 4CX35 sqmm Al | Set | Termination Kit | 600
30 |  | 4Cx6 sqmm Al | Set | Termination Kit | 40
31 | 1.1kV grade, 85 deg C rating, control cables with stranded copper conductors, PVC Insulation, extruded PVC, FRLS Inner sheath (Type- ST2), round wire/strip armour as specified elsewhere in the specification and extruded PVC, FRLSH overall sheath (Type-ST2). | 3Cx2.5 sqmm Cu | Set | Termination Kit | 100
32 |  | 5Cx2.5 sqmm Cu | Set | Termination Kit | 3000
33 |  | 7Cx2.5 sqmm Cu | Set | Termination Kit | 200
34 |  | 12Cx2.5 sqmm Cu | Set | Termination Kit | 200
35 |  | 9Cx2.5 sqmm Cu | Set | Termination Kit | 500
36 |  | 20Cx2.5 sqmm Cu | Set | Termination Kit | 80
37 |  | 4Cx1.5 sqmm Cu | Set | Termination Kit | 100
F | OFC, Cat-6 Cable & Conduit Laying with Accessories (RJ245 termintion, Splicing etc)
1 | 50 MM PVC Conduit Laying |  | Meters | Conduit | 5000
3 | Splicing/termination with Accessories |  | No's | Misc | 24
G | Base Frame & Cable Tray Supports System with Accessories as per attched General notes and details of GA & Tray Layout Drg's.
1 | MS Steel Support Structure of Sizes (ISA 50x50x6/65x65x6, ISMC-75/100/125/150/200 and Insert plates Etc .) Structures should be Red Oxide & GI Painted: |  | MT | Structure | 600
2 | Supply, Fabrication, Installation of 6mm checkered plate |  | MT | Structure | 30
H | Lightning Protection System
1 | 25x6mm GS Flat |  | Meters | Earthing | 4000
2 | 1.5 Mtr long AL Air Terminal on RCC Roof |  | No's | Lightning Protection | 60
3 | VERTICAL AIR TERMINATION RODS 20 mm DIA, 1000 MM LONG GS |  | No's | Lightning Protection | 20

## Table 2
4 | Non Treated Earth Pit (with 40MM dia 3 Mtr long) including soil excavation and backfilling as per IS3043 (consider depth upto 3.5 Mtr.) | No's | Earthing | 100
5 | Test Links | No's | Lightning Protection | 100
6 | Clamp for Lightning protection 50X6mm GS flat @ 1mtr along with support insulators | No's | Lightning Protection | 2000
7 | Clamp for Lightning protection 25X6mm GS flat @ 1mtr along with support insulators | No's | Lightning Protection | 2500
I | Earthing System
1 | 40 MM MS Rod Laying including Excavation & Backfilling Etc. (consider depth upto 1 Mtr.) | Meters | Earthing | 28000
2 | 65x10mm GS Flat | Meters | Earthing | 19000
3 | 50x10mm GS Flat | Meters | Earthing | 1500
4 | 50x6mm GS Flat | Meters | Earthing | 1500
5 | 25x6 MM GS Flat | Meters | Earthing | 3000
6 | 25x3 MM GS Flat | Meters | Earthing | 2600
7 | ROD ELECTRODE (40mm, 3000mm longrod-MS) | No's | Earthing | 60
8 | 8 SWG Wire | Meters | Earthing | 1000
9 | Treated Earth Pit 65mm dia 3 Mtr. Long GI Pipe including soil excavation and backfilling , charcoal and salt and test link as per IS 3043. | No's | Earthing | 200
10 | PIPE ELECTRODE, 3000 mm LONG 65 mm NB, HEAVY DUTY MS PIPE | No's | Earthing | 36
11 | 6 Sq.mm Copper cable with lugs & hardwares for earthing | Meters | Earthing | 1000
J | Miscellaneous
1 | Civil works (including supply of Cement, brick, Concrete & sand) | Cu. mtr | Misc | 100
2 | Expansion Fastener - M8 x 92 | Nos. | Misc | 300
3 | Expansion Fastener - M10 x 108 | Nos. | Misc | 500
4 | Red Oxide Paint | Ltr | Misc | 30
5 | Paint (Bituminous) | Ltr | Misc | 30
6 | GI Paint or as per Requirpment | Ltr | Misc | 10
7 | FRP Ladder - A type (3 Mtr) | No's | Misc | 6
8 | FRP Ladder - A type (6 Mtr) | No's | Misc | 6
K | Pipes
1 | 100 mm dia. G.I. Pipes [Class C (heavy type)] | Meters | Conduit | 200
2 | 150 mm dia. G.I. Pipes [Class C (heavy type)] | Meters | Conduit | 150
3 | 200 mm dia. G.I. Pipes [Class C (heavy type)] | Meters | Conduit | 100
4 | 65 mm dia. G.I. Pipes [Class C (heavy type)] | Meters | Conduit | 200
5 | 100 mm dia. PVC Pipes (Medium duty) | Meters | Conduit | 120
6 | 150 mm dia. PVC Pipes (Medium duty) | Meters | Conduit | 120
7 | 200 mm dia. PVC Pipes (Medium duty) | Meters | Conduit | 60
8 | 65 mm dia. PVC Pipes (Medium duty) | Meters | Conduit | 60
9 | 100 mm dia. Flexible Pipes | Meters | Conduit | 30
10 | 150 mm dia. Flexible Pipes | Meters | Conduit | 30
11 | 65 mm dia. Flexible Pipes | Meters | Conduit | 30
12 | 100mm dia NP3 Hume Pipes as per IS 459 | Meters | Conduit | 30
13 | 150mm dia HDPE Pipes as per IS 8008 Part-I | Meters | Conduit | 30
L | Safety Equipment
1 | Arc Flash Suit for 11kV Voltage System 40 Cal | Nos. | Misc | 10
2 | Arc Flash Suit for 415V Voltage System 4 Cal | Nos. | Misc | 16
3 | Insulated Rescue Hook | Nos. | Misc | 24
4 | Hand gloves suitable for the operation of 11kV, 6.6kV Voltage : 11000V & 6600V HAND Gloves with Box test in accordance with IEC 61482-1-2, ATPV test in accordance with IEC 61482-1-1, DIN EN 388, DIN EN 407 having Direct incident energy-(class 2) 423 kJ / m2, Extended direct incident energy (Eio)-(class 2) 1050 ... 1390 kJ / m2, ATPV (Arc Thermal Performance Value)-32.8 cal / cm2 | Nos. | Misc | 16
5 | Hand Gloves suitable for 415 Volt Voltage | Nos. | Misc | 22
6 | 11 KV Grade 2.5 mm Thick Insulation Rubber Mat as per IS 15652, Class B Type, Max. Leakage Current as 10 mAmp, Flame retardant type, anti skid | Meters | Misc | 450
7 | 1.1 KV Grade 2 mm Thick Insulation Rubber Mat as per IS 15652, Class B Type, Max. Leakage Current as 10 mAmp, Flame retardant type, anti skid | Meters | Misc | 2000
8 | Shock Treatment charts complete with frame and glass | Nos. | Misc | 120
9 | Danger/Caution boards as per IS : 2251 | Nos. | Misc | 140
10 | LOTO Locks | Nos. | Misc | 200
11 | LOTO BOX | No's | Misc | 10
12 | First aid kit | No's | Misc | 40
M | Fire Sealing Material/Fire rated cable coating
1 | 2 Hours Fire Rated Fire Stop sealing system for opening below panels, switchgears, control panels, cable/cable trays opening Class B type (Wool Sheet/slab Type) | Sq Meter | Misc | 200
2 | 2 Hours Fire rated Fire retardant cable coating compound for cable runs (Class B Type) | Ltr | Misc | 170
N | Illumination Sytem(LED Based)
1 | LED based Illumination System (Indoor & Outdoor) complete with LED Lighting fixtures, Lighting Panels, Lighting Poles, Switch boxes, single phase Receptacles, three phase welding Receptacles, Conduits, Portable emergency Lantern with sealed maintenance free lead acid battery, Cables, Wires, Poles, Earthing wires, etc. Refer Annexure-4 for the detailed BOQ. | Refer Annexure- 4 | Illumination | 1

## Table 3
Annexure 4 - Illumination Sytem (LED Based)
Sl. No. | Items Description | Description | UOM | Total Qty Supply
LED based Illumination System (Indoor & Outdoor) complete with LED Lighting fixtures, Lighting Panels, Lighting Poles, Switch boxes, single phase Receptacles, three phase welding Receptacles, Conduits, Portable emergency Lantern with sealed maintenance free lead acid battery, Cables, Wires, Poles, Earthing wires, etc. (Lighting fixture : Unit rate of installation of Lighting fixtures shall be applicable for the quantity supplied, complete with all the components required for installation e.g. support clamp, lamps, ballast, starter, igniter, terminal blocks, brackets, cable glands and lugs, threaded rods, anchor, clamps & connectors, Strut channels, Spring washers, Nuts, GSS H U Bolts, conduit Hanging clamps, Straight clamps, Z-Purling clamp, S-Hooks etc of required sizes.) All high bay fixtures will have vibration damper.
A | Lighting Fixtures
1 | Luminaire Type FC06 (LED) | Industrial type LED fixture suitable for conduit/ surface/ suspended mounting with integral driver aesthetically designed for Switchgear/ Equipment room/ stair case/ corridors. | Nos. | 2300
2 | Luminaire Type FC26 (LED) | Panel (approx. 1200mm x300mm) decorative LED fixture suitable for recess mounting in false ceiling with integral driver aesthetically designed for Control Room/ Office. | Nos. | 300
3 | Luminaire Type FC30 (LED) | Panel 600mm x600mm decorative LED fixture suitable for recess mounting in false ceiling with integral driver aesthetically designed for Control Room/ Office. | Nos. | 550
4 | Luminaire Type FC32 (LED) | Decorative, surface mounted LED fixture having integral driver | Nos. | 80
5 | Luminaire Type FC81 (LED) | Corrosion proof, totally enclosed type LED fixture with integral driver. | Nos. | 360
6 | Luminaire Type SF63 (LED) | Flood light, Heavy duty type LED fixture with integral driver. | Nos. | 120
7 | Luminaire Type SF64 (LED) | Flood light, Heavy duty type LED fixture with integral driver. | Nos. | 140
8 | Luminaire Type SF66 (LED) | Flood light, Heavy duty type LED fixture with integral driver. | Nos. | 80
9 | Luminaire Type SB11 (LED) | Medium Bay, Industrial type LED fixture with integral driver. | Nos. | 200
10 | Luminaire Type SB02 (LED) | High Bay, Industrial type LED fixture with integral driver. | Nos. | 650
11 | Luminaire Type SB03 (LED) | High Bay, Industrial type LED fixture with integral driver suitable for mounting height> 1Om. | Nos. | 210
12 | Luminaire Type SS61 (LED) | Street light, LED fixture with integral driver. | Nos. | 40
13 | Luminaire Type SS62 (LED) | Street light, LED fixture with integral driver. | Nos. | 600
14 | Luminaire Type SS63 (LED) | Street light, LED fixture with integral driver. | Nos. | 720
15 | Luminaire Type SW41 (LED) | Well glass type, vapour proof LED fixture suitable for Boiler/ ESP platforms | Nos. | 8200
16 | Luminaire Type SW42 (LED) | Well glass type, vapour proof LED fixture suitable for Boiler/ ESP platforms | Nos. | 2500
17 | Luminaire Type MW96 | 1x125 W Mercury, well glass, flame proof increased safety luminaire with vitreous enamelled reflector and cast aluminium alloy LM6 housing for Div. 2 areas along with suitable HPMV lamp. | Nos. | 400
18 | Luminaire Type FC07 | 1x18 W Fluorescent, industrial box type base and vitreous enamelled side reflectors operating on 220V DC input supply along with suitable CFL lamp. | Nos. | 600
19 | Luminaire Type FC33 | 1x18 W Fluorescent, decorative, recessed type with mirror optic reflector operating on 220V DC input supply along with suitable CFL lamp. | Nos. | 160
20 | Luminaire Type FC34 | 1x18 W Fluorescent, dust proof, totally enclosed type with sheet steel housing operating on 220V DC input supply along with suitable CFL lamp. | Nos. | 500
21 | LUMINAIRES TYPE DOWNLIGHTER 18W(LED) | Recessed Mounted Downlighter with Integral driver aesthetically designed for Control Room/ Office * For Downlighter* (LED), nomenclature FC35 (LED) to be used in drawing. | Nos. | 100
22 | COVE LIGHT (LED) - 5 MTR STRIP | COVE LIGHT(LED)# shall be 5 MTR strip per piece. Cove lighting, if required shall be provided for better aesthetics in false ceiling of common control room(CCR) and ESP Control room. # For COVE LIGHT (LED), nomenclature FC36 (LED) to be used in drawing. | Nos. | 200
23 | Emergency Exit lights with LED fittings with sealed maintenance free battery sized to provide 2 hours backup complete with charger, plug, extension card etc housed in enclosure suitable for operation on 240V AC supply. |  | Nos. | 100
24 | Portable emergency lantern with 2x10 W LED lamp with sealed maintenance free Ni-Cd battery sized to provide 4 hours backup complete with charger, plug, extension card etc housed in enclosure suitable for operation on 240V AC supply. |  | Nos. | 25
25 | Wall/ parapet mounted , LED flood light Luminaire having system power consumption not more than 150W , cool white light output 5700-6500K colour temperature, Built in constant current electronic driver, IP-66 Powder coated high pressure die cast aluminium housing with separate driver compartment ,heat sink designed in aluminium extrusion & glare free light output. |  | Nos. | 320
26 | Explosion proof 2x36W LED Tube Light Fixture |  | Nos. | 90
27 | Recessed mounted 2'X2' LED Luminaire having system power consumption not more than 36W , neutral white light output 5500-6500K colour temperature, Built in constant current electronic driver, Powder coated CRCA sheet steel housing, with high efficiency acrylic diffuser for uniform & glare free light output. |  | Nos. | 60
28 | Surface/Suspended Mounted LED light fixture having system power consumption not more than 40W Batten, cool white light output 5500-6500K colour temperature , Built in constant current electronic driver , made of CRCA with high efficiency opel diffuser for uniform & glare free light output. |  | Nos. | 100
29 | Supply of Recessed mounted , Circular LED Luminaire having system power consumption not more than 13W , cool white light output 4000K colour temperature, Built in constant current electronic driver, Powder coated CRCA/AL sheet steel housing with high efficiency acrylic diffuser for uniform & glare free light output. |  | Nos | 50
30 | Wall mounted mirror 10W LED light with 4000K |  | Nos | 50
31 | Emergency lighting Units - With Ni-Cd battery and 2 X 6 W LED lamp |  | Nos | 16
B | Switch boxes for individual control of circuits (Switchboards consisting of switch boxes, switches, switch plates and fixing accessories.)
1 | Type SWB1 |  | Nos. | 160
2 | Type SWB2 |  | Nos. | 60
3 | Type SWB3 |  | Nos. | 20
4 | One no 6A 5 pin power socket with one no 6A Switch having indication including back box, cover plate etc. |  | Nos | 80
5 | One no 6/16A 5 pin power socket with one no 16A Switch having indication including back box, cover plate etc. |  | Nos | 100
6 | Three no 6A 5 pin power socket with one 16A Switch having indication including back box, cover plate etc. |  | Nos | 120
7 | Switch Box Enclosure 2 M with plate |  | Nos | 16
8 | Switch Box Enclosure 4 M with plate |  | Nos | 16
9 | Switch Box Enclosure 6 M with plate |  | Nos | 16
10 | Switch Box Enclosure 8 M with plate |  | Nos | 16
11 | Switch Box Enclosure 10 M with plate |  | Nos | 16
C | Junction boxes
1 | Type JB-F | Provided with four (4) way stud type terminals for terminating upto 2 nos. 10 mm2 stranded aluminium conductors on each terminal, suitable for outdoor installations. | Nos. | 16800
2 | Type JB-FE | Same as above JB-F but with an additional epoxy coating of 50 micron thickness. | Nos. | 360
3 | Type JB-S | Provided with four (4) way stud type terminals, each terminal suitable for terminating upto two nos. of 3.5Cx50 mm2 stranded aluminium conductors & with one no.6A HRC fuse and link. | Nos. | 320
4 | Type A - GI junction boxes | Size of junction box shall be 125mm x 125mm. Terminals of the JB shall be suitable for 4 sqmm cable. | NOS. | 200
5 | Type B - GI junction boxes | Size of junction box shall be 125mm x 125mm. Terminals of the JB shall be suitable for 4 sqmm cable. | NOS. | 300
6 | Type C (GI Type for Street Lighting Poles) junction boxes | Size of junction box shall be 250x250mm. Terminals of the JB shall be suitable for 16 sqmm cable. | NOS. | 360
D | Receptacles
1 | Type RA |  | Nos. | 1000
2 | Type RA (Flame proof) |  | Nos. | 20
3 | Type RB |  | Nos. | 232
4 | Type RC |  | Nos. | 216
5 | Type RC (Flame proof) |  | Nos. | 6
6 | 32 A, 240V, 5 pin, surface/recess mounting industrial type receptacle with a safety cover and a switch/MCB in FRP/Sheet steel enclosure having degree of protection of IP 55. |  | Nos. | 100
7 | 63 A, 415V, 4P with earth, surface/recess mounting 5 pin, industrial type receptacle with spring operated cover, interlocks, ELCB (100mA) switch, fuse units with plug in FRP / Sheet steel enclosure having degree of protection of IP 55. |  | Nos. | 40
E | Ceiling fans with electronic regulators & down rod etc.
1 | 1200 mm sweep |  | Nos. | 8
2 | 1400 mm sweep |  | Nos. | 16
3 | Pedestal Fan | Pedestal Fan will have 400mm Sweep (50-65 Wattage). | Nos. | 8
F | 24V supply module & lamps unit complete with all accessories Each 24V A.C. supply module shall have one (1) no dry type two winding transformer and necessary terminals for incoming and outgoing connections. The 240V terminals of 24V AC supply module shall be fed from AC emergency lighting panels (ACELP). Details of 24V A.C. supply modules shall be as given below: Module type: Portable type/ Fixed type with receptacle distribution panel Transformer rating: 500 VA, Transformer voltage ratio: 240/26.5 Volt Primary side isolation: DP MCB with HRC fuse, Isolation rating: 16A, HRC fuse rating: 6A Secondary side isolation: SPN MCB with HRC fuse, Isolation rating: 6A, HRC fuse rating: 16A
1 | Fixed type 24V supply modules |  | Nos. | 60
2 | Portable type 24V supply modules |  | Nos. | 20
3 | Portable halogen lamp unit | 24V portable halogen lamp unit along with flexible copper cable shall be supplied as per details below: Lamp wattage: 40 W Cable size: 2.5 sq. mm Stranded copper Cable length: 20 meter | Nos. | 20
4 | 5A, 24V industrial type sockets |  | Nos. | 240
G | Wires
1 | 1.5 sq.mm (Cu) 1.1kV grade,XLPE insulated stranded copper wires |  | Mtrs | 3000
2 | 2.5 sq.mm (Cu) 1.1kV grade,XLPE insulated stranded copper wires |  | Mtrs | 5500
3 | 4 sq.mm (Cu) 1.1kV grade,XLPE insulated stranded copper wires |  | Mtrs | 2000
H | Street lighting Pole
1 | Street lighting Double arm Swaged tubular galvanized steel pole (9 mtr. above ground) including foundation along with necessary pipe-reducer / fixing-bracket for fixing the Luminaire, weather proof junction box with fixing brackets, 3mtr. long 40mm dia MS rod, 25x3mm GI flat, DP 6A MCB, 1.5Sq.mm FRLS Copper wire, 2nos. 2 mtr. long 50mm dia GI Pipe for cable entry, Base plate, Foundation Bolts, nuts etc. with 2x150W LED Street lighting fixture IP-65 FRP junction box shall be provided with necessary terminal suitable for termination of 2nos. of 4Cx35Sq.mm Al. Armoured. Cable. |  | Nos. | 60
2 | Street lighting Single arm Swaged tubular galvanized steel pole (9 mtr. above ground) including foundation along with necessary pipe-reducer / fixing-bracket for fixing the Luminaire, weather proof junction box with fixing brackets, 3mtr. long 40mm dia MS rod, 25x3mm GI flat, DP 6A MCB, 1.5Sq.mm FRLS Copper wire, 2nos. 2 mtr. long 50mm dia GI Pipe for cable entry, Base plate, Foundation Bolts, nuts etc. with 150W LED Street lighting fixture IP-65 FRP junction box shall be provided with necessary terminal suitable for termination of 2nos. of 4Cx35Sq.mm Al. Armoured. Cable. |  | Nos. | 300
3 | Half pole, bracket, CRCA junction box of IP 55 with loop in loop out facility & accessories for periphery lighting (with 70 W LED Medium Bay Lamp) |  | Nos | 50
4 | J-Type Pole 3 Meter GI Type with Junction box |  | Nos. | 30
5 | J-Type Pole 2 Meter GI Type with Junction box |  | Nos. | 40
I | High Mast
1 | 20 M High Mast hot dip galvanized Raising/Lowering type Lighting mast having galvanized lantern carriage arrangement, integral power tool, 24 nos 200W LED light, Aviation obstruction light 2 nos, lightning protection, earthing, wire, civil foundation works and Feeder pillar, control panel with raise/ lower mechanism.Control panel housing suitable control circuit for the operation of the mast, precision timer for automatic On/Off control |  | Nos. | 10
J | Lighting Panels & Receptacles Panels
1 | Lighting Panel: (Type - LP-A) | Double door type RAL 7032 paint shade, wall mounted suitable for flush mounting, bottom cable entry, suitable for pad locking arrangement with following with 415 V AC , 3ph, 4W bus & one 63 A 4P MCB as incomer and 18 nos 20A, 240V Double Pole RCBO 30ma as outgoing in sheet steel enclosure. LP shall have degree of protection of IP 55 | Nos. | 32
2 | Lighting SDB - (Type - LP-C) | Lighting SDB having Incoming : 16 A DPRCBO and Outgoing : 6 A DP MCB (6Nos | Nos. | 10
3 | Street Lighting panel - (Type - LP-F) | Street Lighting panel with 415 V AC , 3ph, 4W bus & one 63A 4P MCB Isolator, 63A TP Contactor , Synchronous timer, Auto/Manual selector switch, photo electric switch, by pass switch for timer/ photo switch, push buttons, indicating lamps, at incomer and 20A, 6 nos. 415V AC 4P RCBO as outgoing feeder in sheet steel enclosure. Light sensor shall be enclosed in separate weather proof enclosure. LP shall have dgree of protection of IP 55 | Nos. | 40
4 | Street Lighting panel - (Type - LP-G) | Street Lighting panel with 415 V AC , 3ph, 4W bus & one 63A 4P MCB, 63A TP Contactor , Synchronous timer, Auto/Manual selector switch, photo electric switch, by pass switch for timer/ photo switch, push buttons, indicating lamps, at incomer and 20A, 6 nos. 240V AC (DP type) RCBO as outgoing feeder in sheet steel enclosure. Light sensor shall be enclosed in separate weather proof enclosure. LP shall have dgree of protection of IP 55 | Nos. | 20
5 | Receptacle panel - (Type - RP-A) | Receptacle panel with 415 V AC , 3ph, 4W bus & 63 A RCBO 100 mA as incomer and 20A, 12 nos. DP MCB as outgoing in sheet steel enclosure. RP shall have dgree of protection of IP 55 | Nos. | 8
6 | Receptacle panel - (Type - RP-B) | Receptacle panel with 415 V AC , 3ph, 4W bus & One 63A TPN 30 mA RCBO isolator incomer and 20 A, 12 nos. 240V AC SP MCB as outgoing in sheet steel enclosure. RP shall have dgree of protection of IP 55 | Nos. | 6
7 | Receptacle panel - (Type - RP-C) | Receptacle panel with 415 V AC , 3ph, 4W bus & One 63A TPN 30mA RCBO isolator incomer and 20 A, 6 nos. 240V AC SP MCB as outgoing in sheet steel enclosure. RP shall have degree of protection of IP 55 | Nos. | 4
K | Supply and installation of following sizes of galvanized steel conduits from lighting panels to lighting fixtures/switchboards/ single phase receptacles including necessary fittings (bends, circular boxes, adaptor, coupler etc) , clamps, saddles & hardwares .
1 | 20mm dia galvanized steel conduits | Thickness - 1.6mm | Mtrs | 600
2 | 25mm dia galvanized steel conduits | Thickness - 1.6mm | Mtrs | 12000
3 | 40mm dia galvanized steel conduits | Thickness - 2mm | Mtrs | 3000
4 | 20 mm DIA flexible steel conduits | Thickness - 1.6mm | Mtrs | 200
5 | 25 mm DIA flexible steel conduits | Thickness - 1.6mm | Mtrs | 800
L | Flexible PVC Conduit (Colour shall be RAL 9002)
1 | 20 mm Dia flexible PVC conduit including necessary fittings (adapter, nipple etc) and hardwares |  | Mtrs | 300
2 | 40 mm Dia flexible PVC conduit including necessary fittings (adapter, nipple etc) and hardwares |  | Mtrs | 300
M | SUB MAINS / CIRCUIT MAINS
Wiring of Submains/ circuit mains in concealed or surface conduit system in 25 mm diameter rigid PVC conduit of medium guage having ISI and FIA approval with all necessary accessories as per IS 9537:3. 1100 V grade FRLS copper flexible wires for Phase, neutral & earth etc., complete The cost of conduit shall be included. The laying cost shall also include civil works such as small chipping work if necessory at site. Flexible PVC conduit shall be used wherever required.
1 | SUB MAINS / CIRCUIT MAINS : DB to first light point (applicable for MCB Controlled point) or DB to first point Switch box or Switchbox to Switchbox
2 | FRLS, 2 runs of 4 sq.mm copper wire + 1 run of 2.5 sq.mm copper wire with 25mm dia. PVC, conduit (From DB TO 20A socket/6+16A Socket) |  | Rmt | 1200
3 | FRLS, 2 runs of 2.5 sq.mm copper wire + 1 run of 1.5 sq.mm copper wire with 25mm dia. PVC, conduit (From DB to Switch Board/ 6A Power Socket, Switchboard to Switchboard) |  | Rmt | 1400
4 | FRLS, 2 runs of 1.5 sq.mm copper wire + 1 run of 1.5 sq.mm copper wire with 20mm dia. PVC, conduit |  | Rmt | 1200
N | Point wiring cum submain / circuit wiring
Wiring with 2 x 1.5 sq.mm PVC insulated 1100 V grade FRLS copper conductor wires and 1 x 1.5 sq.mm PVC insulated earth wire in, 20 mm diameter rigid PVC conduit of medium guage having ISI and FIA approval with all necessary accessories conduit as per IS 9537:3. Height of ceiling varies from 4.5 to 4.8 meters. A separate neutral shall be run for each circuit. Flexible PVC conduit shall be used wherever required. Light/Fan point shall be inclusive of Moduler Switches / Switch Boxes/Back Box/connectors/ Junction Box / ceiling rose / terminations etc. For point length greater than 10 mtr. additional route length to be taken from above line items
1 | Single light point controlled by a 1no 6A switch : |  | Nos | 100
2 | Two light point controlled by a 1no 6A switch : |  | Nos | 140
3 | Three light point controlled by a 1no 6A switch): |  | Nos | 150
4 | Four light points controlled by 1 Nos of 6A switches : |  | Nos | 120
5 | Five light points controlled by 1 Nos of 6A switches : |  | Nos | 24
6 | Exhaust fan point with 6A socket provided near fan and controlled by a 6A switch |  | Nos | 60
O | Following sizes of FRLS XLPE insulated Armoured copper Cable from lighting panels to lighting fixtures/switchboards/ single phase receptacles in conduits including termination at ends using suitable crimping lugs
1 | 1.5 sq.mm 3 Core FRLS XLPE insulated Armoured copper Cable (Outgoing from LP/Looping/earthing) |  | Meter | 2000
2 | 2.5 sq.mm 3 Core Cable FRLS XLPE insulated Armoured copper Cable (Outgoing from LP/Looping) |  | Meter | 7000
3 | 4 sq.mm 3 Core. FRLS XLPE insulated Armoured copper Cable (Outgoing from LP/Looping) |  | Meter | 1200
P | GI type Pre fabricated Cable Tray complete with Coupler Plates, Fasteners, Clamps and Fixing Hardware as required
1 | 100mm wide GI ladder Cable Trays |  | Meter | 300
2 | 150mm wide GI ladder Cable Trays |  | Meter | 400
3 | 300mm wide GI ladder Cable Trays |  | Meter | 500
Q | STRUCTURAL STEEL
1 | Supply, fabrication, erection of MS base frames, supports etc. made out of rolled MS channels, angles, pipes, plates etc. including welding, bolting, riveting, grouting etc. applying one coat of primer and two finished coats of approved epoxy anticorrosive paint . |  | MT | 10
R | EARTHING ITEMS
1 | 14 SWG GS Wire |  | MTRS. | 100000
2 | 3 M long 40mm dia MS rod |  | NOS. | 30
3 | 25X3 mm GS Flat |  | MTRS. | 1200
S | 1.1kV grade, stranded Aluminum / Copper conductor, XLPE insulated, armoured, overall FRLS extruded PVC sheathed cables confirming to IS 7098 Part-I.
1 | 3.5Cx35 Al |  | MTRS. | 1500
2 | 4Cx16 Al |  | MTRS. | 2000
3 | 2Cx4 Cu |  | MTRS. | 1000
4 | 4Cx2.5 Cu |  | MTRS. | 15000
5 | 3Cx2.5 Cu |  | MTRS. | 5000
6 | 2Cx2.5 Cu |  | MTRS. | 3000
T | CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as per cable schedule. (1 Set consisting of 1 double compression brass gland , Nos of Lugs & Material Cu/Al shall be same as number of core of cable & type of cable)
1 | 3.5Cx35 Al |  | Set | 400
2 | 4Cx16 Al |  | Set | 200
3 | 2Cx4 Cu |  | Set | 100
4 | 4Cx2.5 Cu |  | Set | 1700
5 | 3Cx2.5 Cu |  | Set | 180
6 | 2Cx2.5 Cu |  | Set | 100
U | BURRIED CABLE TRENCH
1 | Construction of buried cable trenches of following sizes including excavation and back filling , river sand bedding, spreading of brick etc . 600x750x8000mm |  | cubic meter | -
V | Accessories for (Saddel, PvC Grip, Screw ETC) Saddling Cable & Conduit |  | Lot | 1
W | Ladder
1 | Free standing shall be aluminium ladder, adjustable from 5M to 10M |  | Nos | 4
2 | wheel mounted adjustable aluminium ladder shall be 10M high aluminium ladder. |  | Nos | 4