## Sheet1
section_context_for_this_product_block | full_product_description | core_product_name | size | feature_or_specifications | acronymed_core_product_name | quantity | unit
W ¦ EMULSION PLANT > W1 ¦ FDA SYSTEM | Supply, installation, testing and commissioning of aspiration detector with CMOS imager combined with multiple photodiode for reliable very early warning in a wide range of environments with minimal nuisance alarms. The detector should have 4 pipe inlet and min 100m pipelength support per inlet.The detector should have Smart on-board filter retains dust count and remaining filter life for predictable maintenance& coverage area of min 5000 Sq. | aspiration detector | pipe inlet: 4, pipelength support per inlet: min 100m, coverage area: min 5000 Sq. | imager: CMOS, sensor: multiple photodiode, feature: very early warning, feature: minimal nuisance alarms, feature: Smart on-board filter retains dust count and remaining filter life for predictable maintenance |  | 2.0 | Nos
W ¦ EMULSION PLANT > W1 ¦ FDA SYSTEM | Supply,Installation,Testing & Commissioning of UL/VDS listed CPVC Pipe 25 mm Dia & Pipe Accessories for the Aspiration detection. | cpvc pipe | diameter: 25 mm | standard: UL(underwriters laboratories), standard: VDS, feature: listed, feature: for the Aspiration detection |  | 212.0 | Mtr
W ¦ EMULSION PLANT > W1 ¦ FDA SYSTEM | Supply, erection, fabrication, testing and commission of VOC detector with range of 1 – 1000 ppm isobutylene equivalent.and following accessoriesa) DigiPID internal dust filter (Pack of 5) b) Waterproof Filter Assy, RAEGuard2 PID, Pack of 5 c) DigiPID Teflon UV electrode shield pack of 10 d) DigiPID Dust Cover e) Air Drying Pre Filter Kit f) DigiPID external water trap filter (Pack of 5) | voc detector | range: 1 – 1000 ppm isobutylene equivalent | accessories: DigiPID internal dust filter (Pack of 5), accessories: Waterproof Filter Assy, RAEGuard2 PID, Pack of 5, accessories: DigiPID Teflon UV electrode shield pack of 10, accessories: DigiPID Dust Cover, accessories: Air Drying Pre Filter Kit, accessories: DigiPID external water trap filter (Pack of 5) |  | 3.0 | Nos
W ¦ EMULSION PLANT > W1 ¦ FDA SYSTEM | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable trays |  | material: GI(galvanized iron), feature: for laying all type of cables, feature: including all necessary structural supports |  | 18.0 | Mtr
W ¦ EMULSION PLANT > W2 ¦ PA SYSTEM | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | ip based networkable touch screen paging station |  | feature: selection of zones, feature: supervision of system status, feature: setting of scheduled broadcasts, feature: central exchange with stand by CPU, feature: built-in monitoring loudspeaker, feature: goose-neck microphone, feature: LCD touchscreen display, feature: audio input |  | 1.0 | Nos
W ¦ EMULSION PLANT > W2 ¦ PA SYSTEM | 30 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | horn type speaker | power: 30 W | feature: high efficiency, feature: weather protection IP 65, feature: weatherproof type, feature: suitable for outdoor area |  | 4.0 | Nos
W ¦ EMULSION PLANT > W2 ¦ PA SYSTEM | Rack Mounted 125 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | power amplifier | power: 125 watt | mounting: rack mounted, feature: battery back up, feature: wattage shall be as per requirement |  | 1.0 | Nos
W ¦ EMULSION PLANT > W2 ¦ PA SYSTEM | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | xlpe cu cable | core: 2C, cross section: 1.5 mm2 | feature: multi stranded, feature: shielded, feature: armoured, feature: for power & signal |  | 150.0 | Mtr
W ¦ EMULSION PLANT > W2 ¦ PA SYSTEM | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | dvd player |  | feature: hook up to amplifiers of PA system, feature: for music in the common areas |  | 1.0 | Nos
W ¦ EMULSION PLANT > W2 ¦ PA SYSTEM | Paging Loudspeaker | paging loudspeaker |  |  |  | 1.0 | Nos