## Sheet1
section_context_for_this_product_block | full_product_description | core_product_name | size | feature_or_specifications | acronymed_core_product_name | quantity | unit
U ¦ GARBAGE YARD > U1 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection , testing & commissioning of Deluge valve with dry pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 3/2 way Solenoid Valve, air filter regulator etc. & manual release unit. The valve shall be electro-pneumatic double inter lock system as per scheme drawing. | deluge valve |  | assembly: dry pilot trim, fitted-with: strainer, fitted-with: drain valve, fitted-with: pressure gauge, fitted-with: pressure switch, fitted-with: flame proof 3/2 way solenoid valve, fitted-with: air filter regulator, fitted-with: manual release unit, system: electro-pneumatic double inter lock
U ¦ GARBAGE YARD > U1 ¦ FOAM WATER SPRAY SYSTEM | 80 mm NB | deluge valve | size: 80 mm NB |  |  | 1.0 | Nos
U ¦ GARBAGE YARD > U1 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. | gate valve |  | material: cs(carbon steel), standard: API 600, class: 150, end-connection: matching flanges, included: nuts & bolts
U ¦ GARBAGE YARD > U1 ¦ FOAM WATER SPRAY SYSTEM | 80 mm NB | gate valve | size: 80 mm NB |  |  | 3.0 | Nos
U ¦ GARBAGE YARD > U1 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing and commissioning of Y-Strainer. | y-strainer
U ¦ GARBAGE YARD > U1 ¦ FOAM WATER SPRAY SYSTEM | 80 mm NB | y-strainer | size: 80 mm NB |  |  | 1.0 | Nos
U ¦ GARBAGE YARD > U1 ¦ FOAM WATER SPRAY SYSTEM | Supply,installation,testing and commissioning of Foam Sprinkler nozzle with necessary threaded fittings as per drawing. The sprinkler shall be Open Aspiration, Pendent type, K-42 with standard spray angle.End connection 1/2" NPT/BSP.UL/FM Approved. | foam sprinkler nozzle |  | feature: open aspiration, type: pendent, k-factor: 42, spray angle: standard, end connection: 1/2" NPT/BSP, certification: UL(underwriters laboratories), certification: FM(factory mutual)
U ¦ GARBAGE YARD > U1 ¦ FOAM WATER SPRAY SYSTEM | Spray nozzle K factor -42 | foam sprinkler nozzle | k-factor: 42 |  |  | 25.0 | Nos
U ¦ GARBAGE YARD > U1 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing and commissioning of Ratio Controller. | ratio controller |  |  |  |  | Nos
U ¦ GARBAGE YARD > U1 ¦ FOAM WATER SPRAY SYSTEM | 80 mm NB | ratio controller | size: 80 mm NB |  |  | 1.0 | Nos
U ¦ GARBAGE YARD > U1 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing and commissioning of Foam bladder tank vertical type ,manufacturing as per ASME, section-VIII part- I. The bladder material shall be BUNA-N. The Bladder Tank shall be supplied along with all necessary valves, Hydraulically Operated Foam Concentrae Control Valve ,fittingss & instruments as per Technical data sheet attached with Tender documents. | foam bladder tank |  | type: vertical, standard: ASME(american society of mechanical engineers) section-VIII part-I, bladder material: BUNA-N, included: all necessary valves, included: hydraulically operated foam concentrate control valve, included: fittings & instruments
U ¦ GARBAGE YARD > U1 ¦ FOAM WATER SPRAY SYSTEM | Capacity of 500 ltr. | foam bladder tank | tank capacity: 500 ltr. |  |  | 1.0 | Nos
U ¦ GARBAGE YARD > U1 ¦ FOAM WATER SPRAY SYSTEM | Supply of AR-AFFF(3%) foam concentrate(PFOS/PFAS free) having sp. Gravity 1.0±.02 g/mlat 20⁰C , PH 7.0-8.5 & viscosity 1200 ±300 cps. | foam concentrate |  | type: AR-AFFF(3%), feature: PFOS/PFAS free, specific gravity: 1.0±.02 g/ml at 20⁰C, pH: 7.0-8.5, viscosity: 1200 ±300 cps |  | 500.0 | Ltr
U ¦ GARBAGE YARD > U1 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. | ms black steel pipe | thickness: 5.4mm | grade: heavy, standard: IS 1239 Part -1(indian standard 1239 Part -1), fittings: elbows, fittings: tees, fittings: flanges, fittings: reducers, fittings: clamps, supports: ms support, fasteners: dash fasteners, coating: two coats of approved primer, coating: two coats of approved paint, pipe joints: grooved with groove coupling, scope: all related civil work and supports of vendor's scope
U ¦ GARBAGE YARD > U1 ¦ FOAM WATER SPRAY SYSTEM | 80 mm NB | ms black steel pipe | size: 80 mm NB |  |  | 45.0 | Mtr
U ¦ GARBAGE YARD > U2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of IR Detector | ir detector |  |  |  | 2.0 | Nos
U ¦ GARBAGE YARD > U2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Manual Call point | manual call point |  | type: analogue addressable |  | 1.0 | Nos
U ¦ GARBAGE YARD > U2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of Hooter cum strobe | hooter cum strobe |  |  |  | 1.0 | Nos
U ¦ GARBAGE YARD > U2 ¦ FDA SYSTEM | Supply, erction, testing & commissioning of analogue addressable Control Module | control module |  | type: analogue addressable |  | 1.0 | Nos
U ¦ GARBAGE YARD > U2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Isolator Module | isolator module |  | type: analogue addressable |  | 2.0 | Nos
U ¦ GARBAGE YARD > U2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Monitor module | monitor module |  | type: analogue addressable |  | 3.0 | Nos
U ¦ GARBAGE YARD > U2 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. | armoured cabling |  | included: lugs, included: laying and termination of both ends
U ¦ GARBAGE YARD > U2 ¦ FDA SYSTEM | 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cabling | size: 2C x 1.5 mm2 | type: loop cable |  | 72.0 | Mtr
U ¦ GARBAGE YARD > U2 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. | armoured cabling |  | included: lugs, included: laying and termination of both ends
U ¦ GARBAGE YARD > U2 ¦ FDA SYSTEM | 2C x 1.5 mm2 Armoured ( Power cable) | armoured cabling | size: 2C x 1.5 mm2 | type: power cable |  | 26.0 | Mtr
U ¦ GARBAGE YARD > U2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of 6 Watt Ceiling mounted Speakers | ceiling mounted speakers | power: 6 Watt |  |  | 4.0 | Nos
U ¦ GARBAGE YARD > U2 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. | armoured cabling |  | included: lugs, included: laying and termination of both ends
U ¦ GARBAGE YARD > U2 ¦ FDA SYSTEM | 2C x 1.5 mm2 Armoured ( Speaker cable) | armoured cabling | size: 2C x 1.5 mm2 | type: speaker cable |  | 36.0 | Mtr
U ¦ GARBAGE YARD > U3 ¦ PA SYSTEM | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | ip based networkable touch screen paging station |  | feature: selection of zones, feature: supervision of system status, feature: setting of scheduled broadcasts, feature: central exchange with stand by CPU, feature: built-in monitoring loudspeaker, feature: goose-neck microphone, feature: LCD touchscreen display, feature: audio input |  | 1.0 | Nos
U ¦ GARBAGE YARD > U3 ¦ PA SYSTEM | 6 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | horn type of speaker | power: 6 W | feature: high efficiency, feature: weather protection IP 65 (weatherproof type, suitable for outdoor area) |  | 4.0 | Nos
U ¦ GARBAGE YARD > U3 ¦ PA SYSTEM | Rack Mounted 125 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | power amplifier | power: 125 watt | mounting: rack mounted, feature: battery back up, note: wattage shall be as per requirement |  | 1.0 | Nos
U ¦ GARBAGE YARD > U3 ¦ PA SYSTEM | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | xlpe cu cable | core: 2C, cross section: 1.5 mm2 | conductor: multi stranded, feature: shielded, feature: armoured, application: for power & signal |  | 50.0 | Mtr
U ¦ GARBAGE YARD > U3 ¦ PA SYSTEM | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | dvd player |  | feature: hook up to amplifiers of PA system for music in the common areas |  | 1.0 | Nos
U ¦ GARBAGE YARD > U3 ¦ PA SYSTEM | Paging Loudspeaker | paging loudspeaker |  |  |  | 1.0 | Nos