## Sheet1
section_context_for_this_product_block | full_product_description | core_product_name | size | feature_or_specifications | acronymed_core_product_name | quantity | unit
X ¦ PLC AUTOMATION | SUPPLY & INSTALLATION OF PLC BASED DV CONTROL PANEL FOR FOAM SPRINKLER SYSTEM AND FIRE WATER PUMPING SYSTEM INTERGRATION PANEL WITH PLC. Supply,Installation,Termination of cable,Testing and Commissioning of PLC Based Deluge Valve Control Panel with accessories. The panel should have local push botton switched for emergency operation from panel.Panel and associated accessories shall be designed to withstand environmental conditions at site.Panel in open areas shall be weatherproof to IP-65 as per IS/ IEC-60529. Canopy/Shed of adequate sizes shall be provided for each panel to protect from weather, the cost of the same shall be included in the panel cost.No extra payment shall be made for providing fixture , fittings & accessories. PLC Based DELUGE VALVE CONTROL PANEL should contain the following:- 1. Programmable Logic Controller. 2.Solid State type or microprocessor based programmable type Alarm Annunciator with sounder. 3.UPS. 4.Cables (Power & Control) Specification of Programmable Logic Controller (PLC) : 1.Input Power: 24vdc,Redundant Supply. 2.Application capabilities with up to 7 expansion I/O modules for a maximum of 256 discrete I/O. 3.Up to 6 embedded 100 kHz highspeed counters (on controllers with dc inputs) 4.2 Serial ports with DF1/ DH485/Modbus RTU/DNP3/ASCII protocol support. 5.Ethernet port provides you with EtherNet/IP, DNP3 over IP and Modbus TCP/IP protocol support as well as web server and email capabilities. 6.Built-in LCD with backlight allows you to view controller and I/O status, and provides a simple interface for messages, bit / integer monitoring and manipulation. 9.Memory:non-volatile battery backed RAM. 10.online editing:yes. 11.Operating Temp.:-20°C...+60°C. 12.Storage Temp:-40°C (or -30°C)...+85°C. Specification of Solid State type or microprocessor based programmable type Alarm Annunciator with sounder: Window display shall be back lighted incandescent lamps or cluster LED type integral power supply. Specification of UPS: 1.Alarm Condition: 1 hours. 2.Standalone Condition: 4 Hours. | plc based deluge valve control panel |  | system: foam sprinkler system and fire water pumping system integration, feature: local push button switches for emergency operation, feature: weatherproof to IP-65, standard: IS/IEC-60529 (indian standard/international electrotechnical commission), feature: canopy/shed for weather protection, feature: no extra payment for fixture, fittings & accessories, contains: programmable logic controller, contains: solid state or microprocessor based programmable alarm annunciator with sounder, contains: UPS, contains: cables (power & control), programmable logic controller input power: 24vdc, programmable logic controller supply: redundant, programmable logic controller expansion: up to 7 expansion I/O modules (max 256 discrete I/O), programmable logic controller counters: up to 6 embedded 100 kHz highspeed counters (on controllers with dc inputs), programmable logic controller serial ports: 2 (DF1/DH485/Modbus RTU/DNP3/ASCII protocol support), programmable logic controller ethernet port: EtherNet/IP, DNP3 over IP, Modbus TCP/IP, web server, email, programmable logic controller display: built-in LCD with backlight, programmable logic controller memory: non-volatile battery backed RAM, programmable logic controller online editing: yes, programmable logic controller operating temperature: -20°C...+60°C, programmable logic controller storage temperature: -40°C (or -30°C)...+85°C, alarm annunciator display: back lighted incandescent lamps or cluster LED type, alarm annunciator power supply: integral, UPS alarm condition: 1 hour, UPS standalone condition: 4 hours
X ¦ PLC AUTOMATION | For 22 nos. Deluge Valve IO point 3 nos (22 W + 3 S)-SOLVENT PLANT | plc based deluge valve control panel | deluge valve IO points: 22, panel IO points: 3 (22 W + 3 S) | location: solvent plant |  | 2.0 | Set
X ¦ PLC AUTOMATION | For 3 nos. Deluge Valve IO point 1 nos (3 W + 1 S)-RESIN PLANT | plc based deluge valve control panel | deluge valve IO points: 3, panel IO points: 1 (3 W + 1 S) | location: resin plant |  | 1.0 | Set
X ¦ PLC AUTOMATION | For 2 nos. Deluge Valve IO point 1 nos (2 W + 1 S) -,MONOMER & STYRENE | plc based deluge valve control panel | deluge valve IO points: 2, panel IO points: 1 (2 W + 1 S) | location: monomer & styrene |  | 1.0 | Set
X ¦ PLC AUTOMATION | For 4 nos. Deluge Valve IO point 1 nos(4 W + 1 S) -WATER BASED PLANT | plc based deluge valve control panel | deluge valve IO points: 4, panel IO points: 1 (4 W + 1 S) | location: water based plant |  | 2.0 | Sets
X ¦ PLC AUTOMATION | For 2 nos. Deluge Valve IO point 1 nos (2 W + 1 S)-SUBSTATION BUILDING | plc based deluge valve control panel | deluge valve IO points: 2, panel IO points: 1 (2 W + 1 S) | location: substation building |  | 1.0 | Set
X ¦ PLC AUTOMATION | For 1 nos. Deluge Valve IO point 1 nos (1 W + 1 S) -,SOFA AREA | plc based deluge valve control panel | deluge valve IO points: 1, panel IO points: 1 (1 W + 1 S) | location: sofa area |  | 1.0 | Set
X ¦ PLC AUTOMATION | For 1 nos. Deluge Valve IO point 1 nos (1 W + 1 S)-PTC | plc based deluge valve control panel | deluge valve IO points: 1, panel IO points: 1 (1 W + 1 S) | location: ptc |  | 1.0 | Set
X ¦ PLC AUTOMATION | For 1 nos. Deluge Valve IO point 1 nos (1 W + 1 S) -,FG-1 | plc based deluge valve control panel | deluge valve IO points: 1, panel IO points: 1 (1 W + 1 S) | location: fg-1 |  | 1.0 | Set
X ¦ PLC AUTOMATION | For 1 nos. Deluge Valve IO point 1 nos(1 W + 1 S) -,MONOMER COLD ROOM | plc based deluge valve control panel | deluge valve IO points: 1, panel IO points: 1 (1 W + 1 S) | location: monomer cold room |  | 1.0 | Set
X ¦ PLC AUTOMATION | For 2 nos. Deluge Valve IO point 1 nos (2 W + 1 S) - DEG & MEG TANK FIRM | plc based deluge valve control panel | deluge valve IO points: 2, panel IO points: 1 (2 W + 1 S) | location: DEG & MEG tank firm |  | 1.0 | Set
X ¦ PLC AUTOMATION | For 8 nos. Deluge Valve IO point 1 nos (8 W + 1 S) - resin TANK FIRM foam generator & MVWS. | plc based deluge valve control panel | deluge valve IO points: 8, panel IO points: 1 (8 W + 1 S) | location: resin tank firm foam generator & MVWS |  | 1.0 | Set
X ¦ PLC AUTOMATION | For 4 nos. Deluge Valve IO point 1 nos(4 W + 1 S) - SOFA TANK area foam generator. | plc based deluge valve control panel | deluge valve IO points: 4, panel IO points: 1 (4 W + 1 S) | location: sofa tank area foam generator |  | 1.0 | Set
X ¦ PLC AUTOMATION | For 2 nos. Deluge Valve IO point 1 nos(2 W + 1 S) - styrene & monomer tank area foam generator. | plc based deluge valve control panel | deluge valve IO points: 2, panel IO points: 1 (2 W + 1 S) | location: styrene & monomer tank area foam generator |  | 1.0 | Set
X ¦ PLC AUTOMATION | For 2 nos. Deluge Valve IO point 1 nos (2 W + 1 S) - raw material curtain. | plc based deluge valve control panel | deluge valve IO points: 2, panel IO points: 1 (2 W + 1 S) | location: raw material curtain |  | 1.0 | Set
X ¦ PLC AUTOMATION | For 2 Nos. Electric Motor driven Pump,2 Nos. of Diesel Engine driven Pump,2 nos. of Jockey Pumps, Air Compressor running-"ON" & "OFF" Condition. | plc based deluge valve control panel | electric motor driven pumps: 2, diesel engine driven pumps: 2, jockey pumps: 2 | air compressor condition: ON & OFF |  | 1.0 | Set
X ¦ PLC AUTOMATION | SUPPLY & ERECTION OF HMI PC Supply,Installation and Commissioning of HMI PC with all accessories complete in all respect and UPS of suitable capacity capable supply power for atleast 1 hour in Alarm Condition & 4 hours in Standalone Condition. (Two Sets of HMI PC shall be provided in two different Locations, one at Control Room/Security Cabin and another at Admin Block) Specification of HMI PC: 1.Site specific HMI software and provision for stimulation DV System. 2.HMI Software for one user with paper licence. 3.Harddisk:1TB. 4.RAM: 8 GB. 5.Display:21" LED. 6.OS: windows lateset professional version. 7.DVD drive ± R/RW 16X. 8.Processor 32 bit Intel Xeon Quad Core Processor with 2.8 GHz. 9.Graphics NVIDIA Quadro 600 with 1GB video memory. 10.event history:min 1 month. | hmi pc | harddisk: 1TB, ram: 8 GB, display: 21" LED, processor: 32 bit Intel Xeon Quad Core Processor with 2.8 GHz, graphics: NVIDIA Quadro 600 with 1GB video memory | supply: installation and commissioning, accessories: all, UPS: suitable capacity (1 hour alarm, 4 hours standalone), locations: control room/security cabin, admin block, software: site specific HMI software, stimulation DV system, HMI software for one user with paper licence, OS: windows latest professional version, DVD drive: ± R/RW 16X, event history: min 1 month |  | 2.0 | Sets