## Sheet1
section_context_for_this_product_block | full_product_description | core_product_name | size | feature_or_specifications | acronymed_core_product_name | quantity | unit
R ¦ PRE TREATMENT CHEMICAL (PTC) > R1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 150 mm NB | ms black steel pipe | size: 150 mm NB | material: ms(black steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint: grooved with groove coupling, scope: all related civil work, supports etc of vendor's scope |  | 18.0 | Mtr
R ¦ PRE TREATMENT CHEMICAL (PTC) > R1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 80 mm NB | ms black steel pipe | size: 80 mm NB | material: ms(black steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint: grooved with groove coupling, scope: all related civil work, supports etc of vendor's scope |  | 12.0 | Mtr
R ¦ PRE TREATMENT CHEMICAL (PTC) > R1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 25 mm NB | ms black steel pipe | size: 25 mm NB | material: ms(black steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint: grooved with groove coupling, scope: all related civil work, supports etc of vendor's scope |  | 12.0 | Mtr
R ¦ PRE TREATMENT CHEMICAL (PTC) > R1 ¦ HYDRANT SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. Size 150 mm NB | gate valve | size: 150 mm NB | material: cs(carbon steel), standard: api 600, class: 150, flanges: matching, accessories: nuts & bolts |  | 2.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R1 ¦ HYDRANT SYSTEM | Supply, installation, testing and commissioning of CS Non return valve with companion flanges,nuts & bolts and gaskets. Size 150 mm NB | non return valve | size: 150 mm NB | material: cs(carbon steel), flanges: companion, accessories: nuts & bolts, gaskets |  | 1.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R1 ¦ HYDRANT SYSTEM | Supply & installation of SS oblique type single headed Landing valve with 80 mm inlet and 63 mm outlet SS instantaneous male coupling with rubber cap and chain conforming to IS : 5290 including matching flanges, gasket, nuts and bolts complete. | landing valve | inlet: 80 mm, outlet: 63 mm | material: ss(stainless steel), type: oblique, head: single, coupling: ss(stainless steel) instantaneous male, accessories: rubber cap and chain, standard: indian standard 5290, flanges: matching, accessories: gasket, nuts and bolts |  | 3.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R1 ¦ HYDRANT SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. Size 80 mm NB | butterfly valve | size: 80 mm NB | standard: british standard 5155, type: wafer, flanges: matching, accessories: nuts & bolts, fittings: necessary fittings by erection vendor |  | 3.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R1 ¦ HYDRANT SYSTEM | Supply & installation of SS branch pipe with 20 mm nozzle conforming to IS : 903 complete | branch pipe | nozzle: 20 mm | material: ss(stainless steel), standard: indian standard 903 |  | 3.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R1 ¦ HYDRANT SYSTEM | Supply & installation of 63 mm dia rubberized reinforced rubber line hose pipe in 15 m length conforming to IS : 636 Type II ISI marked with gunmetal male and female instantaneous coupling conforming to IS 903 wounded with 18 SWG copper wire complete | hose pipe | diameter: 63 mm, length: 15 m | type: rubberized reinforced rubber line, standard: indian standard 636 type ii, certification: isi, coupling: gunmetal male and female instantaneous, standard (coupling): indian standard 903, wire: 18 swg copper wire |  | 6.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R1 ¦ HYDRANT SYSTEM | Supply & installation of MS Hose Box of fabricated from 16 SWG CRCA sheet double door with lockable arrangements to accommodate 2 RRL hose of 15 m length and one branch pipe painted white inside and red outside with one key. (750X600X250 mm) | hose box | dimensions: 750X600X250 mm | material: ms(mild steel), fabrication: 16 swg crca sheet, door: double, lockable: yes, capacity: 2 rrl hose of 15 m length and one branch pipe, paint: white inside and red outside, accessories: one key |  | 3.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R1 ¦ HYDRANT SYSTEM | Supply & installation of swinging type hose reel drum fabricated from 14 SWG CRCA sheets painted with red colour stove paint 2 coats over 1 coat of primer with 30 m long 20 mm dia rubber hose pipe with with SS self closing shut – off nozzle of 5 mm outlet fixed on wall. | hose reel drum | hose length: 30 m, hose diameter: 20 mm, nozzle outlet: 5 mm | type: swinging, fabrication: 14 swg crca sheets, paint: red colour stove paint 2 coats over 1 coat of primer, hose: rubber, nozzle: ss(stainless steel) self closing shut-off, mounting: fixed on wall |  | 3.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R1 ¦ HYDRANT SYSTEM | Supply and installation of pressure gauge, 1/2 inch bottom entry, of suitable range with ball valves and other accessories. | pressure gauge | bottom entry: 1/2 inch | range: suitable, accessories: ball valves and other accessories |  | 1.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R1 ¦ HYDRANT SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends Size 25NB | globe valve | size: 25NB | material: bronze, standard: indian standard 778, end-type: screwed |  | 5.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R1 ¦ HYDRANT SYSTEM | Supply & installation of 250ltr foam tank filled with 3% AFFF foam concentrate with foam making branch and pick up tube. | foam tank | tank capacity: 250 ltr | foam concentrate: 3% AFFF (aqueous film forming foam), feature: with foam making branch and pick up tube |  | 1.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection , testing & commissioning of Deluge valve with dry pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 3/2 way Solenoid Valve, air filter regulator etc. & manual release unit. The valve shall be electro-pneumatic double inter lock system as per scheme drawing. 150 mm NB | deluge valve | size: 150 mm NB | feature: dry pilot trim assembly, feature: fitted with strainer, feature: drain valve, feature: pressure gauge, feature: pressure switch, feature: flame proof 3/2 way solenoid valve, feature: air filter regulator, feature: manual release unit, feature: electro-pneumatic double inter lock system, as per scheme drawing |  | 1.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R2 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. 150 mm NB | gate valve | size: 150 mm NB | material: cs(carbon steel), standard: API 600, class: 150, end-type: matching flanges, feature: complete with nuts & bolts |  | 3.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R2 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing of Y- Strainer. Size 150 mm NB | y-strainer | size: 150 mm NB |  |  | 1.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R2 ¦ FOAM WATER SPRAY SYSTEM | Supply,installation,testing and commissioning of Foam Sprinkler nozzle with necessary threaded fittings as per drawing. The sprinkler shall be Open Aspiration, Pendent type, K-42 with standard spray angle.End connection 1/2" NPT/BSP.UL/FM Approved. Spray nozzle K factor -42 | foam sprinkler nozzle | k factor: 42 | feature: open aspiration, type: pendent, spray angle: standard, end connection: 1/2" NPT/BSP, certification: UL(underwriters laboratories), certification: FM(factory mutual), feature: with necessary threaded fittings as per drawing |  | 59.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R2 ¦ FOAM WATER SPRAY SYSTEM | Supply,installation and commissioning of UL/FM approved Quartzoid Bulb Detector for K factor-80. Temp rating 68 deg C | quartzoid bulb detector | k factor: 80 | certification: UL(underwriters laboratories), certification: FM(factory mutual), temperature rating: 68 deg C |  | 59.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R2 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing and commissioning of Ratio Controller. 150NB | ratio controller | size: 150NB |  |  | 1.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R2 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing and commissioning of Foam bladder tank vertical type ,manufacturing as per ASME, section-VIII part- I. The bladder material shall be BUNA-N. The Bladder Tank shall be supplied along with all necessary valves, Hydraulically Operated Foam Concentrae Control Valve ,fittingss & instruments as per Technical data sheet attached with Tender documents. Capacity of 2100 ltr. | foam bladder tank | capacity: 2100 ltr | type: vertical, manufacturing standard: ASME(american society of mechanical engineers) section-VIII part-I, bladder material: BUNA-N, feature: supplied along with all necessary valves, feature: hydraulically operated foam concentrate control valve, feature: fittings & instruments as per technical data sheet attached with tender documents |  | 1.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications; 150 NB | gi c class pipe | size: 150 NB | class: heavy class, standard: indian standard 1239, fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, fixing: clamps to ms brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, location: above ground, specification: as per drawing |  | 12.0 | Mtr
R ¦ PRE TREATMENT CHEMICAL (PTC) > R2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications; 100 NB | gi c class pipe | size: 100 NB | class: heavy class, standard: indian standard 1239, fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, fixing: clamps to ms brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, location: above ground, specification: as per drawing |  | 18.0 | Mtr
R ¦ PRE TREATMENT CHEMICAL (PTC) > R2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications; 80 NB | gi c class pipe | size: 80 NB | class: heavy class, standard: indian standard 1239, fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, fixing: clamps to ms brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, location: above ground, specification: as per drawing |  | 24.0 | Mtr
R ¦ PRE TREATMENT CHEMICAL (PTC) > R2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications; 65 NB | gi c class pipe | size: 65 NB | class: heavy class, standard: indian standard 1239, fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, fixing: clamps to ms brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, location: above ground, specification: as per drawing |  | 24.0 | Mtr
R ¦ PRE TREATMENT CHEMICAL (PTC) > R2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications; 50 NB | gi c class pipe | size: 50 NB | class: heavy class, standard: indian standard 1239, fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, fixing: clamps to ms brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, location: above ground, specification: as per drawing |  | 18.0 | Mtr
R ¦ PRE TREATMENT CHEMICAL (PTC) > R2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications; 40NB | gi c class pipe | size: 40 NB | class: heavy class, standard: indian standard 1239, fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, fixing: clamps to ms brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, location: above ground, specification: as per drawing |  | 66.0 | Mtr
R ¦ PRE TREATMENT CHEMICAL (PTC) > R2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications; 25NB | gi c class pipe | size: 25 NB | class: heavy class, standard: indian standard 1239, fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, fixing: clamps to ms brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, location: above ground, specification: as per drawing |  | 284.0 | Mtr
R ¦ PRE TREATMENT CHEMICAL (PTC) > R2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope.; 80 mm NB | ms black steel pipe | size: 80 mm NB, thickness: 5.4mm | material: ms(mild steel), finish: black, grade: heavy, standard: indian standard 1239 part-1, fittings included: elbows, tees, flanges, reducers, clamps, ms support dash fasteners, paint: two coats approved primer, two coats approved paint, joints: grooved with groove coupling, civil work: vendor's scope |  | 24.0 | Mtr
R ¦ PRE TREATMENT CHEMICAL (PTC) > R2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope.; 65 mm NB | ms black steel pipe | size: 65 mm NB, thickness: 5.4mm | material: ms(mild steel), finish: black, grade: heavy, standard: indian standard 1239 part-1, fittings included: elbows, tees, flanges, reducers, clamps, ms support dash fasteners, paint: two coats approved primer, two coats approved paint, joints: grooved with groove coupling, civil work: vendor's scope |  | 12.0 | Mtr
R ¦ PRE TREATMENT CHEMICAL (PTC) > R2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope.; 50 mm NB | ms black steel pipe | size: 50 mm NB, thickness: 5.4mm | material: ms(mild steel), finish: black, grade: heavy, standard: indian standard 1239 part-1, fittings included: elbows, tees, flanges, reducers, clamps, ms support dash fasteners, paint: two coats approved primer, two coats approved paint, joints: grooved with groove coupling, civil work: vendor's scope |  | 18.0 | Mtr
R ¦ PRE TREATMENT CHEMICAL (PTC) > R3 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved red oxide primer and two coats of approved red enamel paint and welded joints complete with cutting and making good the complete with cutting and making good the walls, floors or any other surface; 80 mm NB | ms black steel pipe | size: 80 mm NB, thickness: 5.4mm | material: ms(mild steel), finish: black, grade: heavy, standard: indian standard 1239 part-1, fittings included: elbows, tees, flanges, reducers, clamps, ms support dash fasteners, paint: two coats approved red oxide primer, two coats approved red enamel paint, joints: welded, installation: cutting and making good walls, floors or any other surface |  | 24.0 | Mtr
R ¦ PRE TREATMENT CHEMICAL (PTC) > R3 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved red oxide primer and two coats of approved red enamel paint and welded joints complete with cutting and making good the complete with cutting and making good the walls, floors or any other surface; 65 mm NB | ms black steel pipe | size: 65 mm NB, thickness: 5.4mm | material: ms(mild steel), finish: black, grade: heavy, standard: indian standard 1239 part-1, fittings included: elbows, tees, flanges, reducers, clamps, ms support dash fasteners, paint: two coats approved red oxide primer, two coats approved red enamel paint, joints: welded, installation: cutting and making good walls, floors or any other surface |  | 12.0 | Mtr
R ¦ PRE TREATMENT CHEMICAL (PTC) > R3 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved red oxide primer and two coats of approved red enamel paint and welded joints complete with cutting and making good the complete with cutting and making good the walls, floors or any other surface; 50 mm NB | ms black steel pipe | size: 50 mm NB, thickness: 5.4mm | material: ms(mild steel), finish: black, grade: heavy, standard: indian standard 1239 part-1, fittings included: elbows, tees, flanges, reducers, clamps, ms support dash fasteners, paint: two coats approved red oxide primer, two coats approved red enamel paint, joints: welded, installation: cutting and making good walls, floors or any other surface |  | 18.0 | Mtr
R ¦ PRE TREATMENT CHEMICAL (PTC) > R3 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved red oxide primer and two coats of approved red enamel paint and welded joints complete with cutting and making good the complete with cutting and making good the walls, floors or any other surface; 40 mm NB | ms black steel pipe | size: 40 mm NB, thickness: 5.4mm | material: ms(mild steel), finish: black, grade: heavy, standard: indian standard 1239 part-1, fittings included: elbows, tees, flanges, reducers, clamps, ms support dash fasteners, paint: two coats approved red oxide primer, two coats approved red enamel paint, joints: welded, installation: cutting and making good walls, floors or any other surface |  | 12.0 | Mtr
R ¦ PRE TREATMENT CHEMICAL (PTC) > R3 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved red oxide primer and two coats of approved red enamel paint and welded joints complete with cutting and making good the complete with cutting and making good the walls, floors or any other surface; 25 mm NB | ms black steel pipe | size: 25 mm NB, thickness: 5.4mm | material: ms(mild steel), finish: black, grade: heavy, standard: indian standard 1239 part-1, fittings included: elbows, tees, flanges, reducers, clamps, ms support dash fasteners, paint: two coats approved red oxide primer, two coats approved red enamel paint, joints: welded, installation: cutting and making good walls, floors or any other surface |  | 24.0 | Mtr
R ¦ PRE TREATMENT CHEMICAL (PTC) > R3 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor.; Size 80 mm NB | butterfly valve | size: 80 mm NB | standard: british standard 5155, type: wafer, flanges: matching, fittings: necessary fittings by erection vendor, fasteners: nuts & bolts |  | 1.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R3 ¦ AUTOMATIC SPRINKLER SYSTEM | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts.; Size 80 mm NB | non return valve | size: 80 mm NB | type: wafer, flanges: matching, fasteners: nuts & bolts |  | 1.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R3 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & fixing of paddle type Flow Switch | flow switch |  | type: paddle |  | 1.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R3 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Fixing of Sprinkler Head Pendent type for K factor-80. Temp rating 68 deg C. UL/FM Approved. | sprinkler head pendent type | k factor: 80 | temperature rating: 68 deg C, certification: UL(underwriters laboratories), certification: FM(factory mutual) |  | 18.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R3 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, installation of automatic 25 NB Air Release Valve | air release valve | size: 25 NB | type: automatic |  | 1.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R3 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends, Size 25NB | globe valve | size: 25 NB | material: bronze, standard: IS(indian standard) 778, end connection: screwed |  | 2.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R3 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends, Size 40NB | globe valve | size: 40 NB | material: bronze, standard: IS(indian standard) 778, end connection: screwed |  | 1.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R3 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Erection and testing of Installation Control Valve complete with trims & gong. Size 80 mm NB | installation control valve | size: 80 mm NB | feature: complete with trims & gong |  | 1.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R4 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | multicriteria detector |  | type: analogue addressable |  | 4.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R4 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of IR Detector | ir detector |  |  |  | 7.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R4 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Manual Call point | manual call point |  | type: analogue addressable |  | 4.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R4 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of Hooter cum strobe | hooter cum strobe |  |  |  | 4.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R4 ¦ FDA SYSTEM | Supply, erction, testing & commissioning of analogue addressable Control Module | control module |  | type: analogue addressable |  | 3.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R4 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Isolator Module | isolator module |  | type: analogue addressable |  | 2.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R4 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Monitor module | monitor module |  | type: analogue addressable |  | 9.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R4 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of 6 Watt Ceiling mounted Speakers | ceiling mounted speakers | power: 6 Watt |  |  | 9.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R4 ¦ FDA SYSTEM | Providing & fixing 100Watt Amplifier with necessary accessories. | amplifier | power: 100 Watt | feature: necessary accessories |  | 1.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R4 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cabling | configuration: 2C x 1.5 mm2 | feature: loop cable, feature: complete with lugs, laying and termination of both ends |  | 256.0 | Mtr
R ¦ PRE TREATMENT CHEMICAL (PTC) > R4 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Power cable) | armoured cabling | configuration: 2C x 1.5 mm2 | feature: power cable, feature: complete with lugs, laying and termination of both ends |  | 127.0 | Mtr
R ¦ PRE TREATMENT CHEMICAL (PTC) > R4 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Speaker cable) | armoured cabling | configuration: 2C x 1.5 mm2 | feature: speaker cable, feature: complete with lugs, laying and termination of both ends |  | 140.0 | Mtr
R ¦ PRE TREATMENT CHEMICAL (PTC) > R4 ¦ FDA SYSTEM | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable trays |  | feature: for laying all type of cables, feature: including all necessary structural supports |  | 256.0 | Mtr
R ¦ PRE TREATMENT CHEMICAL (PTC) > R5 ¦ PA SYSTEM | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | ip based networkable touch screen paging station |  | feature: selection of zones, feature: supervision of system status, feature: setting of scheduled broadcasts, feature: central exchange with stand by cpu, feature: built-in monitoring loudspeaker, feature: goose-neck microphone, feature: lcd touchscreen display, feature: audio input |  | 1.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R5 ¦ PA SYSTEM | 15 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | horn type speaker | power: 15 W | feature: high efficiency, feature: weather protection ip 65 (weatherproof type, suitable for outdoor area) |  | 3.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R5 ¦ PA SYSTEM | Rack Mounted 125 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | power amplifier | power: 125 watt | feature: rack mounted, feature: battery back up, feature: wattage shall be as per requirement |  | 1.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R5 ¦ PA SYSTEM | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | xlpe cu cable | configuration: 2C x 1.5 mm2 | feature: multi stranded, feature: shielded, feature: armoured, feature: for power & signal |  | 90.0 | Mtr
R ¦ PRE TREATMENT CHEMICAL (PTC) > R5 ¦ PA SYSTEM | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | dvd player |  | feature: hook up to amplifiers of pa system for music in the common areas |  | 1.0 | Nos
R ¦ PRE TREATMENT CHEMICAL (PTC) > R5 ¦ PA SYSTEM | Paging Loudspeaker | paging loudspeaker |  |  |  | 1.0 | Nos