## Sheet1
section_context_for_this_product_block | full_product_description | core_product_name | size | feature_or_specifications | acronymed_core_product_name | quantity | unit
V ¦ RESIN TANK | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications a ¦ 150 NB | gi pipe | size: 150 NB | class: c class (heavy class), standard: indian standard 1239, fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, fixing: clamps to ms brackets / hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, application: above ground pipes |  | 75.0 | Mtr
V ¦ RESIN TANK | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications b ¦ 100 NB | gi pipe | size: 100 NB | class: c class (heavy class), standard: indian standard 1239, fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, fixing: clamps to ms brackets / hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, application: above ground pipes |  | 106.0 | Mtr
V ¦ RESIN TANK | Supply, erection , testing & commissioning of Deluge valve with dry pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch,dry pilot actuator, air filter regulator etc. & manual release unit. a ¦ Size 150 NB | deluge valve | size: 150 NB | trim assembly: dry pilot, fitted with: strainer, drain valve, pressure gauge, pressure switch, dry pilot actuator, air filter regulator, manual release unit: included |  | 2.0 | Nos
V ¦ RESIN TANK | Supply, erection , testing & commissioning of Deluge valve with dry pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch,dry pilot actuator, air filter regulator etc. & manual release unit. b ¦ Size 100 NB | deluge valve | size: 100 NB | trim assembly: dry pilot, fitted with: strainer, drain valve, pressure gauge, pressure switch, dry pilot actuator, air filter regulator, manual release unit: included |  | 2.0 | Nos
V ¦ RESIN TANK | Providing & fixing Cast Iron Y Strainer. a ¦ Size 150 NB | y strainer | size: 150 NB | material: cast iron |  | 2.0 | Nos
V ¦ RESIN TANK | Providing & fixing Cast Iron Y Strainer. b ¦ Size 100 NB | y strainer | size: 100 NB | material: cast iron |  | 2.0 | Nos
V ¦ RESIN TANK | Supply & fixing of SS-304 FOAM GENERATOR with Minimum flow 120lpm | foam generator |  | material: ss-304, minimum flow: 120 lpm |  | 6.0 | Nos
V ¦ RESIN TANK | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. a ¦ Size 150 NB | gate valve | size: 150 NB | material: cs(carbon steel), standard: api 600, class: 150, flanges: matching, included: nuts & bolts |  | 6.0 | Nos
V ¦ RESIN TANK | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. b ¦ Size 100 NB | gate valve | size: 100 NB | material: cs(carbon steel), standard: api 600, class: 150, flanges: matching, included: nuts & bolts |  | 6.0 | Nos
V ¦ RESIN TANK | Supply, installation, testing and commissioning of Atmospheric Foam tank vertical type ,manufacturing as per ASME, section-VIII part- I. Tank shall be supplied along with all necessary valves, fittingss & instruments as per Technical data sheet attached with Tender documents. a ¦ Capacity of 250 ltr. | atmospheric foam tank | capacity: 250 ltr. | type: vertical, standard: asme section-viii part-i, supplied with: all necessary valves, fittings & instruments, reference: technical data sheet attached with tender documents |  | 2.0 | Nos
V ¦ RESIN TANK | Supply, installation, testing and commissioning of Atmospheric Foam tank vertical type ,manufacturing as per ASME, section-VIII part- I. Tank shall be supplied along with all necessary valves, fittingss & instruments as per Technical data sheet attached with Tender documents. b ¦ Capacity of 150 ltr. | atmospheric foam tank | capacity: 150 ltr. | type: vertical, standard: asme section-viii part-i, supplied with: all necessary valves, fittings & instruments, reference: technical data sheet attached with tender documents |  | 2.0 | Nos
V ¦ RESIN TANK | Supply of AR-AFFF(3%) foam concentrate (PFOS/PFAS free) having sp. Gravity 1.0±.02 g/mlat 20⁰C , pH 7.0-8.5 & viscosity 1200 ±300 cps. | foam concentrate |  | type: ar-afff(3%), feature: pfos/pfas free, specific gravity: 1.0±.02 g/ml at 20⁰c, ph: 7.0-8.5, viscosity: 1200 ±300 cps |  | 800.0 | Ltr
V ¦ RESIN TANK | Supply, installation, testing and commissioning of Inline Inductor a ¦ 150NB | inline inductor | size: 150NB |  |  | 2.0 | Nos
V ¦ RESIN TANK | b ¦ 100 NB | inline inductor | size: 100 NB |  |  | 2.0 | Nos
V2 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, erection , testing & commissioning of Deluge valve with wet pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 3/2 way Solenoid Valve, air filter regulator etc. & manual release unit. The valve shall be electro-pneumatic type. | deluge valve |  | trim assembly: wet pilot, included: strainer, included: drain valve, included: pressure gauge, included: pressure switch, included: flame proof 3/2 way solenoid valve, included: air filter regulator, included: manual release unit, type: electro-pneumatic
V2 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | a ¦ 100 NB | deluge valve | size: 100 NB |  |  | 1.0 | Mtr
V2 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | b ¦ 80 NB | deluge valve | size: 80 NB |  |  | 3.0 | Mtr
V2 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. | gate valve |  | material: cs(carbon steel), standard: API 600, class: 150, included: matching flanges, included: nuts & bolts
V2 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | a ¦ 100 NB | gate valve | size: 100 NB |  |  | 3.0 | Mtr
V2 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | b ¦ 80 NB | gate valve | size: 80 NB |  |  | 9.0 | Mtr
V2 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Y- Strainer | y strainer
V2 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | a ¦ 100 NB | y strainer | size: 100 NB |  |  | 1.0 | Mtr
V2 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | b ¦ 80 NB | y strainer | size: 80 NB |  |  | 3.0 | Mtr
V2 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply,installation and commissioning of UL/FM approved Medium Velocity Water Spray Nozzle. UL/FM Approved. | medium velocity water spray nozzle |  | certification: UL(underwriters laboratories), certification: FM(factory mutual)
V2 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | a ¦ MVWS nozzle K factor 18, spray angle 100⁰ | medium velocity water spray nozzle | k factor: 18, spray angle: 100⁰ |  |  | 91.0 | Nos
V2 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply,installation and commissioning of UL/FM approved Quartzoid Bulb Detector for K factor-80. Temp rating 68 deg C | quartzoid bulb detector | k factor: 80, temperature rating: 68 deg C | certification: UL(underwriters laboratories), certification: FM(factory mutual) |  | 91.0 | Nos
V2 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications | gi "c" class pipes |  | class: heavy, standard: IS 1239, fittings: threaded or grooved, included: elbow, included: tee, included: reducer, included: welding flanges, included: clamps, included: ms brackets / hangers, included: steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, location: above ground
V2 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | a ¦ 100 NB | gi "c" class pipes | size: 100 NB |  |  | 14.0 | Mtr
V2 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | b ¦ 80 NB | gi "c" class pipes | size: 80 NB |  |  | 60.0 | Mtr
V2 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | c ¦ 65 NB | gi "c" class pipes | size: 65 NB |  |  | 210.0 | Mtr
V2 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. | ms black steel pipe | thickness: 5.4mm | grade: heavy, standard: IS 1239 Part -1, fittings: elbows, fittings: tees, fittings: flanges, fittings: reduces clamps, fittings: ms support dash fasteners, paint: two coats of approved primer, paint: two coats of approved paint, joints: grooved with groove coupling, civil work: vendor's scope
V2 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | a ¦ 100 mm NB | ms black steel pipe | size: 100 mm NB |  |  | 24.0 | Mtr
V2 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | b ¦ 80 mm NB | ms black steel pipe | size: 80 mm NB |  |  | 86.0 | Mtr
V2 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | c ¦ 25 mm NB | ms black steel pipe | size: 25 mm NB |  |  | 230.0 | Mtr
V2 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, erction, testing & commissioning of analogue addressable Control Module | analogue addressable control module |  |  |  | 4.0 | Nos
V2 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, erction, testing & commissioning of analogue addressable Monitor Module | analogue addressable monitor module |  |  |  | 4.0 | Nos
V3 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Monitor module | analogue addressable monitor module |  |  |  | 9.0 | Nos
V3 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of IR Detector | ir detector |  |  |  | 9.0 | Nos
V3 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. | armoured cabling |  | feature: complete with lugs, feature: laying and termination of both ends
V3 ¦ FDA SYSTEM | a ¦ 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cabling | size: 2C x 1.5 mm2 | type: loop cable |  | 60.0 | Mtr
V3 ¦ FDA SYSTEM | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable trays |  | feature: for laying all type of cables as indicated above, feature: including all necessary structural supports |  | 62.0 | Mtr