## Sheet1
section_context_for_this_product_block | full_product_description | core_product_name | size | feature_or_specifications | acronymed_core_product_name | quantity | unit
O ¦ SECURITY ROOM > O1 ¦ FDA SYSTEM | Supply, installation, testing and commissioning of Microprocessor based 6 Loop expandable upto 10 loops,Networkable analogue addressable type fire alarm control panel with 640 character LCD display.Detectors can be any mix of ion, photo, laser photo,thermal, or multi-sensor detectors; modules can be addressable pull stations, normally open contact devices,two-wire smoke, notification, or relay modules. Four access levels, Printer Port,RS-485 port for repeater/mimic panel communication,240 volts AC power supply, automatic battery charger, 24 volts sealed lead acid batteries sufficient for 24 hours normal working and then be capable of operating the system for 10 Min during an emergency conditions as required. The Panel shall have compatibility with BACKNET/MODBUS CARD for integration. | fire alarm control panel | loops: 6 (expandable upto 10), lcd display: 640 character | type: microprocessor based, type: networkable analogue addressable, detector compatibility: ion, photo, laser photo, thermal, multi-sensor, module compatibility: addressable pull stations, normally open contact devices, two-wire smoke, notification, relay modules, access levels: four, port: printer port, port: RS-485 (repeater/mimic panel communication), power supply: 240 volts AC, battery: automatic charger, battery: 24 volts sealed lead acid, battery backup: 24 hours normal + 10 min emergency, integration compatibility: BACKNET/MODBUS CARD |  | 1.0 | Nos
O ¦ SECURITY ROOM > O1 ¦ FDA SYSTEM | Providing & fixing of PA console with selector zone facility with necessary accessories. | pa console |  | feature: selector zone facility, accessories: necessary accessories | pa console | 1.0 | Nos
O ¦ SECURITY ROOM > O1 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | multicriteria detector |  | type: analogue addressable |  | 6.0 | Nos
O ¦ SECURITY ROOM > O1 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Manual Call point | manual call point |  | type: analogue addressable |  | 2.0 | Nos
O ¦ SECURITY ROOM > O1 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of Hooter cum strobe | hooter cum strobe |  |  |  | 2.0 | Nos
O ¦ SECURITY ROOM > O1 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of Telephone jack. | telephone jack |  |  |  | 1.0 | Nos
O ¦ SECURITY ROOM > O1 ¦ FDA SYSTEM | Supply, erction, testing & commissioning of analogue addressable Control Module | control module |  | type: analogue addressable |  | 1.0 | Nos
O ¦ SECURITY ROOM > O1 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Isolator Module | isolator module |  | type: analogue addressable |  | 2.0 | Nos
O ¦ SECURITY ROOM > O1 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cabling | cable: 2C x 1.5 mm2 | feature: complete with lugs, laying and termination of both ends, cable type: loop cable |  | 38.0 | Mtr
O ¦ SECURITY ROOM > O1 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Power cable) | armoured cabling | cable: 2C x 1.5 mm2 | feature: complete with lugs, laying and termination of both ends, cable type: power cable |  | 29.0 | Mtr
O ¦ SECURITY ROOM > O1 ¦ FDA SYSTEM | Providing & fixing FRLS CABLING complete with lugs, laying and termination of both ends. 2C x 0.5 mm2 Armoured ( Telephone cable) | frls cabling | cable: 2C x 0.5 mm2 | feature: complete with lugs, laying and termination of both ends, cable type: telephone cable |  | 12.0 | Mtr
O ¦ SECURITY ROOM > O2 ¦ PA SYSTEM | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | ip based networkable touch screen paging station |  | feature: selection of zones, feature: supervision of system status, feature: setting of scheduled broadcasts, feature: central exchange with stand by CPU, feature: built-in monitoring loudspeaker, feature: goose-neck microphone, feature: LCD touchscreen display, feature: audio input |  | 1.0 | Nos
O ¦ SECURITY ROOM > O2 ¦ PA SYSTEM | 6 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | horn type of speaker | power: 6 W | feature: high efficiency, feature: weather protection IP 65, feature: weatherproof type, feature: suitable for outdoor area |  | 3.0 | Nos
O ¦ SECURITY ROOM > O2 ¦ PA SYSTEM | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | xlpe cu cable | core: 2C, cross section: 1.5 mm2 | feature: multi stranded, feature: shielded, feature: armoured, feature: for power & signal |  | 19.0 | Mtr
O ¦ SECURITY ROOM > O2 ¦ PA SYSTEM | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | dvd player |  | feature: hook up to amplifiers of PA system, feature: for music in the common areas |  | 1.0 | Nos
O ¦ SECURITY ROOM > O2 ¦ PA SYSTEM | Paging Loudspeaker | paging loudspeaker |  |  |  | 1.0 | Nos