## Sheet1
section_context_for_this_product_block | full_product_description | core_product_name | size | feature_or_specifications | acronymed_core_product_name | quantity | unit
['J ¦ WATER BASED PLANT', 'J1 ¦ HYDRANT SYSTEM'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 150 mm NB | ms black steel pipe | size: 150 mm NB | material: ms(black steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, scope: all related civil work, supports etc of vendor's scope |  | 12.0 | Mtr
['J ¦ WATER BASED PLANT', 'J1 ¦ HYDRANT SYSTEM'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 80 mm NB | ms black steel pipe | size: 80 mm NB | material: ms(black steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, scope: all related civil work, supports etc of vendor's scope |  | 24.0 | Mtr
['J ¦ WATER BASED PLANT', 'J1 ¦ HYDRANT SYSTEM'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 25 mm NB | ms black steel pipe | size: 25 mm NB | material: ms(black steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, scope: all related civil work, supports etc of vendor's scope |  | 6.0 | Mtr
['J ¦ WATER BASED PLANT', 'J1 ¦ HYDRANT SYSTEM'] | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. Size 150 mm NB | gate valve | size: 150 mm NB | material: cs(carbon steel), standard: api 600, class: 150, flanges: matching, accessories: nuts & bolts |  | 1.0 | Nos
['J ¦ WATER BASED PLANT', 'J1 ¦ HYDRANT SYSTEM'] | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts confirming IS:5312(PN16). Size 150 mm NB | non return valve | size: 150 mm NB | type: wafer, flanges: matching, accessories: nuts & bolts, standard: indian standard 5312(pn16) |  | 1.0 | Nos
['J ¦ WATER BASED PLANT', 'J1 ¦ HYDRANT SYSTEM'] | Supply & installation of SS oblique type single headed Landing valve with 80 mm inlet and 63 mm outlet SS instantaneous male coupling with rubber cap and chain conforming to IS : 5290 including matching flanges, gasket, nuts and bolts complete. | landing valve | inlet: 80 mm, outlet: 63 mm | material: ss(stainless steel), type: oblique, head: single, coupling: ss instantaneous male, accessories: rubber cap and chain, standard: indian standard 5290, flanges: matching, accessories: gasket, nuts and bolts |  | 4.0 | Nos
['J ¦ WATER BASED PLANT', 'J1 ¦ HYDRANT SYSTEM'] | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. Size 80 mm NB | butterfly valve | size: 80 mm NB | standard: british standard 5155, type: wafer, flanges: matching, accessories: nuts & bolts, fittings: necessary fittings by erection vendor |  | 4.0 | Nos
['J ¦ WATER BASED PLANT', 'J1 ¦ HYDRANT SYSTEM'] | Supply & installation of SS branch pipe with 20 mm nozzle conforming to IS : 903 complete | branch pipe | nozzle: 20 mm | material: ss(stainless steel), standard: indian standard 903 |  | 4.0 | Nos
['J ¦ WATER BASED PLANT', 'J1 ¦ HYDRANT SYSTEM'] | Supply & installation of 63 mm dia rubberized reinforced rubber line hose pipe in 15 m length conforming to IS : 636 Type II ISI marked with gunmetal male and female instantaneous coupling conforming to IS 903 wounded with 18 SWG copper wire complete | hose pipe | diameter: 63 mm, length: 15 m | type: rubberized reinforced rubber line, standard: indian standard 636 type ii, certification: isi marked, coupling: gunmetal male and female instantaneous, coupling standard: indian standard 903, wire: 18 swg copper wire |  | 8.0 | Nos
['J ¦ WATER BASED PLANT', 'J1 ¦ HYDRANT SYSTEM'] | Supply & installation of MS Hose Box of fabricated from 16 SWG CRCA sheet double door with lockable arrangements to accommodate 2 RRL hose of 15 m length and one branch pipe painted white inside and red outside with one key. (750X600X250 mm) | hose box | dimensions: 750X600X250 mm | material: ms(mild steel), fabrication: 16 swg crca sheet, door: double, lockable: yes, capacity: 2 rrl hose of 15 m length and one branch pipe, paint: white inside and red outside, accessories: one key |  | 4.0 | Nos
['J ¦ WATER BASED PLANT', 'J1 ¦ HYDRANT SYSTEM'] | Supply & installation of swinging type hose reel drum fabricated from 14 SWG CRCA sheets painted with red colour stove paint 2 coats over 1 coat of primer with 30 m long 20 mm dia rubber hose pipe with with SS self closing shut – off nozzle of 5 mm outlet fixed on wall. | hose reel drum | hose length: 30 m, hose diameter: 20 mm, nozzle outlet: 5 mm | type: swinging, fabrication: 14 swg crca sheets, paint: red colour stove paint 2 coats over 1 coat of primer, hose: rubber, nozzle: ss(self closing shut-off), installation: fixed on wall |  | 4.0 | Nos
['J ¦ WATER BASED PLANT', 'J1 ¦ HYDRANT SYSTEM'] | Supply and installation of pressure gauge, 1/2 inch bottom entry, of suitable range with ball valves and other accessories. | pressure gauge | bottom entry: 1/2 inch | range: suitable, accessories: ball valves and other accessories |  | 1.0 | Nos
['J ¦ WATER BASED PLANT', 'J1 ¦ HYDRANT SYSTEM'] | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends, Size 25NB | globe valve | size: 25NB | material: bronze, standard: indian standard 778, ends: screwed |  | 6.0 | Nos
['J ¦ WATER BASED PLANT', 'J2 ¦ AUTOMATIC SPRINKLER SYSTEM'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope., 150 mm NB | ms black steel pipe | size: 150 mm NB | material: ms(black steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved with groove coupling, scope: all related civil work, supports etc of vendor's scope |  | 121.0 | Mtr
['J ¦ WATER BASED PLANT', 'J2 ¦ AUTOMATIC SPRINKLER SYSTEM'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope., 100 mm NB | ms black steel pipe | size: 100 mm NB | material: ms(black steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved with groove coupling, scope: all related civil work, supports etc of vendor's scope |  | 101.0 | Mtr
['J ¦ WATER BASED PLANT', 'J2 ¦ AUTOMATIC SPRINKLER SYSTEM'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope., 80 mm NB | ms black steel pipe | size: 80 mm NB | material: ms(black steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved with groove coupling, scope: all related civil work, supports etc of vendor's scope |  | 66.0 | Mtr
['J ¦ WATER BASED PLANT', 'J2 ¦ AUTOMATIC SPRINKLER SYSTEM'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope., 65 mm NB | ms black steel pipe | size: 65 mm NB | material: ms(black steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved with groove coupling, scope: all related civil work, supports etc of vendor's scope |  | 286.0 | Mtr
['J ¦ WATER BASED PLANT', 'J2 ¦ AUTOMATIC SPRINKLER SYSTEM'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope., 50 mm NB | ms black steel pipe | size: 50 mm NB | material: ms(black steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved with groove coupling, scope: all related civil work, supports etc of vendor's scope |  | 386.0 | Mtr
['J ¦ WATER BASED PLANT', 'J2 ¦ AUTOMATIC SPRINKLER SYSTEM'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope., 40 mm NB | ms black steel pipe | size: 40 mm NB | material: ms(black steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved with groove coupling, scope: all related civil work, supports etc of vendor's scope |  | 602.0 | Mtr
['J ¦ WATER BASED PLANT', 'J2 ¦ AUTOMATIC SPRINKLER SYSTEM'] | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor., Size150 mm NB | butterfly valve | size: 150 mm NB | standard: british standard 5155, type: wafer, flanges: matching, fittings: necessary fittings by erection vendor |  | 7.0 | Nos
['J ¦ WATER BASED PLANT', 'J2 ¦ AUTOMATIC SPRINKLER SYSTEM'] | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts confirming IS:5312(PN16)., Size150 mm NB | non return valve | size: 150 mm NB | type: wafer, flanges: matching, standard: indian standard 5312(PN16) |  | 7.0 | Nos
['J ¦ WATER BASED PLANT', 'J2 ¦ AUTOMATIC SPRINKLER SYSTEM'] | Supply & fixing of paddle type Flow Switch | flow switch |  | type: paddle |  | 7.0 | Nos
['J ¦ WATER BASED PLANT', 'J2 ¦ AUTOMATIC SPRINKLER SYSTEM'] | Supply,Fixing of Sprinkler Head Pendent type for K factor-160. Temp rating 68 deg C.UL/FM Approved. | sprinkler head pendent type |  | k factor: 160, temperature rating: 68 deg C, certification: UL(underwriters laboratories)/FM(factory mutual) approved |  | 540.0 | Nos
['J ¦ WATER BASED PLANT', 'J2 ¦ AUTOMATIC SPRINKLER SYSTEM'] | Supply, installation of automatic 25 NB Air Release Valve | air release valve | size: 25 NB | type: automatic |  | 1.0 | Nos
['J ¦ WATER BASED PLANT', 'J2 ¦ AUTOMATIC SPRINKLER SYSTEM'] | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends, Size 40NB | globe valve | size: 40NB | material: bronze, standard: indian standard 778, ends: screwed |  | 7.0 | Nos
['J ¦ WATER BASED PLANT', 'J2 ¦ AUTOMATIC SPRINKLER SYSTEM'] | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends, Size 25NB | globe valve | size: 25NB | material: bronze, standard: indian standard 778, ends: screwed |  | 2.0 | Nos
['J ¦ WATER BASED PLANT', 'J2 ¦ AUTOMATIC SPRINKLER SYSTEM'] | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. Size 150 mm NB | gate valve | size: 150 mm NB | material: cs(carbon steel), standard: API 600, class: 150, ends: flanged, feature: complete with nuts & bolts |  | 1.0 | Nos
['J ¦ WATER BASED PLANT', 'J3 ¦ WATER CURTAIN'] | Supply, erection and testing of heavy grade(class-C) pipes of thickness 5.4mm conforming to IS-1239 including all fittings viz. tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer and structural steels for pipe supports. Hanger support with anchor fasteners and clamps shall be supplied to fix the pipes on ceiling wall etc. including supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners) as per specification. Cutting of floors, walls etc and making it good after erection of pipes shall be of vendor's scope. Necessary painting with 2 coats of primer and 2 coats of synthetic enamel paints to be done and supply of paints shall be with vendor's scope. Size 50 NB | heavy grade pipe | size: 50 NB | grade: class-C, thickness: 5.4mm, standard: IS-1239 (indian standard 1239), fittings: tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer, structural steels for pipe supports, hanger support: anchor fasteners and clamps, installation: ceiling wall/floor/wall/ceiling with clamps, hangers (using anchor fastners), painting: 2 coats of primer and 2 coats of synthetic enamel paints, feature: supply of paints included |  | 56.0 | Mtr
['J ¦ WATER BASED PLANT', 'J3 ¦ WATER CURTAIN'] | Supply, erection and testing of heavy grade(class-C) pipes of thickness 5.4mm conforming to IS-1239 including all fittings viz. tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer and structural steels for pipe supports. Hanger support with anchor fasteners and clamps shall be supplied to fix the pipes on ceiling wall etc. including supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners) as per specification. Cutting of floors, walls etc and making it good after erection of pipes shall be of vendor's scope. Necessary painting with 2 coats of primer and 2 coats of synthetic enamel paints to be done and supply of paints shall be with vendor's scope. Size 65 NB | heavy grade pipe | size: 65 NB | grade: class-C, thickness: 5.4mm, standard: IS-1239 (indian standard 1239), fittings: tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer, structural steels for pipe supports, hanger support: anchor fasteners and clamps, installation: ceiling wall/floor/wall/ceiling with clamps, hangers (using anchor fastners), painting: 2 coats of primer and 2 coats of synthetic enamel paints, feature: supply of paints included |  | 52.0 | Mtr
['J ¦ WATER BASED PLANT', 'J3 ¦ WATER CURTAIN'] | Supply, erection and testing of heavy grade(class-C) pipes of thickness 5.4mm conforming to IS-1239 including all fittings viz. tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer and structural steels for pipe supports. Hanger support with anchor fasteners and clamps shall be supplied to fix the pipes on ceiling wall etc. including supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners) as per specification. Cutting of floors, walls etc and making it good after erection of pipes shall be of vendor's scope. Necessary painting with 2 coats of primer and 2 coats of synthetic enamel paints to be done and supply of paints shall be with vendor's scope. Size 80 NB | heavy grade pipe | size: 80 NB | grade: class-C, thickness: 5.4mm, standard: IS-1239 (indian standard 1239), fittings: tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer, structural steels for pipe supports, hanger support: anchor fasteners and clamps, installation: ceiling wall/floor/wall/ceiling with clamps, hangers (using anchor fastners), painting: 2 coats of primer and 2 coats of synthetic enamel paints, feature: supply of paints included |  | 66.0 | Mtr
['J ¦ WATER BASED PLANT', 'J3 ¦ WATER CURTAIN'] | Supply, erection and testing of heavy grade(class-C) pipes of thickness 5.4mm conforming to IS-1239 including all fittings viz. tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer and structural steels for pipe supports. Hanger support with anchor fasteners and clamps shall be supplied to fix the pipes on ceiling wall etc. including supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners) as per specification. Cutting of floors, walls etc and making it good after erection of pipes shall be of vendor's scope. Necessary painting with 2 coats of primer and 2 coats of synthetic enamel paints to be done and supply of paints shall be with vendor's scope. Size 100 NB | heavy grade pipe | size: 100 NB | grade: class-C, thickness: 5.4mm, standard: IS-1239 (indian standard 1239), fittings: tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer, structural steels for pipe supports, hanger support: anchor fasteners and clamps, installation: ceiling wall/floor/wall/ceiling with clamps, hangers (using anchor fastners), painting: 2 coats of primer and 2 coats of synthetic enamel paints, feature: supply of paints included |  | 36.0 | Mtr
['J ¦ WATER BASED PLANT', 'J3 ¦ WATER CURTAIN'] | Supply, erection , testing & commissioning of Deluge valve with wet pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 2 way Solenoid Valve, air filter regulator etc. & manual release unit. Size 80 NB | deluge valve | size: 80 NB | trim assembly: wet pilot, fitted with: strainer, drain valve, pressure gauge, pressure switch, solenoid valve: flame proof 2 way, air filter regulator: included, manual release unit: included |  | 1.0 | Nos
['J ¦ WATER BASED PLANT', 'J3 ¦ WATER CURTAIN'] | Supply, erection , testing & commissioning of Deluge valve with wet pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 2 way Solenoid Valve, air filter regulator etc. & manual release unit. Size 100 NB | deluge valve | size: 100 NB | trim assembly: wet pilot, fitted with: strainer, drain valve, pressure gauge, pressure switch, solenoid valve: flame proof 2 way, air filter regulator: included, manual release unit: included |  | 3.0 | Nos
['J ¦ WATER BASED PLANT', 'J3 ¦ WATER CURTAIN'] | Providing & fixing Cast Iron Y Strainer. Size 80 NB | y strainer | size: 80 NB | material: cast iron |  | 1.0 | Nos
['J ¦ WATER BASED PLANT', 'J3 ¦ WATER CURTAIN'] | Providing & fixing Cast Iron Y Strainer. Size 100 NB | y strainer | size: 100 NB | material: cast iron |  | 3.0 | Nos
['J ¦ WATER BASED PLANT', 'J3 ¦ WATER CURTAIN'] | Supply & fixing of SS Water Curtain Nozzle (K>=71)).UL/FM Approved. | water curtain nozzle |  | material: ss(stainless steel), k-factor: >=71, certification: UL(underwriters laboratories), certification: FM(factory mutual) |  | 67.0 | Nos
['J ¦ WATER BASED PLANT', 'J3 ¦ WATER CURTAIN'] | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. Size 80 NB | gate valve | size: 80 NB | material: cs(carbon steel), standard: API 600, class: 150, ends: flanged, feature: complete with nuts & bolts |  | 3.0 | Nos
['J ¦ WATER BASED PLANT', 'J3 ¦ WATER CURTAIN'] | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. Size 100 NB | gate valve | size: 100 NB | material: cs(carbon steel), standard: API 600, class: 150, ends: flanged, feature: complete with nuts & bolts |  | 9.0 | Nos
['J ¦ WATER BASED PLANT', 'J3 ¦ WATER CURTAIN'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. Size 150 mm NB | ms black steel pipe | size: 150 mm NB | material: ms(mild steel), finish: black, grade: heavy, thickness: 5.4mm, standard: IS 1239 Part-1 (indian standard 1239 part-1), fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved with groove coupling, civil work: all related civil work, supports included |  | 18.0 | Mtr
['J ¦ WATER BASED PLANT', 'J3 ¦ WATER CURTAIN'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. Size 100 mm NB | ms black steel pipe | size: 100 mm NB | material: ms(mild steel), finish: black, grade: heavy, thickness: 5.4mm, standard: IS 1239 Part-1 (indian standard 1239 part-1), fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved with groove coupling, civil work: all related civil work, supports included |  | 24.0 | Mtr
['J ¦ WATER BASED PLANT', 'J3 ¦ WATER CURTAIN'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. Size 80 mm NB | ms black steel pipe | size: 80 mm NB | material: ms(mild steel), finish: black, grade: heavy, thickness: 5.4mm, standard: IS 1239 Part-1 (indian standard 1239 part-1), fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved with groove coupling, civil work: all related civil work, supports included |  | 12.0 | Mtr
['J ¦ WATER BASED PLANT', 'J4 ¦ FDA SYSTEM'] | Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | multicriteria detector |  | type: analogue addressable |  | 15.0 | Nos
['J ¦ WATER BASED PLANT', 'J4 ¦ FDA SYSTEM'] | Supply, erection, testing & commissioning of analogue addressable Manual Call point | manual call point |  | type: analogue addressable |  | 12.0 | Nos
['J ¦ WATER BASED PLANT', 'J4 ¦ FDA SYSTEM'] | Supply, erection, testing & commissioning of Hooter cum strobe | hooter cum strobe |  |  |  | 12.0 | Nos
['J ¦ WATER BASED PLANT', 'J4 ¦ FDA SYSTEM'] | Supply, erection, testing & commissioning of Telephone jack. | telephone jack |  |  |  | 2.0 | Nos
['J ¦ WATER BASED PLANT', 'J4 ¦ FDA SYSTEM'] | Supply, erction, testing & commissioning of analogue addressable Control Module | control module |  | type: analogue addressable |  | 4.0 | Nos
['J ¦ WATER BASED PLANT', 'J4 ¦ FDA SYSTEM'] | Supply, erection, testing & commissioning of analogue addressable Isolator Module | isolator module |  | type: analogue addressable |  | 2.0 | Nos
['J ¦ WATER BASED PLANT', 'J4 ¦ FDA SYSTEM'] | Supply, erection, testing & commissioning of analogue addressable Monitor module | monitor module |  | type: analogue addressable |  | 2.0 | Nos
['J ¦ WATER BASED PLANT', 'J4 ¦ FDA SYSTEM'] | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. | armoured cabling |  | feature: complete with lugs, laying and termination of both ends
['J ¦ WATER BASED PLANT', 'J4 ¦ FDA SYSTEM'] | 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cable | size: 2C x 1.5 mm2 | type: loop cable |  | 572.0 | Mtr
['J ¦ WATER BASED PLANT', 'J4 ¦ FDA SYSTEM'] | Supply, installation, testing and commissioning of aspiration detector with CMOS imager combined with multiple photodiode for reliable very early warning in a wide range of environments with minimal nuisance alarms. The detector should have 4 pipe inlet and min 100m pipelength support per inlet.The detector should have Smart on-board filter retains dust count and remaining filter life for predictable maintenance& coverage area of min 5000 Sq. | aspiration detector | pipe inlet: 4, pipelength support per inlet: min 100m, coverage area: min 5000 Sq. | imager: CMOS(complementary metal oxide semiconductor), sensor: multiple photodiode, feature: reliable very early warning, feature: minimal nuisance alarms, feature: smart on-board filter retains dust count and remaining filter life for predictable maintenance |  | 7.0 | Nos
['J ¦ WATER BASED PLANT', 'J4 ¦ FDA SYSTEM'] | Supply,Installation,Testing & Commissioning of UL/VDS listed CPVC Pipe 25 mm Dia & Pipe Accessories for the Aspiration detection. | cpvc pipe | diameter: 25 mm | certification: UL(underwriters laboratories), certification: VDS, feature: listed, accessories: pipe accessories for the aspiration detection |  | 980.0 | Mtr
['J ¦ WATER BASED PLANT', 'J4 ¦ FDA SYSTEM'] | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. | armoured cabling |  | feature: complete with lugs, laying and termination of both ends
['J ¦ WATER BASED PLANT', 'J4 ¦ FDA SYSTEM'] | 2C x 1.5 mm2 Armoured ( Power cable) | armoured cable | size: 2C x 1.5 mm2 | type: power cable |  | 706.0 | Mtr
['J ¦ WATER BASED PLANT', 'J4 ¦ FDA SYSTEM'] | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable trays |  | feature: for laying all type of cables as indicated above, feature: including all necessary structural supports |  | 1158.0 | Mtr
['J ¦ WATER BASED PLANT', 'J5 ¦ PA SYSTEM'] | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | ip based networkable touch screen paging station |  | feature: selection of zones, feature: supervision of system status, feature: setting of scheduled broadcasts, feature: central exchange with stand by CPU, feature: built-in monitoring loudspeaker, feature: goose-neck microphone, feature: LCD touchscreen display, feature: audio input |  | 1.0 | Nos
['J ¦ WATER BASED PLANT', 'J5 ¦ PA SYSTEM'] | 9 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | horn type speaker | power: 9 W | feature: high efficiency, feature: weather protection IP 65, feature: weatherproof type, feature: suitable for outdoor area |  | 5.0 | Nos
['J ¦ WATER BASED PLANT', 'J5 ¦ PA SYSTEM'] | 30 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | horn type speaker | power: 30 W | feature: high efficiency, feature: weather protection IP 65, feature: weatherproof type, feature: suitable for outdoor area |  | 4.0 | Nos
['J ¦ WATER BASED PLANT', 'J5 ¦ PA SYSTEM'] | Rack Mounted 200 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | power amplifier | power: 200 watt | mounting: rack mounted, feature: battery back up, feature: wattage shall be as per requirement |  | 1.0 | Nos
['J ¦ WATER BASED PLANT', 'J5 ¦ PA SYSTEM'] | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | armoured xlpe cu cable | size: 2C x 1.5 mm2 | feature: multi stranded, feature: shielded, feature: armoured, material: XLPE, material: copper, application: power & signal |  | 350.0 | Mtr
['J ¦ WATER BASED PLANT', 'J5 ¦ PA SYSTEM'] | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | dvd player |  | feature: hook up to amplifiers of PA system for music in the common areas |  | 1.0 | Nos
['J ¦ WATER BASED PLANT', 'J5 ¦ PA SYSTEM'] | Paging Loudspeaker | paging loudspeaker |  |  |  | 1.0 | Nos