## Sheet1
section_context_for_this_product_block | full_product_description | core_product_name | acronymed_core_product_name | size | feature_or_specifications | quantity | unit
['A ¦ UPS'] | 1 ¦ 5kVA Stand-Alone UPS with SCVS Bypass, battery bank (1X 100%) having 1hr backup along with it's mounting Stainless Steel rack, Battery isolation box & Intercell connectors suitable for batteries and along with required cable & cablibg accessories for UPS, battery bank, UPS ACDB. (For Raw Water reservoir Control room) 5 KVA UPS DB shall have below feeders Incoming : 63 A DP MCCB : 2 nos Outgoing : 16A DP MCB (12 Nos) : 32A DP MCB (4 Nos) : 6A DP MCB (4 Nos) | uninterruptible power supply | ups (uninterruptible power supply) | capacity: 5 kVA, backup: 1 hr | bypass: scvs (static continuous voltage stabilizer), battery bank: 1x100%, mounting: stainless steel rack, accessories: battery isolation box, intercell connectors, required cable & cabling accessories for ups, battery bank, ups acdb, location: raw water reservoir control room, db feeders: incoming 63 a dp mccb 2 nos, outgoing 16a dp mcb 12 nos, 32a dp mcb 4 nos, 6a dp mcb 4 nos | 1.0 | Set
['B ¦ DC System 220 Volt (Battery Charger & Battery Bank)'] | 1 ¦ 50AH, 220V DC Battery (1x100%) & 25A Battery Charger (Dual Float cum boost battery charger) complete with Rack, accessories etc. & 220V DC distribution board. Intercoinnecting DC cable between battery, battery cherger, Battery isolation box and 220V DC distribuion board. 220V DCDB Incoming : 63 A DP MCCB : 1 nos Outgoing : 16A DP MCB (6 Nos) : 32A DP MCB (6 Nos) | dc system | dc system | battery capacity: 50AH, battery voltage: 220V, charger current: 25A | battery bank: 1x100%, charger type: dual float cum boost battery charger, includes: rack, accessories, 220v dc distribution board, interconnecting dc cable between battery, battery charger, battery isolation box and 220v dc distribution board, dcdb feeders: incoming 63 a dp mccb 1 nos, outgoing 16a dp mcb 6 nos, 32a dp mcb 6 nos | 1.0 | Set
['C ¦ 11 KV (UE) & 6.6 KV (UE) HT Cable Jointing & End Termination'] | 1 ¦ 11 KV (UE) Heat Shrinkable Indoor End Termination With Double Compression Gland ¦ 1C x 400 sqmm AL | heat shrinkable indoor end termination |  | cable size: 1C x 400 sqmm | voltage: 11 kv (ue), gland type: double compression, conductor material: aluminium | 270.0 | No's
['C ¦ 11 KV (UE) & 6.6 KV (UE) HT Cable Jointing & End Termination'] | 2 ¦ nan ¦ 1C x 300 sqmm AL | heat shrinkable indoor end termination |  | cable size: 1C x 300 sqmm | voltage: 11 kv (ue), gland type: double compression, conductor material: aluminium | 40.0 | No's
['C ¦ 11 KV (UE) & 6.6 KV (UE) HT Cable Jointing & End Termination'] | 3 ¦ nan ¦ 3C x 240 sqmm AL | heat shrinkable indoor end termination |  | cable size: 3C x 240 sqmm | voltage: 11 kv (ue), gland type: double compression, conductor material: aluminium | 150.0 | No's
['C ¦ 11 KV (UE) & 6.6 KV (UE) HT Cable Jointing & End Termination'] | 4 ¦ nan ¦ 3C x 300 sqmm AL | heat shrinkable indoor end termination |  | cable size: 3C x 300 sqmm | voltage: 11 kv (ue), gland type: double compression, conductor material: aluminium | 10.0 | No's
['C ¦ 11 KV (UE) & 6.6 KV (UE) HT Cable Jointing & End Termination'] | 5 ¦ 11 KV (UE) Heat Shrinkable Outdoor Straight Through Termination ¦ 1C x 400 sqmm AL | heat shrinkable outdoor straight through termination |  | cable size: 1C x 400 sqmm | voltage: 11 kv (ue), conductor material: aluminium | 160.0 | No's
['C ¦ 11 KV (UE) & 6.6 KV (UE) HT Cable Jointing & End Termination'] | 6 ¦ nan ¦ 1C x 300 sqmm AL | heat shrinkable outdoor straight through termination |  | cable size: 1C x 300 sqmm | voltage: 11 kv (ue), conductor material: aluminium | 30.0 | No's
['C ¦ 11 KV (UE) & 6.6 KV (UE) HT Cable Jointing & End Termination'] | 7 ¦ nan ¦ 3C x 240 sqmm AL | heat shrinkable outdoor straight through termination |  | cable size: 3C x 240 sqmm | voltage: 11 kv (ue), conductor material: aluminium | 90.0 | No's
['C ¦ 11 KV (UE) & 6.6 KV (UE) HT Cable Jointing & End Termination'] | 8 ¦ nan ¦ 3C x 300 sqmm AL | heat shrinkable outdoor straight through termination |  | cable size: 3C x 300 sqmm | voltage: 11 kv (ue), conductor material: aluminium | 6.0 | No's
['C ¦ 11 KV (UE) & 6.6 KV (UE) HT Cable Jointing & End Termination'] | 9 ¦ 6.6 KV (UE) Heat Shrinkable Indoor End Termination With Double Compression Gland ¦ 1C x 185 sqmm AL | heat shrinkable indoor end termination |  | cable size: 1C x 185 sqmm | voltage: 6.6 kv (ue), gland type: double compression, conductor material: aluminium | 24.0 | No's
['C ¦ 11 KV (UE) & 6.6 KV (UE) HT Cable Jointing & End Termination'] | 10 ¦ nan ¦ 3C x 185 sqmm AL | heat shrinkable indoor end termination |  | cable size: 3C x 185 sqmm | voltage: 6.6 kv (ue), gland type: double compression, conductor material: aluminium | 100.0 | No's
['C ¦ 11 KV (UE) & 6.6 KV (UE) HT Cable Jointing & End Termination'] | 11 ¦ nan ¦ 3C x 300 sqmm AL | heat shrinkable indoor end termination |  | cable size: 3C x 300 sqmm | voltage: 6.6 kv (ue), gland type: double compression, conductor material: aluminium | 20.0 | No's
['C ¦ 11 KV (UE) & 6.6 KV (UE) HT Cable Jointing & End Termination'] | 12 ¦ 6.6 KV (UE) Heat Shrinkable Outdoor Straight Through Termination ¦ 1C x 185 sqmm AL | heat shrinkable outdoor straight through termination |  | cable size: 1C x 185 sqmm | voltage: 6.6 kv (ue), conductor material: aluminium | 2.0 | No's
['C ¦ 11 KV (UE) & 6.6 KV (UE) HT Cable Jointing & End Termination'] | 13 ¦ nan ¦ 3C x 185 sqmm AL | heat shrinkable outdoor straight through termination |  | cable size: 3C x 185 sqmm | voltage: 6.6 kv (ue), conductor material: aluminium | 76.0 | No's
['C ¦ 11 KV (UE) & 6.6 KV (UE) HT Cable Jointing & End Termination'] | 14 ¦ nan ¦ 3C x 300 sqmm AL | heat shrinkable outdoor straight through termination |  | cable size: 3C x 300 sqmm | voltage: 6.6 kv (ue), conductor material: aluminium | 2.0 | No's
['C ¦ 11 KV (UE) & 6.6 KV (UE) HT Cable Jointing & End Termination'] | 15 ¦ 11 KV (UE) Heat Shrinkable Outdoor End Termination Kit for NGR ¦ 1C x 300 sqmm AL | heat shrinkable outdoor end termination kit |  | cable size: 1C x 300 sqmm | voltage: 11 kv (ue), application: ngr (neutral grounding resistor), conductor material: aluminium | 16.0 | No's
['C ¦ 11 KV (UE) & 6.6 KV (UE) HT Cable Jointing & End Termination'] | 16 ¦ 6.6 KV (UE) Heat Shrinkable Outdoor End Termination Kit for NGR ¦ 1C x 185 sqmm AL | heat shrinkable outdoor end termination kit |  | cable size: 1C x 185 sqmm | voltage: 6.6 kv (ue), application: ngr (neutral grounding resistor), conductor material: aluminium | 24.0 | No's
['C ¦ 11 KV (UE) & 6.6 KV (UE) HT Cable Jointing & End Termination'] | 17 ¦ 19/33 KV (E)Heat Shrinkable Indoor End Termination With Double Compression Gland ¦ 1C x 400 sqmm AL | heat shrinkable indoor end termination |  | cable size: 1C x 400 sqmm | voltage: 19/33 kv (e), gland type: double compression, conductor material: aluminium | 6.0 | No's
['D ¦ Trefoil Cable Clamps (Material PVC)'] | 1 ¦ 11 KV (UE) grade, Aluminium conductor, XLPE insulated, FRLS PVC ¦ 1Cx400 mm2 (Dia - 55mm) | trefoil cable clamp |  | cable size: 1Cx400 mm2, diameter: 55mm | voltage: 11 kv (ue), conductor material: aluminium, insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke) pvc (polyvinyl chloride), clamp material: pvc (polyvinyl chloride) | 12000.0 | Nos.
['D ¦ Trefoil Cable Clamps (Material PVC)'] | nan ¦ sheathed armoured cables ¦ 1Cx300 mm2 (Dia - 45mm) | trefoil cable clamp |  | cable size: 1Cx300 mm2, diameter: 45mm | sheath: armoured, clamp material: pvc (polyvinyl chloride) | 2000.0 | Nos.
['D ¦ Trefoil Cable Clamps (Material PVC)'] | 2 ¦ 6.6 KV (UE) grade, Aluminium conductor, XLPE insulated, FRLS PVC sheathed armoured cables ¦ 1Cx185 mm2 (Dia - 40mm) | trefoil cable clamp |  | cable size: 1Cx185 mm2, diameter: 40mm | voltage: 6.6 kv (ue), conductor material: aluminium, insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke) pvc (polyvinyl chloride), armoured, clamp material: pvc (polyvinyl chloride) | 20.0 | Nos.
['D ¦ Trefoil Cable Clamps (Material PVC)'] | 3 ¦ 1,1 KV (UE) grade, Aluminium conductor, XLPE insulated, FRLS PVC sheathed armoured cables ¦ 1Cx630 mm2 (Dia - 45mm) | trefoil cable clamp |  | cable size: 1Cx630 mm2, diameter: 45mm | voltage: 1.1 kv (ue), conductor material: aluminium, insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke) pvc (polyvinyl chloride), armoured, clamp material: pvc (polyvinyl chloride) | 5000.0 | Nos.
['D ¦ Trefoil Cable Clamps (Material PVC)'] | 4 ¦ 1,1 KV (UE) grade, Aluminium conductor, XLPE insulated, FRLS PVC sheathed armoured cables ¦ 1Cx400 mm2 (Dia - 65mm) | trefoil cable clamp |  | cable size: 1Cx400 mm2, diameter: 65mm | voltage: 1.1 kv (ue), conductor material: aluminium, insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke) pvc (polyvinyl chloride), armoured, clamp material: pvc (polyvinyl chloride) | 4000.0 | Nos.
['E ¦ POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule'] | 1 ¦ 1.1kV, 90 Deg.C rating, heavy duty power cables with stranded Copper conductor, extruded XLPE insulation, extruded PVC, FRLS inner sheath (Type-ST2), aluminium round wire armour for single core cables and galvanized steel strip /wire armour for Multi core cables, and extruded PVC, FR-LSH (Type-ST2) overall sheath. ¦ 2Cx2.5 sqmm Cu | power and control cable termination |  | cable size: 2Cx2.5 sqmm | voltage: 1.1kv, temperature rating: 90 deg.c, cable type: heavy duty, conductor material: copper, insulation: xlpe (cross-linked polyethylene), inner sheath: frls (flame retardant low smoke) pvc (polyvinyl chloride) type-st2, armour: aluminium round wire (single core), galvanized steel strip/wire (multi core), overall sheath: fr-lsh (flame retardant low smoke halogen) pvc (polyvinyl chloride) type-st2 | 500.0 | Set
['E ¦ POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule'] | 2 ¦ 3Cx2.5 sqmm Cu ¦ Termination Kit | power and control cable termination |  | cable size: 3Cx2.5 sqmm | conductor material: copper, kit type: termination kit | 3500.0 | Set
['E ¦ POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule'] | 3 ¦ 4Cx2.5 sqmm Cu ¦ Termination Kit | power and control cable termination |  | cable size: 4Cx2.5 sqmm | conductor material: copper, kit type: termination kit | 20.0 | Set
['E ¦ POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule'] | 4 ¦ 2Cx4 sqmm Cu ¦ Termination Kit | power and control cable termination |  | cable size: 2Cx4 sqmm | conductor material: copper, kit type: termination kit | 120.0 | Set
['E ¦ POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule'] | 5 ¦ 3Cx4 sqmm Cu ¦ Termination Kit | power and control cable termination |  | cable size: 3Cx4 sqmm | conductor material: copper, kit type: termination kit | 100.0 | Set
['E ¦ POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule'] | 6 ¦ 4Cx4 sqmm Cu ¦ Termination Kit | power and control cable termination |  | cable size: 4Cx4 sqmm | conductor material: copper, kit type: termination kit | 100.0 | Set
['E ¦ POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule'] | 7 ¦ 1.1kV, 90 Deg.C rating, heavy duty power cables with stranded Aluminium conductor, extruded XLPE insulation, extruded PVC, FRLS inner sheath (Type-ST2), aluminium round wire armour for single core cables and galvanized steel strip /wire armour for Multi core cables, and extruded PVC, FR-LSH (Type-ST2) overall sheath. ¦ 1Cx630 sqmm Al ¦ Termination Kit | power and control cable termination |  | cable size: 1Cx630 sqmm | voltage: 1.1kv, temperature rating: 90 deg.c, cable type: heavy duty, conductor material: aluminium, insulation: xlpe (cross-linked polyethylene), inner sheath: frls (flame retardant low smoke) pvc (polyvinyl chloride) type-st2, armour: aluminium round wire (single core), galvanized steel strip/wire (multi core), overall sheath: fr-lsh (flame retardant low smoke halogen) pvc (polyvinyl chloride) type-st2, kit type: termination kit | 1100.0 | Set
['E ¦ POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule'] | 8 ¦ 2CX120 sqmm Al ¦ Termination Kit | power and control cable termination |  | cable size: 2CX120 sqmm | conductor material: aluminium, kit type: termination kit | 950.0 | Set
['E ¦ POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule'] | 9 ¦ 2CX16 sqmm Al ¦ Termination Kit | power and control cable termination |  | cable size: 2CX16 sqmm | conductor material: aluminium, kit type: termination kit | 250.0 | Set
['E ¦ POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule'] | 10 ¦ 2CX185 sqmm Al ¦ Termination Kit | power and control cable termination |  | cable size: 2CX185 sqmm | conductor material: aluminium, kit type: termination kit | 100.0 | Set
['E ¦ POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule'] | 11 ¦ 2CX35 sqmm Al ¦ Termination Kit | power and control cable termination |  | cable size: 2CX35 sqmm | conductor material: aluminium, kit type: termination kit | 80.0 | Set
['E ¦ POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule'] | 12 ¦ 2CX50 sqmm Al ¦ Termination Kit | power and control cable termination |  | cable size: 2CX50 sqmm | conductor material: aluminium, kit type: termination kit | 80.0 | Set
['E ¦ POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule'] | 13 ¦ 3.5CX50 sqmm Al ¦ Termination Kit | power and control cable termination |  | cable size: 3.5CX50 sqmm | conductor material: aluminium, kit type: termination kit | 50.0 | Set
['E ¦ POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule'] | 14 ¦ 3.5CX70 sqmm Al ¦ Termination Kit | power and control cable termination |  | cable size: 3.5CX70 sqmm | conductor material: aluminium, kit type: termination kit | 280.0 | Set
['E ¦ POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule'] | 15 ¦ 3.5CX95 sqmm Al ¦ Termination Kit | power and control cable termination |  | cable size: 3.5CX95 sqmm | conductor material: aluminium, kit type: termination kit | 400.0 | Set
['E ¦ POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule'] | 16 ¦ 3.5CX150 sqmm Al ¦ Termination Kit | power and control cable termination |  | cable size: 3.5CX150 sqmm | conductor material: aluminium, kit type: termination kit | 40.0 | Set
['E ¦ POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule'] | 17 ¦ 3.5CX185 sqmm Al ¦ Termination Kit | power and control cable termination |  | cable size: 3.5CX185 sqmm | conductor material: aluminium, kit type: termination kit | 80.0 | Set
['E ¦ POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule'] | 18 ¦ 3.5CX240 sqmm Al ¦ Termination Kit | power and control cable termination |  | cable size: 3.5CX240 sqmm | conductor material: aluminium, kit type: termination kit | 40.0 | Set
['E ¦ POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule'] | 19 ¦ 3.5CX300 sqmm Al ¦ Termination Kit | power and control cable termination |  | cable size: 3.5CX300 sqmm | conductor material: aluminium, kit type: termination kit | 160.0 | Set
['E ¦ POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule'] | 20 ¦ 3CX16 sqmm Al ¦ Termination Kit | power and control cable termination |  | cable size: 3CX16 sqmm | conductor material: aluminium, kit type: termination kit | 600.0 | Set
['E ¦ POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule'] | 21 ¦ 3CX35 sqmm Al ¦ Termination Kit | power and control cable termination |  | cable size: 3CX35 sqmm | conductor material: aluminium, kit type: termination kit | 1100.0 | Set
['E ¦ POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule'] | 22 ¦ 3CX50 sqmm Al ¦ Termination Kit | power and control cable termination |  | cable size: 3CX50 sqmm | conductor material: aluminium, kit type: termination kit | 40.0 | Set
['E ¦ POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule'] | 23 ¦ 3CX70 sqmm Al ¦ Termination Kit | power and control cable termination |  | cable size: 3CX70 sqmm | conductor material: aluminium, kit type: termination kit | 100.0 | Set
['E ¦ POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule'] | 24 ¦ 3CX95 sqmm Al ¦ Termination Kit | power and control cable termination |  | cable size: 3CX95 sqmm | conductor material: aluminium, kit type: termination kit | 150.0 | Set
['E ¦ POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule'] | 25 ¦ 3CX150 sqmm Al ¦ Termination Kit | power and control cable termination |  | cable size: 3CX150 sqmm | conductor material: aluminium, kit type: termination kit | 30.0 | Set
['E ¦ POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule'] | 26 ¦ 3CX185 sqmm Al ¦ Termination Kit | power and control cable termination |  | cable size: 3CX185 sqmm | conductor material: aluminium, kit type: termination kit | 50.0 | Set
['E ¦ POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule'] | 27 ¦ 3CX240 sqmm Al ¦ Termination Kit | power and control cable termination |  | cable size: 3CX240 sqmm | conductor material: aluminium, kit type: termination kit | 200.0 | Set
['E ¦ POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule'] | 28 ¦ 4CX16 sqmm Al ¦ Termination Kit | power and control cable termination |  | cable size: 4CX16 sqmm | conductor material: aluminium, kit type: termination kit | 200.0 | Set
['E ¦ POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule'] | 29 ¦ 4CX35 sqmm Al ¦ Termination Kit | power and control cable termination |  | cable size: 4CX35 sqmm | conductor material: aluminium, kit type: termination kit | 600.0 | Set
['E ¦ POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule'] | 30 ¦ 4Cx6 sqmm Al ¦ Termination Kit | power and control cable termination |  | cable size: 4Cx6 sqmm | conductor material: aluminium, kit type: termination kit | 40.0 | Set
['E ¦ POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule'] | 31 ¦ 1.1kV grade, 85 deg C rating, control cables with stranded copper conductors, PVC Insulation, extruded PVC, FRLS Inner sheath (Type- ST2), round wire/strip armour as specified elsewhere in the specification and extruded PVC, FRLSH overall sheath (Type-ST2). ¦ 3Cx2.5 sqmm Cu ¦ Termination Kit | control cable termination |  | cable size: 3Cx2.5 sqmm | voltage: 1.1kv, temperature rating: 85 deg c, conductor material: copper, insulation: pvc (polyvinyl chloride), inner sheath: frls (flame retardant low smoke) pvc (polyvinyl chloride) type-st2, armour: round wire/strip, overall sheath: frlsh (flame retardant low smoke halogen) pvc (polyvinyl chloride) type-st2, kit type: termination kit | 100.0 | Set
['E ¦ POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule'] | 32 ¦ 5Cx2.5 sqmm Cu ¦ Termination Kit | control cable termination |  | cable size: 5Cx2.5 sqmm | conductor material: copper, kit type: termination kit | 3000.0 | Set
['E ¦ POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule'] | 33 ¦ 7Cx2.5 sqmm Cu ¦ Termination Kit | control cable termination |  | cable size: 7Cx2.5 sqmm | conductor material: copper, kit type: termination kit | 200.0 | Set
['E ¦ POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule'] | 34 ¦ 12Cx2.5 sqmm Cu ¦ Termination Kit | control cable termination |  | cable size: 12Cx2.5 sqmm | conductor material: copper, kit type: termination kit | 200.0 | Set
['E ¦ POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule'] | 35 ¦ 9Cx2.5 sqmm Cu ¦ Termination Kit | control cable termination |  | cable size: 9Cx2.5 sqmm | conductor material: copper, kit type: termination kit | 500.0 | Set
['E ¦ POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule'] | 36 ¦ 20Cx2.5 sqmm Cu ¦ Termination Kit | control cable termination |  | cable size: 20Cx2.5 sqmm | conductor material: copper, kit type: termination kit | 80.0 | Set
['E ¦ POWER & Control CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as Cable Schedule'] | 37 ¦ 4Cx1.5 sqmm Cu ¦ Termination Kit | control cable termination |  | cable size: 4Cx1.5 sqmm | conductor material: copper, kit type: termination kit | 100.0 | Set
['F ¦ OFC, Cat-6 Cable & Conduit Laying with Accessories (RJ245 termintion, Splicing etc)'] | 1 ¦ 50 MM PVC Conduit Laying | pvc conduit laying |  | conduit size: 50 mm | material: pvc (polyvinyl chloride) | 5000.0 | Meters
['F ¦ OFC, Cat-6 Cable & Conduit Laying with Accessories (RJ245 termintion, Splicing etc)'] | 3 ¦ Splicing/termination with Accessories | splicing or termination |  |  |  | 24.0 | No's
["G ¦ Base Frame & Cable Tray Supports System with Accessories as per attched General notes and details of GA & Tray Layout Drg's."] | 1 ¦ MS Steel Support Structure of Sizes (ISA 50x50x6/65x65x6, ISMC-75/100/125/150/200 and Insert plates Etc .) Structures should be Red Oxide & GI Painted: | ms steel support structure |  | isa size: 50x50x6 or 65x65x6, ismc size: 75 or 100 or 125 or 150 or 200 | material: ms (mild steel), finish: red oxide & gi (galvanized iron) painted | 600.0 | MT
["G ¦ Base Frame & Cable Tray Supports System with Accessories as per attched General notes and details of GA & Tray Layout Drg's."] | 2 ¦ Supply, Fabrication, Installation of 6mm checkered plate | checkered plate supply fabrication installation |  | plate thickness: 6 mm |  | 30.0 | MT
['H ¦ Lightning Protection System'] | 1 ¦ 25x6mm GS Flat | gs flat |  | flat size: 25x6 mm | material: gs (galvanized steel) | 4000.0 | Meters
['H ¦ Lightning Protection System'] | 2 ¦ 1.5 Mtr long AL Air Terminal on RCC Roof | al air terminal |  | length: 1.5 mtr | material: al (aluminium), installation: on rcc (reinforced cement concrete) roof | 60.0 | No's
['H ¦ Lightning Protection System'] | 3 ¦ VERTICAL AIR TERMINATION RODS 20 mm DIA, 1000 MM LONG GS | vertical air termination rod |  | diameter: 20 mm, length: 1000 mm | material: gs (galvanized steel) | 20.0 | No's