## Sheet1
0 | 1 | 2 | 3 | 4
2 | Luminaire Type FC26 (LED) | Panel (approx. 1200mm x300mm) decorative LED fixture suitable for recess mounting in false ceiling with integral driver aesthetically designed for Control Room/ Office. | Nos. | 300
3 | Luminaire Type FC30 (LED) | Panel 600mm x600mm decorative LED fixture suitable for recess mounting in false ceiling with integral driver aesthetically designed for Control Room/ Office. | Nos. | 550
4 | Luminaire Type FC32 (LED) | Decorative, surface mounted LED fixture having integral driver | Nos. | 80
5 | Luminaire Type FC81 (LED) | Corrosion proof, totally enclosed type LED fixture with integral driver. | Nos. | 360
6 | Luminaire Type SF63 (LED) | Flood light, Heavy duty type LED fixture with integral driver. | Nos. | 120
7 | Luminaire Type SF64 (LED) | Flood light, Heavy duty type LED fixture with integral driver. | Nos. | 140
8 | Luminaire Type SF66 (LED) | Flood light, Heavy duty type LED fixture with integral driver. | Nos. | 80
9 | Luminaire Type SB11 (LED) | Medium Bay, Industrial type LED fixture with integral driver. | Nos. | 200
10 | Luminaire Type SB02 (LED) | High Bay, Industrial type LED fixture with integral driver. | Nos. | 650
11 | Luminaire Type SB03 (LED) | High Bay, Industrial type LED fixture with integral driver suitable for mounting height> 1Om. | Nos. | 210
12 | Luminaire Type SS61 (LED) | Street light, LED fixture with integral driver. | Nos. | 40
13 | Luminaire Type SS62 (LED) | Street light, LED fixture with integral driver. | Nos. | 600
14 | Luminaire Type SS63 (LED) | Street light, LED fixture with integral driver. | Nos. | 720
15 | Luminaire Type SW41 (LED) | Well glass type, vapour proof LED fixture suitable for Boiler/ ESP platforms | Nos. | 8200
16 | Luminaire Type SW42 (LED) | Well glass type, vapour proof LED fixture suitable for Boiler/ ESP platforms | Nos. | 2500
17 | Luminaire Type MW96 | 1x125 W Mercury, well glass, flame proof increased safety luminaire with vitreous enamelled reflector and cast aluminium alloy LM6 housing for Div. 2 areas along with suitable HPMV lamp. | Nos. | 400
18 | Luminaire Type FC07 | 1x18 W Fluorescent, industrial box type base and vitreous enamelled side reflectors operating on 220V DC input supply along with suitable CFL lamp. | Nos. | 600
19 | Luminaire Type FC33 | 1x18 W Fluorescent, decorative, recessed type with mirror optic reflector operating on 220V DC input supply along with suitable CFL lamp. | Nos. | 160
20 | Luminaire Type FC34 | 1x18 W Fluorescent, dust proof, totally enclosed type with sheet steel housing operating on 220V DC input supply along with suitable CFL lamp. | Nos. | 500
21 | LUMINAIRES TYPE DOWNLIGHTER 18W(LED) | Recessed Mounted Downlighter with Integral driver aesthetically designed for Control Room/ Office * For Downlighter* (LED), nomenclature FC35 (LED) to be used in drawing. | Nos. | 100
22 | COVE LIGHT (LED) - 5 MTR STRIP | COVE LIGHT(LED)# shall be 5 MTR strip per piece. Cove lighting, if required shall be provided for better aesthetics in false ceiling of common control room(CCR) and ESP Control room. # For COVE LIGHT (LED), nomenclature FC36 (LED) to be used in drawing. | Nos. | 200
23 | Emergency Exit lights with LED fittings with sealed maintenance free battery sized to provide 2 hours backup complete with charger, plug, extension card etc housed in enclosure suitable for operation on 240V AC supply. |  | Nos. | 100
24 | Portable emergency lantern with 2x10 W LED lamp with sealed maintenance free Ni-Cd battery sized to provide 4 hours backup complete with charger, plug, extension card etc housed in enclosure suitable for operation on 240V AC supply. |  | Nos. | 25
25 | Wall/ parapet mounted , LED flood light Luminaire having system power consumption not more than 150W , cool white light output 5700-6500K colour temperature, Built in constant current electronic driver, IP-66 Powder coated high pressure die cast aluminium housing with separate driver compartment ,heat sink designed in aluminium extrusion & glare free light output. |  | Nos. | 320
26 | Explosion proof 2x36W LED Tube Light Fixture |  | Nos. | 90
27 | Recessed mounted 2'X2' LED Luminaire having system power consumption not more than 36W , neutral white light output 5500-6500K colour temperature, Built in constant current electronic driver, Powder coated CRCA sheet steel housing, with high efficiency acrylic diffuser for uniform & glare free light output. |  | Nos. | 60
28 | Surface/Suspended Mounted LED light fixture having system power consumption not more than 40W Batten, cool white light output 5500-6500K colour temperature , Built in constant current electronic driver , made of CRCA with high efficiency opel diffuser for uniform & glare free light output. |  | Nos. | 100
29 | Supply of Recessed mounted , Circular LED Luminaire having system power consumption not more than 13W , cool white light output 4000K colour temperature, Built in constant current electronic driver, Powder coated CRCA/AL sheet steel housing with high efficiency acrylic diffuser for uniform & glare free light output. |  | Nos | 50
30 | Wall mounted mirror 10W LED light with 4000K |  | Nos | 50
31 | Emergency lighting Units - With Ni-Cd battery and 2 X 6 W LED lamp |  | Nos | 16
B | Switch boxes for individual control of circuits (Switchboards consisting of switch boxes, switches, switch plates and fixing accessories.)
1 | Type SWB1 |  | Nos. | 160
2 | Type SWB2 |  | Nos. | 60
3 | Type SWB3 |  | Nos. | 20
4 | One no 6A 5 pin power socket with one no 6A Switch having indication including back box, cover plate etc. |  | Nos | 80
5 | One no 6/16A 5 pin power socket with one no 16A Switch having indication including back box, cover plate etc. |  | Nos | 100
6 | Three no 6A 5 pin power socket with one 16A Switch having indication including back box, cover plate etc. |  | Nos | 120
7 | Switch Box Enclosure 2 M with plate |  | Nos | 16
8 | Switch Box Enclosure 4 M with plate |  | Nos | 16
9 | Switch Box Enclosure 6 M with plate |  | Nos | 16
10 | Switch Box Enclosure 8 M with plate |  | Nos | 16
11 | Switch Box Enclosure 10 M with plate |  | Nos | 16
C | Junction boxes
1 | Type JB-F | Provided with four (4) way stud type terminals for terminating upto 2 nos. 10 mm2 stranded aluminium conductors on each terminal, suitable for outdoor installations. | Nos. | 16800
2 | Type JB-FE | Same as above JB-F but with an additional epoxy coating of 50 micron thickness. | Nos. | 360
3 | Type JB-S | Provided with four (4) way stud type terminals, each terminal suitable for terminating upto two nos. of 3.5Cx50 mm2 stranded aluminium conductors & with one no.6A HRC fuse and link. | Nos. | 320
4 | Type A - GI junction boxes | Size of junction box shall be 125mm x 125mm. Terminals of the JB shall be suitable for 4 sqmm cable. | NOS. | 200
5 | Type B - GI junction boxes | Size of junction box shall be 125mm x 125mm. Terminals of the JB shall be suitable for 4 sqmm cable. | NOS. | 300
6 | Type C (GI Type for Street Lighting Poles) junction boxes | Size of junction box shall be 250x250mm. Terminals of the JB shall be suitable for 16 sqmm cable. | NOS. | 360
D | Receptacles
1 | Type RA |  | Nos. | 1000
2 | Type RA (Flame proof) |  | Nos. | 20
3 | Type RB |  | Nos. | 232
4 | Type RC |  | Nos. | 216
5 | Type RC (Flame proof) |  | Nos. | 6
6 | 32 A, 240V, 5 pin, surface/recess mounting industrial type receptacle with a safety cover and a switch/MCB in FRP/Sheet steel enclosure having degree of protection of IP 55. |  | Nos. | 100
7 | 63 A, 415V, 4P with earth, surface/recess mounting 5 pin, industrial type receptacle with spring operated cover, interlocks, ELCB (100mA) switch, fuse units with plug in FRP / Sheet steel enclosure having degree of protection of IP 55. |  | Nos. | 40
E | Ceiling fans with electronic regulators & down rod etc.
1 | 1200 mm sweep |  | Nos. | 8
2 | 1400 mm sweep |  | Nos. | 16
3 | Pedestal Fan | Pedestal Fan will have 400mm Sweep (50-65 Wattage). | Nos. | 8
F | 24V supply module & lamps unit complete with all accessories Each 24V A.C. supply module shall have one (1) no dry type two winding transformer and necessary terminals for incoming and outgoing connections. The 240V terminals of 24V AC supply module shall be fed from AC emergency lighting panels (ACELP). Details of 24V A.C. supply modules shall be as given below: Module type: Portable type/ Fixed type with receptacle distribution panel Transformer rating: 500 VA, Transformer voltage ratio: 240/26.5 Volt Primary side isolation: DP MCB with HRC fuse, Isolation rating: 16A, HRC fuse rating: 6A Secondary side isolation: SPN MCB with HRC fuse, Isolation rating: 6A, HRC fuse rating: 16A
1 | Fixed type 24V supply modules |  | Nos. | 60
2 | Portable type 24V supply modules |  | Nos. | 20
3 | Portable halogen lamp unit | 24V portable halogen lamp unit along with flexible copper cable shall be supplied as per details below: Lamp wattage: 40 W Cable size: 2.5 sq. mm Stranded copper Cable length: 20 meter | Nos. | 20
4 | 5A, 24V industrial type sockets |  | Nos. | 240
G | Wires
1 | 1.5 sq.mm (Cu) 1.1kV grade,XLPE insulated stranded copper wires |  | Mtrs | 3000
2 | 2.5 sq.mm (Cu) 1.1kV grade,XLPE insulated stranded copper wires |  | Mtrs | 5500
3 | 4 sq.mm (Cu) 1.1kV grade,XLPE insulated stranded copper wires |  | Mtrs | 2000
H | Street lighting Pole
1 | Street lighting Double arm Swaged tubular galvanized steel pole (9 mtr. above ground) including foundation along with necessary pipe-reducer / fixing-bracket for fixing the Luminaire, weather proof junction box with fixing brackets, 3mtr. long 40mm dia MS rod, 25x3mm GI flat, DP 6A MCB, 1.5Sq.mm FRLS Copper wire, 2nos. 2 mtr. long 50mm dia GI Pipe for cable entry, Base plate, Foundation Bolts, nuts etc. with 2x150W LED Street lighting fixture IP-65 FRP junction box shall be provided with necessary terminal suitable for termination of 2nos. of 4Cx35Sq.mm Al. Armoured. Cable. |  | Nos. | 60
2 | Street lighting Single arm Swaged tubular galvanized steel pole (9 mtr. above ground) including foundation along with necessary pipe-reducer / fixing-bracket for fixing the Luminaire, weather proof junction box with fixing brackets, 3mtr. long 40mm dia MS rod, 25x3mm GI flat, DP 6A MCB, 1.5Sq.mm FRLS Copper wire, 2nos. 2 mtr. long 50mm dia GI Pipe for cable entry, Base plate, Foundation Bolts, nuts etc. with 150W LED Street lighting fixture IP-65 FRP junction box shall be provided with necessary terminal suitable for termination of 2nos. of 4Cx35Sq.mm Al. Armoured. Cable. |  | Nos. | 300
3 | Half pole, bracket, CRCA junction box of IP 55 with loop in loop out facility & accessories for periphery lighting (with 70 W LED Medium Bay Lamp) |  | Nos | 50
4 | J-Type Pole 3 Meter GI Type with Junction box |  | Nos. | 30
5 | J-Type Pole 2 Meter GI Type with Junction box |  | Nos. | 40
I | High Mast
1 | 20 M High Mast hot dip galvanized Raising/Lowering type Lighting mast having galvanized lantern carriage arrangement, integral power tool, 24 nos 200W LED light, Aviation obstruction light 2 nos, lightning protection, earthing, wire, civil foundation works and Feeder pillar, control panel with raise/ lower mechanism.Control panel housing suitable control circuit for the operation of the mast, precision timer for automatic On/Off control |  | Nos. | 10
J | Lighting Panels & Receptacles Panels
1 | Lighting Panel: (Type - LP-A) | Double door type RAL 7032 paint shade, wall mounted suitable for flush mounting, bottom cable entry, suitable for pad locking arrangement with following with 415 V AC , 3ph, 4W bus & one 63 A 4P MCB as incomer and 18 nos 20A, 240V Double Pole RCBO 30ma as outgoing in sheet steel enclosure. LP shall have degree of protection of IP 55 | Nos. | 32
2 | Lighting SDB - (Type - LP-C) | Lighting SDB having Incoming : 16 A DPRCBO and Outgoing : 6 A DP MCB (6Nos | Nos. | 10
3 | Street Lighting panel - (Type - LP-F) | Street Lighting panel with 415 V AC , 3ph, 4W bus & one 63A 4P MCB Isolator, 63A TP Contactor , Synchronous timer, Auto/Manual selector switch, photo electric switch, by pass switch for timer/ photo switch, push buttons, indicating lamps, at incomer and 20A, 6 nos. 415V AC 4P RCBO as outgoing feeder in sheet steel enclosure. Light sensor shall be enclosed in separate weather proof enclosure. LP shall have dgree of protection of IP 55 | Nos. | 40
4 | Street Lighting panel - (Type - LP-G) | Street Lighting panel with 415 V AC , 3ph, 4W bus & one 63A 4P MCB, 63A TP Contactor , Synchronous timer, Auto/Manual selector switch, photo electric switch, by pass switch for timer/ photo switch, push buttons, indicating lamps, at incomer and 20A, 6 nos. 240V AC (DP type) RCBO as outgoing feeder in sheet steel enclosure. Light sensor shall be enclosed in separate weather proof enclosure. LP shall have dgree of protection of IP 55 | Nos. | 20
5 | Receptacle panel - (Type - RP-A) | Receptacle panel with 415 V AC , 3ph, 4W bus & 63 A RCBO 100 mA as incomer and 20A, 12 nos. DP MCB as outgoing in sheet steel enclosure. RP shall have dgree of protection of IP 55 | Nos. | 8
6 | Receptacle panel - (Type - RP-B) | Receptacle panel with 415 V AC , 3ph, 4W bus & One 63A TPN 30 mA RCBO isolator incomer and 20 A, 12 nos. 240V AC SP MCB as outgoing in sheet steel enclosure. RP shall have dgree of protection of IP 55 | Nos. | 6
7 | Receptacle panel - (Type - RP-C) | Receptacle panel with 415 V AC , 3ph, 4W bus & One 63A TPN 30mA RCBO isolator incomer and 20 A, 6 nos. 240V AC SP MCB as outgoing in sheet steel enclosure. RP shall have degree of protection of IP 55 | Nos. | 4
K | Supply and installation of following sizes of galvanized steel conduits from lighting panels to lighting fixtures/switchboards/ single phase receptacles including necessary fittings (bends, circular boxes, adaptor, coupler etc) , clamps, saddles & hardwares .
1 | 20mm dia galvanized steel conduits | Thickness - 1.6mm | Mtrs | 600
2 | 25mm dia galvanized steel conduits | Thickness - 1.6mm | Mtrs | 12000
3 | 40mm dia galvanized steel conduits | Thickness - 2mm | Mtrs | 3000
4 | 20 mm DIA flexible steel conduits | Thickness - 1.6mm | Mtrs | 200
5 | 25 mm DIA flexible steel conduits | Thickness - 1.6mm | Mtrs | 800
L | Flexible PVC Conduit (Colour shall be RAL 9002)
1 | 20 mm Dia flexible PVC conduit including necessary fittings (adapter, nipple etc) and hardwares |  | Mtrs | 300
2 | 40 mm Dia flexible PVC conduit including necessary fittings (adapter, nipple etc) and hardwares |  | Mtrs | 300
M | SUB MAINS / CIRCUIT MAINS
Wiring of Submains/ circuit mains in concealed or surface conduit system in 25 mm diameter rigid PVC conduit of medium guage having ISI and FIA approval with all necessary accessories as per IS 9537:3. 1100 V grade FRLS copper flexible wires for Phase, neutral & earth etc., complete The cost of conduit shall be included. The laying cost shall also include civil works such as small chipping work if necessory at site. Flexible PVC conduit shall be used wherever required.
1 | SUB MAINS / CIRCUIT MAINS : DB to first light point (applicable for MCB Controlled point) or DB to first point Switch box or Switchbox to Switchbox
2 | FRLS, 2 runs of 4 sq.mm copper wire + 1 run of 2.5 sq.mm copper wire with 25mm dia. PVC, conduit (From DB TO 20A socket/6+16A Socket) |  | Rmt | 1200
3 | FRLS, 2 runs of 2.5 sq.mm copper wire + 1 run of 1.5 sq.mm copper wire with 25mm dia. PVC, conduit (From DB to Switch Board/ 6A Power Socket, Switchboard to Switchboard) |  | Rmt | 1400
4 | FRLS, 2 runs of 1.5 sq.mm copper wire + 1 run of 1.5 sq.mm copper wire with 20mm dia. PVC, conduit |  | Rmt | 1200
N | Point wiring cum submain / circuit wiring
Wiring with 2 x 1.5 sq.mm PVC insulated 1100 V grade FRLS copper conductor wires and 1 x 1.5 sq.mm PVC insulated earth wire in, 20 mm diameter rigid PVC conduit of medium guage having ISI and FIA approval with all necessary accessories conduit as per IS 9537:3. Height of ceiling varies from 4.5 to 4.8 meters. A separate neutral shall be run for each circuit. Flexible PVC conduit shall be used wherever required. Light/Fan point shall be inclusive of Moduler Switches / Switch Boxes/Back Box/connectors/ Junction Box / ceiling rose / terminations etc. For point length greater than 10 mtr. additional route length to be taken from above line items
1 | Single light point controlled by a 1no 6A switch : |  | Nos | 100
2 | Two light point controlled by a 1no 6A switch : |  | Nos | 140
3 | Three light point controlled by a 1no 6A switch): |  | Nos | 150
4 | Four light points controlled by 1 Nos of 6A switches : |  | Nos | 120
5 | Five light points controlled by 1 Nos of 6A switches : |  | Nos | 24
6 | Exhaust fan point with 6A socket provided near fan and controlled by a 6A switch |  | Nos | 60
O | Following sizes of FRLS XLPE insulated Armoured copper Cable from lighting panels to lighting fixtures/switchboards/ single phase receptacles in conduits including termination at ends using suitable crimping lugs
1 | 1.5 sq.mm 3 Core FRLS XLPE insulated Armoured copper Cable (Outgoing from LP/Looping/earthing) |  | Meter | 2000
2 | 2.5 sq.mm 3 Core Cable FRLS XLPE insulated Armoured copper Cable (Outgoing from LP/Looping) |  | Meter | 7000
3 | 4 sq.mm 3 Core. FRLS XLPE insulated Armoured copper Cable (Outgoing from LP/Looping) |  | Meter | 1200
P | GI type Pre fabricated Cable Tray complete with Coupler Plates, Fasteners, Clamps and Fixing Hardware as required
1 | 100mm wide GI ladder Cable Trays |  | Meter | 300
2 | 150mm wide GI ladder Cable Trays |  | Meter | 400
3 | 300mm wide GI ladder Cable Trays |  | Meter | 500
Q | STRUCTURAL STEEL
1 | Supply, fabrication, erection of MS base frames, supports etc. made out of rolled MS channels, angles, pipes, plates etc. including welding, bolting, riveting, grouting etc. applying one coat of primer and two finished coats of approved epoxy anticorrosive paint . |  | MT | 10
R | EARTHING ITEMS
1 | 14 SWG GS Wire |  | MTRS. | 100000
2 | 3 M long 40mm dia MS rod |  | NOS. | 30
3 | 25X3 mm GS Flat |  | MTRS. | 1200
S | 1.1kV grade, stranded Aluminum / Copper conductor, XLPE insulated, armoured, overall FRLS extruded PVC sheathed cables confirming to IS 7098 Part-I.
1 | 3.5Cx35 Al |  | MTRS. | 1500
2 | 4Cx16 Al |  | MTRS. | 2000
3 | 2Cx4 Cu |  | MTRS. | 1000
4 | 4Cx2.5 Cu |  | MTRS. | 15000
5 | 3Cx2.5 Cu |  | MTRS. | 5000
6 | 2Cx2.5 Cu |  | MTRS. | 3000
T | CABLE TERMINATION Including Glands, lugs, cable tags, Cable ferrules, Cable ties etc. as per cable schedule. (1 Set consisting of 1 double compression brass gland , Nos of Lugs & Material Cu/Al shall be same as number of core of cable & type of cable)
1 | 3.5Cx35 Al |  | Set | 400
2 | 4Cx16 Al |  | Set | 200
3 | 2Cx4 Cu |  | Set | 100
4 | 4Cx2.5 Cu |  | Set | 1700
5 | 3Cx2.5 Cu |  | Set | 180
6 | 2Cx2.5 Cu |  | Set | 100
U | BURRIED CABLE TRENCH
1 | Construction of buried cable trenches of following sizes including excavation and back filling , river sand bedding, spreading of brick etc . 600x750x8000mm |  | cubic meter | -
V | Accessories for (Saddel, PvC Grip, Screw ETC) Saddling Cable & Conduit |  | Lot | 1
W | Ladder
1 | Free standing shall be aluminium ladder, adjustable from 5M to 10M |  | Nos | 4
2 | wheel mounted adjustable aluminium ladder shall be 10M high aluminium ladder. |  | Nos | 4