## Sheet1
section_context_for_this_product_block | full_product_description | core_product_name | acronymed_core_product_name | size | feature_or_specifications | quantity | unit
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 1.1 ¦ Design and supply of H-pole Structure for 11 KV Incoming Power Supply with Gang operated isolator, D.O. fuse with base, lightning arrestors, Insulator, earthing, construction of earth Pits, fencing, gate, gravel laying, padlocking, signages including all civil works for 11 KV Supply. The design shall be in line with Electricity board guidelines. | h-pole structure |  | supply voltage: 11 KV | feature: gang operated isolator, feature: d.o. (drop out) fuse with base, feature: lightning arrestors, feature: insulator, feature: earthing, feature: construction of earth pits, feature: fencing, feature: gate, feature: gravel laying, feature: padlocking, feature: signages, feature: all civil works, standard: electricity board guidelines | 1.0 | Set
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 2.1 ¦ 11 KV, 630 A, VCB panel indoor type comprising of metering and protection system including numerical relay, auxiliary relay, CTs, PTs , indication lamp, switches along with Weather proof double compression Ni plated brass cable gland and crimping type cable lugs for all incoming and outgoing cables and as per specfication.. | vcb panel | vcb panel (vacuum circuit breaker panel) | supply voltage: 11 KV, current: 630 A | type: indoor, feature: metering and protection system, feature: numerical relay, feature: auxiliary relay, feature: cts (current transformers), feature: pts (potential transformers), feature: indication lamp, feature: switches, feature: weather proof double compression ni (nickel) plated brass cable gland, feature: crimping type cable lugs for all incoming and outgoing cables, standard: as per specification | 1.0 | No.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 3.1 ¦ 500 KVA, 11KV/433V, Dyn11, AN type with off load tap changer power transformer complete with all accessories as per attached specifications & DS. | power transformer |  | capacity: 500 KVA, primary voltage: 11 KV, secondary voltage: 433 V | vector group: dyn11, cooling type: an (air natural), feature: off load tap changer, feature: complete with all accessories, standard: as per attached specifications & ds (data sheet) | 1.0 | No.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 3.2 ¦ 200KVA, 415V/433V, Dyn1, natural air cooled Dry type Lighting transformer as per attached specifications & DS. | lighting transformer |  | capacity: 200 KVA, primary voltage: 415 V, secondary voltage: 433 V | vector group: dyn1, cooling type: natural air cooled, type: dry type, standard: as per attached specifications & ds (data sheet) | 1.0 | No.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 4.1 ¦ PMCC: 415V, 3phase, 4 wire, 50 Hz, 800A, 50 KA for 1second, double front fully draw out type PMCC comprising of ACBs, CTs/PTs, relays, indicating lamps etc. as per attached SLDs, specifications & DS. | pmcc (power and motor control center) | pmcc | voltage: 415 V, phases: 3 phase, wires: 4 wire, frequency: 50 Hz, current: 800 A, short circuit withstand: 50 KA for 1 second | type: double front fully draw out, feature: acbs (air circuit breakers), feature: cts/pts (current transformers/potential transformers), feature: relays, feature: indicating lamps, standard: as per attached slds (single line diagrams), specifications & ds (data sheet) | 1.0 | No.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 4.2 ¦ MLDB: 415V, 3phase, 4 wire, 50 Hz, 400A, 25KA for 1second MLDB including as per attached SLD, specifications & DS. | mldb (main lighting distribution board) | mldb | voltage: 415 V, phases: 3 phase, wires: 4 wire, frequency: 50 Hz, current: 400 A, short circuit withstand: 25 KA for 1 second | standard: as per attached sld (single line diagram), specifications & ds (data sheet) | 1.0 | No.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 4.3 ¦ Fire water MCC: 415V, 3phase, 4 wire, 50 Hz, 400A, 50KA for 1second MCC including as per attached SLD, specifications & DS. | fire water mcc (motor control center) | mcc | voltage: 415 V, phases: 3 phase, wires: 4 wire, frequency: 50 Hz, current: 400 A, short circuit withstand: 50 KA for 1 second | standard: as per attached sld (single line diagram), specifications & ds (data sheet) | 1.0 | No.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 4.4 ¦ CAPACITOR PANEL : 415V, 3Ph-N, 50Hz, 50KA for 1second, 250KVAR capacitor panel with capacitors 2X75, 1X50, 2X25 KVAR) and APFC relay, protections, filters etc. as per attached SLD, specifications & DS including weather proof double compression Ni plated brass cable glands and lugs for all incoming and outgoing feeders. | capacitor panel |  | voltage: 415 V, phases: 3 phase-neutral, frequency: 50 Hz, short circuit withstand: 50 KA for 1 second, capacity: 250 KVAR (2X75, 1X50, 2X25 KVAR) | feature: apfc (automatic power factor correction) relay, feature: protections, feature: filters, standard: as per attached sld (single line diagram), specifications & ds (data sheet), feature: weather proof double compression ni (nickel) plated brass cable glands and lugs for all incoming and outgoing feeders | 1.0 | No.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 5.1 ¦ LDB / LP, W eatherproof, IP 65, incomer 63A, 3 Phase, 4 wire, 3 Way LDB, 10kA for 1 sec with RCBO | ldb (lighting distribution board) | ldb | incomer: 63 A, phases: 3 phase, wires: 4 wire, ways: 3 way, short circuit withstand: 10 KA for 1 sec | type: weatherproof, protection: ip 65, feature: rcbo (residual current circuit breaker with overcurrent protection) | 1.0 | No.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 5.2 ¦ LDB / LP, W eatherproof, IP 65, incomer 63A, 3 Phase, 4 wire, 6 Way LDB, 10kA for 1 sec with RCBO | ldb (lighting distribution board) | ldb | incomer: 63 A, phases: 3 phase, wires: 4 wire, ways: 6 way, short circuit withstand: 10 KA for 1 sec | type: weatherproof, protection: ip 65, feature: rcbo (residual current circuit breaker with overcurrent protection) | 1.0 | No.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 5.3 ¦ LDB / LP, Outdoor type, Flame proof (FLP) Type, IP class suitable for FLP and minimum protection shall be IP-65, incomer 63A, 3 Phase, 4 wire, 3 Way LDB, 10kA for 1 sec with RCBO | ldb (lighting distribution board) | ldb | incomer: 63 A, phases: 3 phase, wires: 4 wire, ways: 3 way, short circuit withstand: 10 KA for 1 sec | type: outdoor, type: flame proof (flp), protection: ip class suitable for flp, minimum protection: ip-65, feature: rcbo (residual current circuit breaker with overcurrent protection) | 5.0 | No.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 5.4 ¦ LDB / LP, Outdoor type, Flame proof (FLP) Type, IP class suitable for FLP and minimum protection shall be IP-65 , incomer 63A, 3 Phase, 4 wire, 6 Way LDB, 10kA for 1 sec with RCBO | ldb (lighting distribution board) | ldb | incomer: 63 A, phases: 3 phase, wires: 4 wire, ways: 6 way, short circuit withstand: 10 KA for 1 sec | type: outdoor, type: flame proof (flp), protection: ip class suitable for flp, minimum protection: ip-65, feature: rcbo (residual current circuit breaker with overcurrent protection) | 1.0 | No.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 5.5 ¦ UPS DB - 230V, 50Hz,Outdoor type, Flame proof (FLP) Type, IP class suitable for FLP and minimum protection shall be IP-65, incomer 63A, 3 Phase, 4 wire, 3 Way LDB, 10kA for 1 sec with RCBO | ups db (uninterruptible power supply distribution board) | ups db | voltage: 230 V, frequency: 50 Hz, incomer: 63 A, phases: 3 phase, wires: 4 wire, ways: 3 way, short circuit withstand: 10 KA for 1 sec | type: outdoor, type: flame proof (flp), protection: ip class suitable for flp, minimum protection: ip-65, feature: rcbo (residual current circuit breaker with overcurrent protection) | 1.0 | No.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 5.6 ¦ Feeder Pillar for street Lighting . 415V, 3Ph, 50Hz, Flame proof (IP class suitable for FLP and minimum protection shall be IP-65) sheet steel enclosure column/structural mounted, with photovoltic cell based control with A/M selector switch, start/stop PB, indicating lamps etc. with 3mm thick FRP canopy and side cover of the following incoming and outgoing feeders: i) 1no.-Incomer 63A, 3 phase RCBO 30 mA ii) 3nos.-O/G 16A TPN MCB | feeder pillar |  | voltage: 415 V, phases: 3 phase, frequency: 50 Hz, enclosure thickness: 3 mm, incomer: 63 A, outgoing: 3 x 16 A tpn mcb | type: flame proof (ip class suitable for flp), minimum protection: ip-65, enclosure: sheet steel, mounting: column/structural, feature: photovoltic cell based control, feature: a/m (auto/manual) selector switch, feature: start/stop pb (push button), feature: indicating lamps, feature: frp (fiber reinforced plastic) canopy and side cover, feature: rcbo 30 ma (residual current circuit breaker with overcurrent protection), feature: tpn mcb (triple pole and neutral miniature circuit breaker) | 1.0 | No.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 5.7 ¦ PDB at outdoor location . 415V, 3Ph, 50Hz, W eatherproof and Flame proof (IP class suitable for FLP and minimum protection shall be IP-65) sheet steel enclosure column/structural mounted, start/stop PB, indicating lamps etc. with 3mm thick FRP canopy and side cover of the following incoming and outgoing feeders: i) 1no.-Incomer 100A TPN MCCB ii) 5nos.-O/G 32A TPN MCCB One outgoing shall be provided with photovoltic cell based control with A/M selector switch, start/stop PB, indicating lamps etc to feed the street light. | pdb (power distribution board) | pdb | voltage: 415 V, phases: 3 phase, frequency: 50 Hz, enclosure thickness: 3 mm, incomer: 100 A tpn mccb, outgoing: 5 x 32 A tpn mccb | type: weatherproof, type: flame proof (ip class suitable for flp), minimum protection: ip-65, enclosure: sheet steel, mounting: column/structural, feature: start/stop pb (push button), feature: indicating lamps, feature: frp (fiber reinforced plastic) canopy and side cover, feature: photovoltic cell based control, feature: a/m (auto/manual) selector switch | 1.0 | No.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 6.1 ¦ 110V, 10A BATTERY CHARGER consisting of dual float cum boost charger and Ni-Cd type battery (43AH) with two hour back up capacity as per attached specifications & DS. | battery charger |  | voltage: 110 V, current: 10 A, battery capacity: 43 AH, backup time: 2 hours | feature: dual float cum boost charger, battery type: ni-cd (nickel-cadmium), standard: as per attached specifications & ds (data sheet) | 1.0 | No.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 6.2 ¦ DC DISTRIBUTION BOARD: 110V DC, 2 wire 63A DC Distribution Board fed by duel float cum boost charger as per attached SLD, specifications & DS. Incomer: 63A DP MCB Outgoing: 15nos. 16A DP MCB | dc distribution board |  | voltage: 110 V DC, wires: 2 wire, incomer: 63 A dp mcb, outgoing: 15 x 16 A dp mcb | fed by: dual float cum boost charger, standard: as per attached sld (single line diagram), specifications & ds (data sheet) | 1.0 | No.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 7.1 ¦ Supply of Flameproof lighting fixtures, Lamps & Accessories as per attached specification. (All Lighting fixtures shall be provided with required no. of FLP double compression stainless steel cable glands and FLP stopping plug and control gear boxes etc. All fixtures shall have inbuilt JBs for loop in loop out facility of 3Cx2.5 sqmm Cu lighting cables) 230 Volt AC, 40W Well glass Flameproof Ex'd',LED lighting fixtures and all other accessories | flameproof lighting fixtures |  | voltage: 230 V AC, power: 40 W | type: well glass, type: flameproof ex'd', type: led, feature: flp (flame proof) double compression stainless steel cable glands, feature: flp stopping plug, feature: control gear boxes, feature: inbuilt jbs (junction boxes) for loop in loop out facility of 3cx2.5 sqmm cu (copper) lighting cables, standard: as per attached specification | 135.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 7.2 ¦ Supply of weatherproof lighting fixtures, Lamps & Accessories as per attached specification. (All Lighting fixtures shall be provided with required no. of double compression stainless steel cable glands and stopping plug. All control gear boxes shall be provided with 3mm thick FRP canopy with side cover. .All fixtures shall have inbuilt JBs for loop in loop out facility of 3Cx2.5 sqmm Cu lighting cables) 230 Volt AC, 40W Well glass weatherproof ,LED lighting fixtures and all other accessories | weatherproof lighting fixtures |  | voltage: 230 V AC, power: 40 W | type: well glass, type: weatherproof, type: led, feature: double compression stainless steel cable glands, feature: stopping plug, feature: control gear boxes with 3 mm thick frp (fiber reinforced plastic) canopy with side cover, feature: inbuilt jbs (junction boxes) for loop in loop out facility of 3cx2.5 sqmm cu (copper) lighting cables, standard: as per attached specification | 22.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 8.1 ¦ 240 Volt AC, 16 A, Cast Aluminium Flameproof Ex'd' (Zone-1, IIA / IIB) 4-way, 125 mm (minimum) internal dimensions junction box with terminals block suitable for 2.5 sq.mm along with flameproof double compression Ni plated brass cables glands for all incoming and outgoing cables,PVC shroud and other accessories. | junction box |  | voltage: 240 V AC, current: 16 A, ways: 4-way, internal dimensions: 125 mm (minimum) | material: cast aluminium, type: flameproof ex'd', zone: zone-1, gas group: iia or iib, terminal block suitability: 2.5 sq.mm, feature: flameproof double compression ni (nickel) plated brass cable glands for all incoming and outgoing cables, feature: pvc shroud, feature: other accessories | 45.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 8.2 ¦ 240 Volt AC, 16 A, Cast Aluminium weatherproof 4-way, 125 mm (minimum) internal dimensions junction box with terminals block suitable for 2.5 sq.mm along with weatherproof double compression Ni plated brass cables glands for all incoming and outgoing cables,PVC shroud and other accessories. | junction box |  | voltage: 240 V AC, current: 16 A, ways: 4-way, internal dimensions: 125 mm (minimum) | material: cast aluminium, type: weatherproof, terminal block suitability: 2.5 sq.mm, feature: weatherproof double compression ni (nickel) plated brass cable glands for all incoming and outgoing cables, feature: pvc shroud, feature: other accessories | 18.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 8.3 ¦ JUNCTION BOXES FOR PUMP MOTOR (WEATHER PROOF, FLAME PROOF): Design, Supply, Installation, Testing and Commissionong of following 415V, 3P, Industrial type, W eatherproof, Flame proof “Ex-d” (suitable for hazardous area of gas group IIA/IIB, temperature class T3 and Zone-1), IP 65 suitable for Wall / Column / Structure mounting Including cabling from JB to terminal box for Star-Delta pump motor having different terminal for star and delta connection. All JBs shall be made up of cast Aluminium alloy (LM6 grade) with Canopy of 14 gauge CRCA sheet with side cover. JBs shall confirm to specification/data sheet of tender document. Junction Boxes shall be complete with busbar of suitable rating, support insulator, suitable for 2 nos. of 1RX 3.5 C X 150 Sqmm of Incoming cable size and 2 nos. of 1RX 3.5 C X 95 Sqmm of outgoing cable size XLPE insulated, extruded PVC inner & outer sheathed, FRLS, Armoured cables & shall be supplied along with FLP type double compression, Ni plated brass cable glands, lugs & plugs. However, exact cable sizes shall be indicated during drawing approval only. | junction box |  | voltage: 415 V, phases: 3P, incoming cable size: 2 nos. of 1RX 3.5 C X 150 Sqmm, outgoing cable size: 2 nos. of 1RX 3.5 C X 95 Sqmm | type: weatherproof, type: flameproof ex-d, suitability: hazardous area of gas group iia or iib, temperature class: t3, zone: zone-1, protection: ip 65, mounting: wall or column or structure, feature: cabling from jb to terminal box for star-delta pump motor having different terminal for star and delta connection, material: cast aluminium alloy (lm6 grade), canopy: 14 gauge crca (cold rolled close annealed) sheet with side cover, feature: busbar of suitable rating, feature: support insulator, cable insulation: xlpe, cable sheath: extruded pvc inner and outer sheathed, cable type: frls (flame retardant low smoke), cable type: armoured, feature: flp (flameproof) type double compression ni (nickel) plated brass cable glands, feature: lugs and plugs, standard: as per specification/data sheet of tender document | 1.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 9 ¦ RECEPTACLES | receptacles
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 9.1 ¦ Supply of flameproof Interlocking type switch sockets and plugs of following ratings as per attached specifications. All switch sockets shall be provided with 3mm thick FRP canopy with side cover and required no. of FLP double compression stainless steel cable glands and FLP stopping plug. i) 415V, 5-pin, 63A flame proof switch socket and plug | switch socket and plug |  | voltage: 415 V, pins: 5-pin, current: 63 A | type: flameproof, type: interlocking, canopy: 3mm thick frp (fiber reinforced plastic) with side cover, cable gland: flp (flameproof) double compression stainless steel, feature: flp stopping plug, standard: as per attached specifications | 4.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 9.1 ¦ Supply of flameproof Interlocking type switch sockets and plugs of following ratings as per attached specifications. All switch sockets shall be provided with 3mm thick FRP canopy with side cover and required no. of FLP double compression stainless steel cable glands and FLP stopping plug. ii) 240V, 3-pin, 16A/5A flame proof switch socket and plug | switch socket and plug |  | voltage: 240 V, pins: 3-pin, current: 16 A or 5 A | type: flameproof, type: interlocking, canopy: 3mm thick frp (fiber reinforced plastic) with side cover, cable gland: flp (flameproof) double compression stainless steel, feature: flp stopping plug, standard: as per attached specifications | 6.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 9.2 ¦ Supply of weatherproof Interlocking type switch sockets and plugs of following ratings as per attached specifications. All switch sockets shall be provided with 3mm thick FRP canopy with side cover and required no. of double compression stainless steel cable glands and stopping plug. i) 415V, 5-pin, 63A weatherproof switch socket and plug | switch socket and plug |  | voltage: 415 V, pins: 5-pin, current: 63 A | type: weatherproof, type: interlocking, canopy: 3mm thick frp (fiber reinforced plastic) with side cover, cable gland: double compression stainless steel, feature: stopping plug, standard: as per attached specifications | 2.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 9.2 ¦ Supply of weatherproof Interlocking type switch sockets and plugs of following ratings as per attached specifications. All switch sockets shall be provided with 3mm thick FRP canopy with side cover and required no. of double compression stainless steel cable glands and stopping plug. ii) 240V, 3-pin, 16A/5A weatherproof switch socket and plug | switch socket and plug |  | voltage: 240 V, pins: 3-pin, current: 16 A or 5 A | type: weatherproof, type: interlocking, canopy: 3mm thick frp (fiber reinforced plastic) with side cover, cable gland: double compression stainless steel, feature: stopping plug, standard: as per attached specifications | 2.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 10 ¦ RIGID/ FLEXIBLE CONDUIT Supply of PVC rigid conduit of min. 2mm thick wall, heavy duty type as per IS (with bends, reducers, couplers etc.) of following sizes:- 10.1 ¦ 25 mm Dia. PVC Rigid Conduit | pvc rigid conduit |  | diameter: 25 mm, wall thickness: min. 2 mm | type: heavy duty, standard: is (indian standard), feature: with bends, reducers, couplers etc. | 50.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 10 ¦ RIGID/ FLEXIBLE CONDUIT Supply of PVC rigid conduit of min. 2mm thick wall, heavy duty type as per IS (with bends, reducers, couplers etc.) of following sizes:- 10.2 ¦ 50 mm Dia. PVC Rigid Conduit | pvc rigid conduit |  | diameter: 50 mm, wall thickness: min. 2 mm | type: heavy duty, standard: is (indian standard), feature: with bends, reducers, couplers etc. | 150.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 10 ¦ RIGID/ FLEXIBLE CONDUIT Supply of PVC rigid conduit of min. 2mm thick wall, heavy duty type as per IS (with bends, reducers, couplers etc.) of following sizes:- 10.3 ¦ 75 mm Dia. PVC Rigid Conduit | pvc rigid conduit |  | diameter: 75 mm, wall thickness: min. 2 mm | type: heavy duty, standard: is (indian standard), feature: with bends, reducers, couplers etc. | 50.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 10 ¦ RIGID/ FLEXIBLE CONDUIT Supply of following PVC flexible conduit of min. 2mm thick wall, heavy duty type & as per IS: 2509. 10.4 ¦ 25 mm Dia PVC Flexible Conduit | pvc flexible conduit |  | diameter: 25 mm, wall thickness: min. 2 mm | type: heavy duty, standard: is 2509 (indian standard 2509) | 425.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 11 ¦ Lighting Cable 0.6/1 kV grade 3C X 2.5 Sqmm Cu XLPE insulated FRLS PVC sheathed Lighting Cable | lighting cable |  | voltage grade: 0.6/1 kV, cores: 3C, conductor size: 2.5 Sqmm | conductor material: cu (copper), insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke) pvc (polyvinyl chloride) | 1800.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 12 ¦ LIGHTING POLES Supply of 9.5 Mtr lighting pole (polygonal type) for base mounting complete with all accessories like MCB & terminal block, JB (as applicable), Zinc passivated hardware for fixtures support & pole support, cable protection pipe with earthing rod/ wire as applicable, clamps, nuts, bolts, etc. | lighting pole |  | height: 9.5 mtr | type: polygonal, mounting: base, accessories: mcb (miniature circuit breaker) and terminal block, jb (junction box) as applicable, hardware: zinc passivated for fixtures support and pole support, cable protection: pipe with earthing rod or wire as applicable, accessories: clamps, nuts, bolts, etc. | 6.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 13 ¦ HIGH MAST LIGHTING TOWER Civil & Structural design, engineering & supply of hot dip galvanised High Mast lighting tower (30 m height) including all accessories for High Mast like 24 nos. of High mast lantern Carraige, 16 nos. of 350 watt LED fixture with lamp, head frame, stainless steel rope, double drum winch, Flameproof junction boxes, Flameproof plugs and sockets, Flameproof feeder pillar, galvanised lantern carrier arrangement, cables and cable accessories control panel for feeder pillar etc. as per specification, data sheet and direction of Engineer- in-charge ingincluding supply of commissioning and 2 years O&M spares. | high mast lighting tower |  | height: 30 m | finish: hot dip galvanised, accessories: 24 nos. high mast lantern carriage, 16 nos. 350 watt led fixture with lamp, head frame, stainless steel rope, double drum winch, flameproof junction boxes, flameproof plugs and sockets, flameproof feeder pillar, galvanised lantern carrier arrangement, cables and cable accessories, control panel for feeder pillar, feature: as per specification, data sheet and direction of engineer-in-charge, feature: supply of commissioning and 2 years o&m (operation and maintenance) spares | 4.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14 ¦ SUPPLY OF HT/ LT CABLES AS PER ENCLOSED SPECIFICATION 11 KV(UE) Grade Cables as per typical specifications ; XLPE insulated; PVC Sheathed; Armoured Aluminium Conductor Cables of Following Sizes As Per Is:1554 (Part-I), IS 7098 Part I & IS 1225-Latest Version and Sealed properly with Pvc Caps of following size:- 14.1 ¦ 3C x 240 sqmm (AL) | armoured aluminium conductor cable |  | voltage grade: 11 kV(UE), cores: 3C, conductor size: 240 sqmm | insulation: xlpe (cross-linked polyethylene), sheath: pvc (polyvinyl chloride), type: armoured, conductor material: aluminium, standard: is 1554 (part-i), is 7098 part i, is 1225-latest version, feature: sealed properly with pvc caps | 250.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14 ¦ SUPPLY OF HT/ LT CABLES AS PER ENCLOSED SPECIFICATION 1.1KV(E) XLPE insulated, FRLS, PVC sheathed aluminium/copper conductor, 1.1 kV grade armoured cable conforming to IS:7098, as per approved make AS PER ENCLOSED SPECIFICATIONS 14.2 ¦ 1C x 400, Sqmm XLPE AL | armoured aluminium conductor cable |  | voltage grade: 1.1 kV(E), cores: 1C, conductor size: 400 sqmm | insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke) pvc (polyvinyl chloride), conductor material: aluminium or copper, type: armoured, standard: is 7098 (indian standard 7098), feature: as per approved make, feature: as per enclosed specifications | 1010.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14 ¦ SUPPLY OF HT/ LT CABLES AS PER ENCLOSED SPECIFICATION 1.1KV(E) XLPE insulated, FRLS, PVC sheathed aluminium/copper conductor, 1.1 kV grade armoured cable conforming to IS:7098, as per approved make AS PER ENCLOSED SPECIFICATIONS 14.3 ¦ 3.5C x 150, Sqmm XLPE AL | armoured aluminium conductor cable |  | voltage grade: 1.1 kV(E), cores: 3.5C, conductor size: 150 sqmm | insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke) pvc (polyvinyl chloride), conductor material: aluminium or copper, type: armoured, standard: is 7098 (indian standard 7098), feature: as per approved make, feature: as per enclosed specifications | 100.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14 ¦ SUPPLY OF HT/ LT CABLES AS PER ENCLOSED SPECIFICATION 1.1KV(E) XLPE insulated, FRLS, PVC sheathed aluminium/copper conductor, 1.1 kV grade armoured cable conforming to IS:7098, as per approved make AS PER ENCLOSED SPECIFICATIONS 14.4 ¦ 3.5C x 95, Sqmm XLPE AL | armoured aluminium conductor cable |  | voltage grade: 1.1 kV(E), cores: 3.5C, conductor size: 95 sqmm | insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke) pvc (polyvinyl chloride), conductor material: aluminium or copper, type: armoured, standard: is 7098 (indian standard 7098), feature: as per approved make, feature: as per enclosed specifications | 500.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14 ¦ SUPPLY OF HT/ LT CABLES AS PER ENCLOSED SPECIFICATION 1.1KV(E) XLPE insulated, FRLS, PVC sheathed aluminium/copper conductor, 1.1 kV grade armoured cable conforming to IS:7098, as per approved make AS PER ENCLOSED SPECIFICATIONS 14.5 ¦ 3.5C X 50, Sqmm XLPE AL | armoured aluminium conductor cable |  | voltage grade: 1.1 kV(E), cores: 3.5C, conductor size: 50 sqmm | insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke) pvc (polyvinyl chloride), conductor material: aluminium or copper, type: armoured, standard: is 7098 (indian standard 7098), feature: as per approved make, feature: as per enclosed specifications | 3000.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14.6 ¦ 4C X 25, Sqmm XLPE AL | armoured aluminium conductor cable |  | cores: 4C, conductor size: 25 sqmm | insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke) pvc (polyvinyl chloride), conductor material: aluminium, type: armoured | 6800.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14.7 ¦ 4C X 16, Sqmm XLPE AL | armoured aluminium conductor cable |  | cores: 4C, conductor size: 16 sqmm | insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke) pvc (polyvinyl chloride), conductor material: aluminium, type: armoured | 600.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14.8 ¦ 4C X 10, Sqmm XLPE AL | armoured aluminium conductor cable |  | cores: 4C, conductor size: 10 sqmm | insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke) pvc (polyvinyl chloride), conductor material: aluminium, type: armoured | 100.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14.9 ¦ 4C X 6, Sqmm XLPE AL | armoured aluminium conductor cable |  | cores: 4C, conductor size: 6 sqmm | insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke) pvc (polyvinyl chloride), conductor material: aluminium, type: armoured | 8000.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14.1 ¦ 4C X 4, Sqmm XLPE AL | armoured aluminium conductor cable |  | cores: 4C, conductor size: 4 sqmm | insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke) pvc (polyvinyl chloride), conductor material: aluminium, type: armoured | 3100.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14.11 ¦ 4C X 2.5, Sqmm XLPE AL | armoured aluminium conductor cable |  | cores: 4C, conductor size: 2.5 sqmm | insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke) pvc (polyvinyl chloride), conductor material: aluminium, type: armoured | 2200.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14.12 ¦ 3C X 6, Sqmm XLPE AL | armoured aluminium conductor cable |  | cores: 3C, conductor size: 6 sqmm | insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke) pvc (polyvinyl chloride), conductor material: aluminium, type: armoured | 400.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14.13 ¦ 3C X 2.5, Sqmm XLPE AL | armoured aluminium conductor cable |  | cores: 3C, conductor size: 2.5 sqmm | insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke) pvc (polyvinyl chloride), conductor material: aluminium, type: armoured | 100.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14.14 ¦ 2C X 4, Sqmm XLPE AL | armoured aluminium conductor cable |  | cores: 2C, conductor size: 4 sqmm | insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke) pvc (polyvinyl chloride), conductor material: aluminium, type: armoured | 200.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14.15 ¦ 2C X 16, Sqmm XLPE AL | armoured aluminium conductor cable |  | cores: 2C, conductor size: 16 sqmm | insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke) pvc (polyvinyl chloride), conductor material: aluminium, type: armoured | 900.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | nan ¦ 1.1KV(E) armoured XLPE, FRLS Control Cable of following size:- 14.16 ¦ 7C x 2.5 SQMM CU | armoured copper control cable |  | voltage grade: 1.1 kV(E), cores: 7C, conductor size: 2.5 sqmm | insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke), conductor material: copper, type: armoured | 27000.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | nan ¦ 1.1KV(E) armoured XLPE, FRLS Control Cable of following size:- 14.17 ¦ 3C x 2.5 SQMM CU | armoured copper control cable |  | voltage grade: 1.1 kV(E), cores: 3C, conductor size: 2.5 sqmm | insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke), conductor material: copper, type: armoured | 800.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 15.16 ¦ 1C x 400, Sqmm XLPE AL | double compression stainless steel cable gland |  | suitable cable size: 1C x 400 sqmm | material: stainless steel, type: double compression, suitability: xlpe (cross-linked polyethylene) frls (flame retardant low smoke) cable, standard: is (indian standard), application: indoor use | 60.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 15.17 ¦ 3.5C x 150, Sqmm XLPE AL | double compression stainless steel cable gland |  | suitable cable size: 3.5C x 150 sqmm | material: stainless steel, type: double compression, suitability: xlpe (cross-linked polyethylene) frls (flame retardant low smoke) cable, standard: is (indian standard), application: indoor use | 6.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 15.18 ¦ 3.5C x 95, Sqmm XLPE AL | double compression stainless steel cable gland |  | suitable cable size: 3.5C x 95 sqmm | material: stainless steel, type: double compression, suitability: xlpe (cross-linked polyethylene) frls (flame retardant low smoke) cable, standard: is (indian standard), application: indoor use | 5.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 15.19 ¦ 3.5C X 50, Sqmm XLPE AL | double compression stainless steel cable gland |  | suitable cable size: 3.5C x 50 sqmm | material: stainless steel, type: double compression, suitability: xlpe (cross-linked polyethylene) frls (flame retardant low smoke) cable, standard: is (indian standard), application: indoor use | 22.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 15.2 ¦ 4C X 25, Sqmm XLPE AL | double compression stainless steel cable gland |  | suitable cable size: 4C x 25 sqmm | material: stainless steel, type: double compression, suitability: xlpe (cross-linked polyethylene) frls (flame retardant low smoke) cable, standard: is (indian standard), application: indoor use | 50.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 15.21 ¦ 4C X 16, Sqmm XLPE AL | double compression stainless steel cable gland |  | suitable cable size: 4C x 16 sqmm | material: stainless steel, type: double compression, suitability: xlpe (cross-linked polyethylene) frls (flame retardant low smoke) cable, standard: is (indian standard), application: indoor use | 50.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 15.22 ¦ 4C X 10, Sqmm XLPE AL | double compression stainless steel cable gland |  | suitable cable size: 4C x 10 sqmm | material: stainless steel, type: double compression, suitability: xlpe (cross-linked polyethylene) frls (flame retardant low smoke) cable, standard: is (indian standard), application: indoor use | 4.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 15.23 ¦ 4C X 6, Sqmm XLPE AL | double compression stainless steel cable gland |  | suitable cable size: 4C x 6 sqmm | material: stainless steel, type: double compression, suitability: xlpe (cross-linked polyethylene) frls (flame retardant low smoke) cable, standard: is (indian standard), application: indoor use | 60.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 15.24 ¦ 4C X 4, Sqmm XLPE AL | double compression stainless steel cable gland |  | suitable cable size: 4C x 4 sqmm | material: stainless steel, type: double compression, suitability: xlpe (cross-linked polyethylene) frls (flame retardant low smoke) cable, standard: is (indian standard), application: indoor use | 15.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 15.25 ¦ 4C X 2.5, Sqmm XLPE AL | double compression stainless steel cable gland |  | suitable cable size: 4C x 2.5 sqmm | material: stainless steel, type: double compression, suitability: xlpe (cross-linked polyethylene) frls (flame retardant low smoke) cable, standard: is (indian standard), application: indoor use | 16.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 15.26 ¦ 3C X 2.5, Sqmm XLPE AL | double compression stainless steel cable gland |  | suitable cable size: 3C x 2.5 sqmm | material: stainless steel, type: double compression, suitability: xlpe (cross-linked polyethylene) frls (flame retardant low smoke) cable, standard: is (indian standard), application: indoor use | 5.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 15.27 ¦ 3C X 6, Sqmm XLPE AL | double compression stainless steel cable gland |  | suitable cable size: 3C x 6 sqmm | material: stainless steel, type: double compression, suitability: xlpe (cross-linked polyethylene) frls (flame retardant low smoke) cable, standard: is (indian standard), application: indoor use | 10.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 15.28 ¦ 2C X 4, Sqmm XLPE AL | double compression stainless steel cable gland |  | suitable cable size: 2C x 4 sqmm | material: stainless steel, type: double compression, suitability: xlpe (cross-linked polyethylene) frls (flame retardant low smoke) cable, standard: is (indian standard), application: indoor use | 4.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 15.29 ¦ 2C X 16, Sqmm XLPE AL | double compression stainless steel cable gland |  | suitable cable size: 2C x 16 sqmm | material: stainless steel, type: double compression, suitability: xlpe (cross-linked polyethylene) frls (flame retardant low smoke) cable, standard: is (indian standard), application: indoor use | 4.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 15.3 ¦ 7C x 2.5 SQMM CU | double compression stainless steel cable gland |  | suitable cable size: 7C x 2.5 sqmm | material: stainless steel, type: double compression, suitability: xlpe (cross-linked polyethylene) frls (flame retardant low smoke) cable, standard: is (indian standard), application: indoor use | 70.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 15.31 ¦ 3C x 2.5 SQMM CU | double compression stainless steel cable gland |  | suitable cable size: 3C x 2.5 sqmm | material: stainless steel, type: double compression, suitability: xlpe (cross-linked polyethylene) frls (flame retardant low smoke) cable, standard: is (indian standard), application: indoor use | 10.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of Raychem make heat shrinkable end termination kit suitable for 11 KV (UE) XLPE, FRLS cables of following sizes. 15.33 ¦ 3C x 240 sqmm (AL) ( suitable for outdoor purpose) | heat shrinkable end termination kit |  | suitable cable size: 3C x 240 sqmm (al) | manufacturer: raychem, type: heat shrinkable, suitability: 11 kv (ue) xlpe (cross-linked polyethylene) frls (flame retardant low smoke) cable, application: outdoor purpose | 1.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of Raychem make heat shrinkable end termination kit suitable for 11 KV (UE) XLPE, FRLS cables of following sizes. 15.34 ¦ 3C x 240 sqmm (AL) ( suitable for indoor purpose) | heat shrinkable end termination kit |  | suitable cable size: 3C x 240 sqmm (al) | manufacturer: raychem, type: heat shrinkable, suitability: 11 kv (ue) xlpe (cross-linked polyethylene) frls (flame retardant low smoke) cable, application: indoor purpose | 3.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 16.1 ¦ 3.5C x 150, Sqmm XLPE AL | crimping type heavy duty long barrel tinned flameproof cable lugs |  | suitable cable size: 3.5C x 150 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, type: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable | 25.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 16.2 ¦ 3.5C x 95, Sqmm XLPE AL | crimping type heavy duty long barrel tinned flameproof cable lugs |  | suitable cable size: 3.5C x 95 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, type: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable | 20.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 16.3 ¦ 3.5C X 50, Sqmm XLPE AL | crimping type heavy duty long barrel tinned flameproof cable lugs |  | suitable cable size: 3.5C x 50 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, type: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable | 80.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 16.4 ¦ 4C X 25, Sqmm XLPE AL | crimping type heavy duty long barrel tinned flameproof cable lugs |  | suitable cable size: 4C x 25 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, type: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable | 200.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 16.5 ¦ 4C X 16, Sqmm XLPE AL | crimping type heavy duty long barrel tinned flameproof cable lugs |  | suitable cable size: 4C x 16 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, type: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable | 200.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 16.6 ¦ 4C X 10, Sqmm XLPE AL | crimping type heavy duty long barrel tinned flameproof cable lugs |  | suitable cable size: 4C x 10 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, type: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable | 8.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 16.7 ¦ 4C X 6, Sqmm XLPE AL | crimping type heavy duty long barrel tinned flameproof cable lugs |  | suitable cable size: 4C x 6 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, type: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable | 240.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 16.8 ¦ 4C X 4, Sqmm XLPE AL | crimping type heavy duty long barrel tinned flameproof cable lugs |  | suitable cable size: 4C x 4 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, type: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable | 60.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 16.8 ¦ 4C X 2.5, Sqmm XLPE AL | crimping type heavy duty long barrel tinned flameproof cable lugs |  | suitable cable size: 4C x 2.5 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, type: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable | 64.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 16.9 ¦ 3C X 2.5, Sqmm XLPE AL | crimping type heavy duty long barrel tinned flameproof cable lugs |  | suitable cable size: 3C x 2.5 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, type: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable | 12.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 16.1 ¦ 3C X 6, Sqmm XLPE AL | crimping type heavy duty long barrel tinned flameproof cable lugs |  | suitable cable size: 3C x 6 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, type: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable | 15.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 16.11 ¦ 2C X 4, Sqmm XLPE AL | crimping type heavy duty long barrel tinned flameproof cable lugs |  | suitable cable size: 2C x 4 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, type: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable | 8.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 16.12 ¦ 2C X 16, Sqmm XLPE AL | crimping type heavy duty long barrel tinned flameproof cable lugs |  | suitable cable size: 2C x 16 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, type: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable | 16.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 16.13 ¦ 7C x 2.5 SQMM CU | crimping type heavy duty long barrel tinned flameproof cable lugs |  | suitable cable size: 7C x 2.5 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, type: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable | 500.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 16.14 ¦ 3C x 2.5 SQMM CU | crimping type heavy duty long barrel tinned flameproof cable lugs |  | suitable cable size: 3C x 2.5 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, type: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable | 100.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 16.15 ¦ 1C x 400, Sqmm XLPE AL | crimping type heavy duty long barrel tinned cable lugs |  | suitable cable size: 1C x 400 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable, feature: indoor use | 60.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 16.16 ¦ 3.5C x 150, Sqmm XLPE AL | crimping type heavy duty long barrel tinned cable lugs |  | suitable cable size: 3.5C x 150 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable, feature: indoor use | 25.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 16.17 ¦ 3.5C x 95, Sqmm XLPE AL | crimping type heavy duty long barrel tinned cable lugs |  | suitable cable size: 3.5C x 95 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable, feature: indoor use | 20.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 16.18 ¦ 3.5C X 50, Sqmm XLPE AL | crimping type heavy duty long barrel tinned cable lugs |  | suitable cable size: 3.5C x 50 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable, feature: indoor use | 80.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 16.19 ¦ 4C X 25, Sqmm XLPE AL | crimping type heavy duty long barrel tinned cable lugs |  | suitable cable size: 4C x 25 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable, feature: indoor use | 200.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 16.2 ¦ 4C X 16, Sqmm XLPE AL | crimping type heavy duty long barrel tinned cable lugs |  | suitable cable size: 4C x 16 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable, feature: indoor use | 200.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 16.21 ¦ 4C X 10, Sqmm XLPE AL | crimping type heavy duty long barrel tinned cable lugs |  | suitable cable size: 4C x 10 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable, feature: indoor use | 8.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 16.22 ¦ 4C X 6, Sqmm XLPE AL | crimping type heavy duty long barrel tinned cable lugs |  | suitable cable size: 4C x 6 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable, feature: indoor use | 240.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 16.23 ¦ 4C X 4, Sqmm XLPE AL | crimping type heavy duty long barrel tinned cable lugs |  | suitable cable size: 4C x 4 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable, feature: indoor use | 60.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 16.24 ¦ 4C X 2.5, Sqmm XLPE AL | crimping type heavy duty long barrel tinned cable lugs |  | suitable cable size: 4C x 2.5 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable, feature: indoor use | 64.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 16.25 ¦ 3C X 2.5, Sqmm XLPE AL | crimping type heavy duty long barrel tinned cable lugs |  | suitable cable size: 3C x 2.5 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable, feature: indoor use | 12.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 16.26 ¦ 3C X 6, Sqmm XLPE AL | crimping type heavy duty long barrel tinned cable lugs |  | suitable cable size: 3C x 6 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable, feature: indoor use | 15.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 16.27 ¦ 2C X 4, Sqmm XLPE AL | crimping type heavy duty long barrel tinned cable lugs |  | suitable cable size: 2C x 4 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable, feature: indoor use | 8.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 16.28 ¦ 2C X 16, Sqmm XLPE AL | crimping type heavy duty long barrel tinned cable lugs |  | suitable cable size: 2C x 16 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable, feature: indoor use | 16.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 16.29 ¦ 7C x 2.5 SQMM CU | crimping type heavy duty long barrel tinned cable lugs |  | suitable cable size: 7C x 2.5 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable, feature: indoor use | 500.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 16.3 ¦ 3C x 2.5 SQMM CU | crimping type heavy duty long barrel tinned cable lugs |  | suitable cable size: 3C x 2.5 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable, feature: indoor use | 100.0 | nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.1 ¦ Ladder type GI cable tray (100mmx2mm, 3 Meter length) with minimum hot dip zinc coating 75 micron with accessories like coupler plates,bends, Stainless steels hardwares like nuts & bolts , bends, washers etc and as per IS & ES:8161. d. ¦ 150mm Wide | ladder type galvanized iron cable tray |  | tray size: 100mm x 2mm, tray length: 3 meter, width: 150mm | coating: hot dip zinc, coating thickness: 75 micron, accessories: coupler plates, accessories: bends, accessories: stainless steel hardware (nuts & bolts, washers), standard: indian standard & engineering standard 8161 | 228.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.1 ¦ Ladder type GI cable tray (100mmx2mm, 3 Meter length) with minimum hot dip zinc coating 75 micron with accessories like coupler plates,bends, Stainless steels hardwares like nuts & bolts , bends, washers etc and as per IS & ES:8161. e. ¦ 50mm Wide | ladder type galvanized iron cable tray |  | tray size: 100mm x 2mm, tray length: 3 meter, width: 50mm | coating: hot dip zinc, coating thickness: 75 micron, accessories: coupler plates, accessories: bends, accessories: stainless steel hardware (nuts & bolts, washers), standard: indian standard & engineering standard 8161 | 100.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.2 ¦ 90 deg Horizontal Bend Ladder type (shall be decided as per detail engineering) a. ¦ 750mm Wide | ladder type cable tray horizontal bend |  | width: 750mm | bend angle: 90 degree, type: ladder, feature: shall be decided as per detail engineering | 4.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.2 ¦ 90 deg Horizontal Bend Ladder type (shall be decided as per detail engineering) b. ¦ 600mm Wide | ladder type cable tray horizontal bend |  | width: 600mm | bend angle: 90 degree, type: ladder, feature: shall be decided as per detail engineering | 16.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.2 ¦ 90 deg Horizontal Bend Ladder type (shall be decided as per detail engineering) c. ¦ 300mm Wide | ladder type cable tray horizontal bend |  | width: 300mm | bend angle: 90 degree, type: ladder, feature: shall be decided as per detail engineering | 8.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.2 ¦ 90 deg Horizontal Bend Ladder type (shall be decided as per detail engineering) d. ¦ 150mm Wide | ladder type cable tray horizontal bend |  | width: 150mm | bend angle: 90 degree, type: ladder, feature: shall be decided as per detail engineering | 5.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.3 ¦ TEE Connection Ladder type (shall be decided as per detail engineering) a. ¦ 600mm Wide | ladder type cable tray tee connection |  | width: 600mm | feature: shall be decided as per detail engineering | 16.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.3 ¦ TEE Connection Ladder type (shall be decided as per detail engineering) b. ¦ 300mm Wide | ladder type cable tray tee connection |  | width: 300mm | feature: shall be decided as per detail engineering | 5.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.4 ¦ 90 deg Vertical Bend (inside) Ladder (shall be decided as per detail engineering) a. ¦ 600mm Wide | ladder type cable tray vertical bend (inside) |  | width: 600mm | bend angle: 90 degree, type: ladder, position: inside, feature: shall be decided as per detail engineering | 10.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.4 ¦ 90 deg Vertical Bend (inside) Ladder (shall be decided as per detail engineering) b. ¦ 300mm Wide | ladder type cable tray vertical bend (inside) |  | width: 300mm | bend angle: 90 degree, type: ladder, position: inside, feature: shall be decided as per detail engineering | 2.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.5 ¦ 90 deg Vertical Bend (outside) Perforated (shall be decided as per detail engineering) a. ¦ 600mm Wide | perforated cable tray vertical bend (outside) |  | width: 600mm | bend angle: 90 degree, type: perforated, position: outside, feature: shall be decided as per detail engineering | 10.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.5 ¦ 90 deg Vertical Bend (outside) Perforated (shall be decided as per detail engineering) b. ¦ 300mm Wide | perforated cable tray vertical bend (outside) |  | width: 300mm | bend angle: 90 degree, type: perforated, position: outside, feature: shall be decided as per detail engineering | 2.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.6 ¦ G.I. Perforated Cable Trays , 100 mm deep, 3 mm thick G.I. perforated cable trays (Min. coating 100 microns of zinc) with bend, reducer, coupler plate and other hardware. a. ¦ 750mm Wide | galvanized iron perforated cable tray |  | depth: 100 mm, thickness: 3 mm, width: 750mm | material: galvanized iron, coating: zinc, coating thickness: 100 microns, accessories: bend, accessories: reducer, accessories: coupler plate, accessories: other hardware | 10.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.6 ¦ G.I. Perforated Cable Trays , 100 mm deep, 3 mm thick G.I. perforated cable trays (Min. coating 100 microns of zinc) with bend, reducer, coupler plate and other hardware. b. ¦ 600mm Wide | galvanized iron perforated cable tray |  | depth: 100 mm, thickness: 3 mm, width: 600mm | material: galvanized iron, coating: zinc, coating thickness: 100 microns, accessories: bend, accessories: reducer, accessories: coupler plate, accessories: other hardware | 550.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.6 ¦ G.I. Perforated Cable Trays , 100 mm deep, 3 mm thick G.I. perforated cable trays (Min. coating 100 microns of zinc) with bend, reducer, coupler plate and other hardware. c. ¦ 300mm Wide | galvanized iron perforated cable tray |  | depth: 100 mm, thickness: 3 mm, width: 300mm | material: galvanized iron, coating: zinc, coating thickness: 100 microns, accessories: bend, accessories: reducer, accessories: coupler plate, accessories: other hardware | 175.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.6 ¦ G.I. Perforated Cable Trays , 100 mm deep, 3 mm thick G.I. perforated cable trays (Min. coating 100 microns of zinc) with bend, reducer, coupler plate and other hardware. d. ¦ 150mm Wide | galvanized iron perforated cable tray |  | depth: 100 mm, thickness: 3 mm, width: 150mm | material: galvanized iron, coating: zinc, coating thickness: 100 microns, accessories: bend, accessories: reducer, accessories: coupler plate, accessories: other hardware | 350.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.6 ¦ G.I. Perforated Cable Trays , 100 mm deep, 3 mm thick G.I. perforated cable trays (Min. coating 100 microns of zinc) with bend, reducer, coupler plate and other hardware. e. ¦ 50mm Wide | galvanized iron perforated cable tray |  | depth: 100 mm, thickness: 3 mm, width: 50mm | material: galvanized iron, coating: zinc, coating thickness: 100 microns, accessories: bend, accessories: reducer, accessories: coupler plate, accessories: other hardware | 100.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.7 ¦ 90 deg Horizontal Bend Perforated (shall be decided as per detail engineering) a. ¦ 750mm Wide | perforated cable tray horizontal bend |  | width: 750mm | bend angle: 90 degree, type: perforated, feature: shall be decided as per detail engineering | 3.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.7 ¦ 90 deg Horizontal Bend Perforated (shall be decided as per detail engineering) b. ¦ 600mm Wide | perforated cable tray horizontal bend |  | width: 600mm | bend angle: 90 degree, type: perforated, feature: shall be decided as per detail engineering | 20.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.7 ¦ 90 deg Horizontal Bend Perforated (shall be decided as per detail engineering) c. ¦ 300mm Wide | perforated cable tray horizontal bend |  | width: 300mm | bend angle: 90 degree, type: perforated, feature: shall be decided as per detail engineering | 20.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.8 ¦ 90 deg Vertical Bend (Inside) Perforated (shall be decided as per detail engineering) a. ¦ 600mm Wide | perforated cable tray vertical bend (inside) |  | width: 600mm | bend angle: 90 degree, type: perforated, position: inside, feature: shall be decided as per detail engineering | 10.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.8 ¦ 90 deg Vertical Bend (Inside) Perforated (shall be decided as per detail engineering) b. ¦ 300mm Wide | perforated cable tray vertical bend (inside) |  | width: 300mm | bend angle: 90 degree, type: perforated, position: inside, feature: shall be decided as per detail engineering | 4.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.8 ¦ 90 deg Vertical Bend (Inside) Perforated (shall be decided as per detail engineering) c. ¦ 150mm Wide | perforated cable tray vertical bend (inside) |  | width: 150mm | bend angle: 90 degree, type: perforated, position: inside, feature: shall be decided as per detail engineering | 20.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.9 ¦ 90 deg Vertical Bend (outside) Perforated (shall be decided as per detail engineering) a. ¦ 600mm Wide | perforated cable tray vertical bend (outside) |  | width: 600mm | bend angle: 90 degree, type: perforated, position: outside, feature: shall be decided as per detail engineering | 10.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.9 ¦ 90 deg Vertical Bend (outside) Perforated (shall be decided as per detail engineering) b. ¦ 300mm Wide | perforated cable tray vertical bend (outside) |  | width: 300mm | bend angle: 90 degree, type: perforated, position: outside, feature: shall be decided as per detail engineering | 4.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.9 ¦ 90 deg Vertical Bend (outside) Perforated (shall be decided as per detail engineering) c. ¦ 150mm Wide | perforated cable tray vertical bend (outside) |  | width: 150mm | bend angle: 90 degree, type: perforated, position: outside, feature: shall be decided as per detail engineering | 20.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.1 ¦ TEE Connection Perforated type (shall be decided as per detail engineering) a. ¦ 600mm Wide | perforated cable tray tee connection |  | width: 600mm | type: perforated, feature: shall be decided as per detail engineering | 8.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 18.1 ¦ Supply and Erection of MS Structural Steel: MS structural steel like ISMC , angles, flats etc conforming to IS-2062. : Structural steel work riveted,bolted or welded in built up sections, trusses & framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete: | ms structural steel supply and erection |  |  | material: ms(mild steel), includes: ISMC, angles, flats, standard: indian standard 2062, work: riveted, bolted or welded in built up sections, trusses & framed work, includes: cutting, hoisting, fixing in position, applying priming coat of approved steel primer | 7.0 | Ton
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 18.2 ¦ Supplying and fixing of 6 mm thick chequered plate on cable trench inside swtich room, DG room, earthing pit including cutting, painting, lifting hooks, etc conforming to IS-3502. | chequered plate supply and fixing |  | thickness: 6 mm | application: cable trench inside switch room, DG room, earthing pit, includes: cutting, painting, lifting hooks, standard: indian standard 3502 | 100.0 | Sqm
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 18.3 ¦ 3mm to 10mm thick MS plate conforming to IS-2062 | ms plate |  | thickness: 3mm to 10mm | material: ms(mild steel), standard: indian standard 2062 | 1.5 | Ton
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 19.1 ¦ 50 x 6 mm GI Strip | gi(galvanized iron) strip |  | dimensions: 50 x 6 mm |  | 4400.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 19.2 ¦ 35 x 6 mm GI Strip | gi(galvanized iron) strip |  | dimensions: 35 x 6 mm |  | 2400.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 19.3 ¦ 25 x 6 mm GI Strip | gi(galvanized iron) strip |  | dimensions: 25 x 6 mm |  | 1100.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 19.4 ¦ 1C x 150 mm2 PVC (Al) cable Green colour | pvc(aluminium) cable |  | core: 1C, area: 150 mm2 | colour: green | 560.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 19.5 ¦ 1C x 95 mm2 PVC (Al) cable Green colour | pvc(aluminium) cable |  | core: 1C, area: 95 mm2 | colour: green | 670.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 19.6 ¦ 1C x 35 mm2 PVC (Al) cable Green colour | pvc(aluminium) cable |  | core: 1C, area: 35 mm2 | colour: green | 330.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 19.7 ¦ 1C x 16 mm2 PVC (Al) cable Green colour | pvc(aluminium) cable |  | core: 1C, area: 16 mm2 | colour: green | 850.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 19.8 ¦ 1C x 2.5 mm2 PVC (Cul) cable Green colour | pvc(copper) cable |  | core: 1C, area: 2.5 mm2 | colour: green | 150.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 19.8 ¦ Hot dip Galvanized 10 Holes ∅13mm ground plate 550mmx50mmx6mm earth connection bar with fixing materials/ accessories , SS hardware etc. (min. coating 120 microns of zinc). | hot dip galvanized ground plate earth connection bar |  | holes: 10, hole diameter: 13mm, plate dimensions: 550mm x 50mm x 6mm | coating: hot dip galvanized, minimum coating: 120 microns of zinc, includes: fixing materials/accessories, ss(stainless steel) hardware | 70.0 | Nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 19.9 ¦ Flexible earth provision inclusive of flexible cable, hanger, grounding clip etc for LPG unloading tanker | flexible earth provision |  |  | includes: flexible cable, hanger, grounding clip, application: LPG unloading tanker | 3.0 | Nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 19.1 ¦ 1000mm long,20 dia. Hot dipped GI air termination rod(lightning rod-120 Micron coating) with all fixing material,accessories as per IS:2309 | gi(galvanized iron) air termination rod |  | length: 1000mm, diameter: 20mm | coating: hot dipped, coating thickness: 120 micron, includes: all fixing material, accessories, standard: indian standard 2309, type: lightning rod | 3.0 | Nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 20.1 ¦ 1C x 150 mm2 PVC (Al) cable Green colour | pvc(aluminium) cable |  | core: 1C, area: 150 mm2 | colour: green | 60.0 | Nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 20.2 ¦ 1C x 95 mm2 PVC (Al) cable Green colour | pvc(aluminium) cable |  | core: 1C, area: 95 mm2 | colour: green | 80.0 | Nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 20.3 ¦ 1C x 35 mm2 PVC (Al) cable Green colour | pvc(aluminium) cable |  | core: 1C, area: 35 mm2 | colour: green | 65.0 | Nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 20.4 ¦ 1C x 16 mm2 PVC (Al) cable Green colour | pvc(aluminium) cable |  | core: 1C, area: 16 mm2 | colour: green | 300.0 | Nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 20.5 ¦ 1C x 2.5 mm2 PVC (Cul) cable Green colour | pvc(copper) cable |  | core: 1C, area: 2.5 mm2 | colour: green | 850.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 20.5 ¦ SQUARE TAPE CLAMP | square tape clamp |  |  |  | 40.0 | Nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 20.6 ¦ TEST LINK | test link |  |  |  | 10.0 | Nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 20.7 ¦ TAPE CLIP | tape clip |  |  |  | 1000.0 | Nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 20.8 ¦ TEE JOINT | tee joint |  |  |  | 700.0 | Nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 20.9 ¦ Earth Pit: Supply of Maintanance Free (chemical) Earth electrode with all parts including required hardware for earth pit (equipment earthing, Neutral earthing and for lightning protection) and required test link for checking earth connectivity.as per specification,Attachment-29 LPG.ENG.117.06.03.2001, IS and direction of Engineer-in-charge icludingincluding supply of commissioning and 2 years O&M spares. ¦ a. ¦ Earth pit for Body Earthing ( BEP) | earth pit |  |  | type: maintenance free (chemical), included parts: all parts including required hardware for earth pit (equipment earthing, neutral earthing and for lightning protection), included: required test link for checking earth connectivity, specification: as per specification,Attachment-29 LPG.ENG.117.06.03.2001, standard: indian standard, included: supply of commissioning and 2 years o&m spares | 23.0 | Nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 20.9 ¦ Earth Pit: Supply of Maintanance Free (chemical) Earth electrode with all parts including required hardware for earth pit (equipment earthing, Neutral earthing and for lightning protection) and required test link for checking earth connectivity.as per specification,Attachment-29 LPG.ENG.117.06.03.2001, IS and direction of Engineer-in-charge icludingincluding supply of commissioning and 2 years O&M spares. ¦ b. ¦ Earth pit for Lightning Earthing ( LEP) | earth pit |  |  | type: maintenance free (chemical), included parts: all parts including required hardware for earth pit (equipment earthing, neutral earthing and for lightning protection), included: required test link for checking earth connectivity, specification: as per specification,Attachment-29 LPG.ENG.117.06.03.2001, standard: indian standard, included: supply of commissioning and 2 years o&m spares | 31.0 | Nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 20.9 ¦ Earth Pit: Supply of Maintanance Free (chemical) Earth electrode with all parts including required hardware for earth pit (equipment earthing, Neutral earthing and for lightning protection) and required test link for checking earth connectivity.as per specification,Attachment-29 LPG.ENG.117.06.03.2001, IS and direction of Engineer-in-charge icludingincluding supply of commissioning and 2 years O&M spares. ¦ c. ¦ Earth pit for Neutral Earthing ( NEP) | earth pit |  |  | type: maintenance free (chemical), included parts: all parts including required hardware for earth pit (equipment earthing, neutral earthing and for lightning protection), included: required test link for checking earth connectivity, specification: as per specification,Attachment-29 LPG.ENG.117.06.03.2001, standard: indian standard, included: supply of commissioning and 2 years o&m spares | 8.0 | Nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 20.9 ¦ Earth Pit: Supply of Maintanance Free (chemical) Earth electrode with all parts including required hardware for earth pit (equipment earthing, Neutral earthing and for lightning protection) and required test link for checking earth connectivity.as per specification,Attachment-29 LPG.ENG.117.06.03.2001, IS and direction of Engineer-in-charge icludingincluding supply of commissioning and 2 years O&M spares. ¦ d. ¦ Instrument earth pit (IEP) | earth pit |  |  | type: maintenance free (chemical), included parts: all parts including required hardware for earth pit (equipment earthing, neutral earthing and for lightning protection), included: required test link for checking earth connectivity, specification: as per specification,Attachment-29 LPG.ENG.117.06.03.2001, standard: indian standard, included: supply of commissioning and 2 years o&m spares | 27.0 | Nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 21 ¦ Earth Pit: Supply of Maintanance Free (chemical) Earth electrode 4 mtr long, 100 mm dia suitable for rocky area with all parts including required hardware for earth pit as required as per IS 3043. The pipe shall be embedded as far as possible vertically into the ground, except when hard rock is encountered, where it may be burled inclined to the vertical, the inclination being limited to 30 degree from the vertical. The connection of MS flat to each electrode shall be made through MS links by bolted joints to enable isolation of the electrode for testing purposes. . This is included with excavation, restoration and removal extra earth/rock. and required test link for checking earth connectivity.as per specification,Attachment-29 LPG.ENG.117.06.03.2001, IS and direction of Engineer-in-charge icludingincluding supply of commissioning and 2 years O&M spares. | earth pit |  | length: 4 mtr, diameter: 100 mm | type: maintenance free (chemical), suitable for: rocky area, included parts: all parts including required hardware for earth pit, standard: indian standard 3043, installation: embedded vertically or inclined up to 30 degree from vertical, connection: ms(mild steel) flat to each electrode through ms links by bolted joints, included: enable isolation of the electrode for testing purposes, included: excavation, restoration and removal extra earth/rock, included: required test link for checking earth connectivity, specification: as per specification,Attachment-29 LPG.ENG.117.06.03.2001, standard: indian standard, included: supply of commissioning and 2 years o&m spares | 8.0 | Nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 22 ¦ GENERAL SAFETY EQUIPMENT | general safety equipment
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 22.1 ¦ 11 kV, 900mm wide, electric grade floor rubber mat conforming to relevant IS. ISI mark shall be there on rubber mat. | floor rubber mat |  | width: 900mm | voltage: 11 kv(kilovolt), grade: electric, standard: indian standard, certification: isi(indian standards institute) mark | 5.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 22.2 ¦ 1.1 kV, 900mm wide, electric grade floor rubber mat (in pieces of length not less than 2 mtrs.) conforming to relevant IS. ISI mark shall be there on rubber mat. | floor rubber mat |  | width: 900mm, length: not less than 2 mtrs. | voltage: 1.1 kv(kilovolt), grade: electric, standard: indian standard, certification: isi(indian standards institute) mark | 60.0 | m
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 22.3 ¦ Rubber Hand Gloves of 11 KV grade. | rubber hand gloves |  |  | voltage: 11 kv(kilovolt), grade: - | 4.0 | Pair
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 22.4 ¦ Rubber Hand Gloves of 415V grade. | rubber hand gloves |  |  | voltage: 415 v(volt), grade: - | 6.0 | Pair
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 22.5 ¦ First aid box of GI, 18 SWG sheet with necessary items. | first aid box |  | sheet thickness: 18 swg(standard wire gauge) | material: gi(galvanized iron), included: necessary items | 8.0 | No.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 22.6 ¦ DANGER PLATE (As per IS 2551) | danger plate |  |  | standard: indian standard 2551 | 30.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 22.7 ¦ CABLE ROUTE MARKER | cable route marker |  |  |  | 200.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 22.8 ¦ CO2 fire extinguishers 5kg with fixing bracket | co2 fire extinguisher |  | capacity: 5kg | included: fixing bracket | 18.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 22.9 ¦ ABC Dry chemical powder (DCP) fire extinguishers 5kg with fixing bracket | abc dry chemical powder fire extinguisher | dcp fire extinguisher | capacity: 5kg | included: fixing bracket | 18.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 21.1 ¦ Shock treatment chart | shock treatment chart |  |  |  | 40.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 21.11 ¦ Fire buckets (4nos.) with sand & M.S. Hooks / stand | fire bucket |  | quantity per set: 4nos. | included: sand & ms(mild steel) hooks / stand | 10.0 | Set
['INST', 'CONTROL & INSTRUMENTATION WORKS', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 1 ¦ FIRE DETECTION SYSTEM | fire detection system
['INST', 'CONTROL & INSTRUMENTATION WORKS', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 1.1 ¦ Presssure Transmitter & solenoid valve for Deluge valve | pressure transmitter and solenoid valve |  |  | application: deluge valve
['INST', 'CONTROL & INSTRUMENTATION WORKS', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 1.1.1 ¦ Supply of pressure transmitter (24 V DC) Exd type, 2 nos. with each DV (1 nos. for air line & 1 no. for water line) Description:IP-66, EExia IIA IIB, T3 (ATEX /CENELEC),CCOE 4 ~ 20 mA +HART, Range: 0~7kg/cm2 (11 nos.) & 0~15kg/cm2 (11 Nos ), Acuracy:0.075% of span. Rangeability – 1:100 , service: water & Air, SS316 cable gland. refer tender specification for detail. | pressure transmitter |  | range: 0~7kg/cm2 (11 nos.) & 0~15kg/cm2 (11 Nos ) | voltage: 24 v dc(direct current), type: exd, included: 2 nos. with each dv(deluge valve) (1 nos. for air line & 1 no. for water line), protection: ip-66, certification: eexia iia iib, t3 (atex /cenelec), ccoe, output: 4 ~ 20 ma +hart, accuracy: 0.075% of span, rangeability: 1:100, service: water & air, cable gland: ss316(stainless steel 316) | 22.0 | Nos.
['INST', 'CONTROL & INSTRUMENTATION WORKS', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 1.1.2 ¦ Supply flameproof solenoid valve (24V DC) suitable for Hazardous area zone-1, IIA/IIB T3, 1/2" NPT connection as per specification (9 nos for DV+2 Nos spares) | solenoid valve |  | connection: 1/2" npt(national pipe thread) | type: flameproof, voltage: 24v dc(direct current), suitable for: hazardous area zone-1, certification: iia/iib t3, included: 9 nos for dv(deluge valve)+2 nos spares | 9.0 | Nos.
['INST', 'CONTROL & INSTRUMENTATION WORKS', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 1.2 ¦ ESD PUSH BUTTON STATION | esd push button station
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 1.2.1 ¦ Supply of ESD Push button station with all accessories like cables , glanding & termination etc. mounted on Exd JBs located at different areas - a)Filling Shed, b)Pump house, c)LPG Bullets, d)TLD , e)Central Monitoring Hub f) plant manager room g) Filled Cylinder Area | esd push button station |  |  | accessories: cables, glanding, termination, mounting: exd (explosion proof) junction boxes, location: filling shed, pump house, lpg bullets, tld, central monitoring hub, plant manager room, filled cylinder area | 7.0 | Nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 1.3.1 ¦ Supply of electric siren at pump house/PMCC/Security room. Scope also includes: a) supply of necessory equipments/component/ accessories including siren controller required to complete system as per tender document. b) supply of any support required for siren & it's panel | electric siren |  |  | location: pump house, pmcc (power and motor control center), security room, accessories: siren controller, necessary equipment, components, support for siren and panel, as per tender document | 1.0 | Nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 1.3.2 ¦ Supply of Hand operated siren for the location of LPG pump house, security room, TLD bay & Empty cum filling shed. | hand operated siren |  |  | location: lpg pump house, security room, tld bay, empty cum filling shed | 4.0 | Nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 1.4.1 ¦ Supply of Fire Alarm System panel along with electronic card and other electrical accessories. All hardware and software to integrate all devices for successful functioning of the system included in the scope. All Fire Alarm Panel Panels shall be integrated through MODBUS / PROFIBUS / OEM RECOMMENDED SERIAL LINK COMMUNICATION. Common Fault Alarm shall be generated in Fire Alarm Panel to hook up through hardware cable to PLC / ESD located at CR. Associated electrical or electronics circuit connecting with the field devices of detection system requires high availability and reliability in confirmation to tender drawings and specification. Fire alarm system shall be UL listed. Fire Detection System Panel shall include below mentioned items: 1. Intelligent Analogue Addressable type non-ex-proof type Manual Call point (06 Nos), to be hooked up with Fire Alarm Panel at CMH, 2. Intelligent Analogue Addressable type Flame proof type Manual Call point (07 Nos), to be hooked up with Fire Alarm Panel at CMH, 3. Isolator Modules (03 Nos), to be hooked up with Fire Alarm Panel at CMH. 4. Control Modules (05 Nos), to be hooked up with Fire Alarm Panel at CMH. 5. Intelligent Analogue Addressable type Multi Criteria Detector (05 Nos) to be hooked up in Fire Alarm Panel of CMH). 6. Response Indicators (05 Nos), 7 Audio Visual Fire Alarm Siren (05 Nos). Above items shall be read in conjuction with Fire Detection drawing & ILSD drawing. | fire alarm system panel |  |  | accessories: electronic card, electrical accessories, hardware, software, integration: modbus, profibus, oem recommended serial link communication, common fault alarm, connection: plc (programmable logic controller), esd (emergency shutdown device) at cr (control room), standard: ul (underwriters laboratories) listed, includes: manual call points (non-ex-proof and flame proof), isolator modules, control modules, multi criteria detector, response indicators, audio visual fire alarm siren, reference: fire detection drawing, ilsd (integrated leak detection system) drawing | 1.0 | Lot
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 1.4.2 ¦ SUPPLY of DV Operation Panel integrating with PLC and with PB (with operation indicating lamp for "DV on Fire" and "DV Operated") for opening of Deluge Valve (09 nos+ 1 spare) . All hardware as required and software included. (1 No. DV panel shall be installed at fire water pump house, 1 No. at main gate security room.) | dv operation panel |  |  | integration: plc (programmable logic controller), pb (push button), indicating lamp: dv on fire, dv operated, for: deluge valve (9 nos + 1 spare), installation: fire water pump house, main gate security room, hardware and software included | 2.0 | Lot
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 2.1.1 ¦ Supply of flameproof/EX -proof , IP-66 IR gas detector suitable to hazardous area Zone-1, IIA/B T3 . Canopy & any otther acessories required is included in scope | ir gas detector |  |  | type: flameproof, ex-proof (explosion proof), ingress protection: ip-66, area suitability: hazardous area zone-1, iia/b t3, accessories: canopy, other accessories included | 28.0 | Nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 2.2.1 ¦ Gas monitoring system: Supply of Dual redundant (Parallel/ Hot Standby) wall mounted Programmable Logic Controller (Process PLC) along with PLC Panels, Input Output modules, Power supply units, Relays with base, barriers, TBs, Dual Ethernet ports per processors, Serial Interface Modules, wirings, glands, plugs, other modules/ hardwares required for interfacing all the required field and Central Monitoring Hub (CMH) equipments including spare requirements, licenses, tags, softwares etc complete as per specification and tender document. AI -28 Nos DI -12 Nos DO -04 Nos Serial Interface Ports: 04 Additional 20% spare (min 1) qty to be supplied over the above mentioned I/O quantity.Size of the PLC panel shall be optimized mode to accomodate all the signals in wall mounted panel only. Gas monitoring system at Central Monitoring Hub (CMH) as per tender documents. the scope also includes supply of all componennt, accessories required for complete the system and customization of reports as detailed in specifications and tender documents. | gas monitoring system |  | ai: 28 nos, di: 12 nos, do: 4 nos, serial interface ports: 4 | redundancy: dual redundant (parallel/hot standby), mounting: wall mounted, controller: programmable logic controller (plc), accessories: plc panels, input output modules, power supply units, relays with base, barriers, tbs (terminal blocks), dual ethernet ports per processor, serial interface modules, wirings, glands, plugs, other modules/hardwares, spare requirements, licenses, tags, software, optimized plc panel size, customization of reports, as per specification and tender document | 1.0 | Lot
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 2.2.2 ¦ Supply of weather proof Repeater panel at security room alongwith hooter & indication of Fault & LEL Alarm as per tender secifications. Panel to be hooked up with GMS at CMH. | weather proof repeater panel |  |  | location: security room, accessories: hooter, indication of fault & lel (lower explosive limit) alarm, connection: gms (gas monitoring system) at cmh (central monitoring hub), as per tender specifications | 1.0 | Nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 2.2.3 ¦ Supply of Flameproof/Ex-Proof cum weatherproof Repeater Panel alongwith Flameproof/Ex-proof Hooter & indication of Fault & LEL Alarm as per tender secifications. same to be hooked up with GMS at CR , All cabling & hardware included (Common repeater panel 1 no. in LPG Pump House room for TLD, LPG P/H & MSV's area gas detectors; 1 no for Filling shed & filled cylinder shed. ) | flameproof cum weatherproof repeater panel |  |  | accessories: flameproof/ex-proof hooter, indication of fault & lel (lower explosive limit) alarm, connection: gms (gas monitoring system) at cr (control room), cabling & hardware included, installation: lpg pump house room for tld, lpg p/h & msv's area gas detectors, filling shed & filled cylinder shed, as per tender specifications | 2.0 | Nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 2.2.4 ¦ Supply of sample gas cylinder for gas detectors sufficient to calibrate min. 21 nos. Gas detectors at a time. All asscessories needed for calibration are included in scope | sample gas cylinder for gas detectors |  | calibration capacity: minimum 21 gas detectors at a time | accessories: all needed for calibration included | 4.0 | Lot
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 3.1.1 ¦ The followings shall be considered for above - i) Servo Gauge with Display , Accuracy +-1mm LAB conditions,Density Measurement - 1 no. for each MSV | servo gauge with display |  |  | accuracy: ±1mm lab conditions, density measurement: included, quantity per msv: 1 | 3.0 | Nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 3.1.2 ¦ ii) Pressure Tx with 2 valve manifold for vapour pressure measurement Range 0 -15 Kg/CM2 - 2 nos. for each MSV | pressure transmitter with 2 valve manifold |  |  | measurement: vapour pressure, range: 0-15 kg/cm2, quantity per msv: 2 | 3.0 | Nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 3.1.3 ¦ iii) Radar Gauge with Display and - +/-1mm LAB condition with Display (Smart typeTank Side Indicator),Temperature sensor interface, Suitable for 6" Sch 10 Stilling pipe,1 Nos. SIL3 Relay Output & Analog Output - 1 no. for each MSV | radar gauge with display |  | stilling pipe suitability: 6" sch 10 | accuracy: ±1mm lab condition, display: smart type tank side indicator, temperature sensor interface: included, relay output: sil3, analog output: included, quantity per msv: 1 | 3.0 | Nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 3.1.4 ¦ iv) Vibration Fork type level switch with HH/LL set points - 1no. For each MSV | vibration fork type level switch |  |  | set points: hh/ll (high high/low low), quantity per msv: 1 | 3.0 | Nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 3.1.5 ¦ v) Smart type tank side indicator for Radar gauge at LPG pump house & interfacing with Radar gauge & Process PLC /safety PLC - 1 no. for each MSV | smart type tank side indicator for radar gauge |  |  | location: lpg pump house, interfacing: radar gauge, process plc (programmable logic controller), safety plc, quantity per msv: 1 | 3.0 | Nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 3.1.6 ¦ vi) Smart type tank side indicator for servo Gauge at LPG pump house & interfacing with servo gauge & Process PLC /safety PLC 1 no. for each MSV | smart type tank side indicator for servo gauge |  |  | location: lpg pump house, interfacing: servo gauge, process plc (programmable logic controller), safety plc, quantity per msv: 1 | 3.0 | Nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 3.1.7 ¦ vii) local indicator for pressure transmitter at LPG pump house - 1 no. for each MSV | local indicator for pressure transmitter |  |  | location: lpg pump house, quantity per msv: 1 | 6.0 | Nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 3.1.8 ¦ viii) Interface (Radar & Servo) | interface for radar and servo |  |  |  | 6.0 | Nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 3.1.9 ¦ ix) 9 Point temperature probe ( to be interface with Radar & Servo) | 9 point temperature probe |  | points: 9 | interface: radar & servo | 3.0 | Nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 2010-01-03 00:00:00 ¦ x) Redundant CIU/FCU with all interfacing , 2 nos of Modbus ports for Process PLC and 2 nos of Modbus ports for TFMS connectivity as required - 1 set | redundant ciu/fcu |  | modbus ports for process plc: 2, modbus ports for tfms: 2 | interfacing: all required, set: 1 | 1.0 | Set
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 2011-01-03 00:00:00 ¦ xii) Verification pin set | verification pin set |  |  |  | 20.0 | Nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 2012-01-03 00:00:00 ¦ xiii)TFMS Software supplied by bidder shall be same make as radar manufacturer and compatible with servo gauges. Licence shall be 12 nos min. | tfms software |  | licence: minimum 12 nos | make: same as radar manufacturer, compatibility: servo gauges | 1.0 | Lot
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 2013-01-03 00:00:00 ¦ xiv) Junction Boxes - | junction boxes |  |  |  | 4.0 | Nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 2014-01-03 00:00:00 ¦ xv) PDB Panel for TFMS. | pdb panel for tfms |  |  |  | 2.0 | Nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 2015-01-03 00:00:00 ¦ xvi) Communication cable, RTD cable, Power cable for TFMS | communication cable, rtd (resistance temperature detector) cable, power cable for tfms |  |  |  | 1.0 | Lot
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 2016-01-03 00:00:00 ¦ xvIi) Audio-Visual Annunciation Panel for annunciation at LPG Pump House, integrated with all Level Switches of MSVs (Single common Panel for all level switches) | audio-visual annunciation panel |  |  | location: lpg pump house, integration: all level switches of msvs (motorised shutoff valves), panel type: single common panel for all level switches | 1.0 | Nos
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 3.2 ¦ Tank Farm Management Servers - Commodity Grade, working on redundant (Primary and Secondary) hot standby mode with software, including backlit LED Monitor, key board and mouse. Supply , Installation, erection and commissioning of Operator Interface Console Computer (OIC) with 22" colour LED monitor, standard keyboard etc. complete as per specifications at Central Monitoring Hub (CMH). | tank farm management servers |  | monitor: 22" colour led | grade: commodity, redundancy: primary and secondary hot standby, software: included, accessories: backlit led monitor, keyboard, mouse, supply, installation, erection, commissioning: included, operator interface console computer (oic): included, location: central monitoring hub (cmh) | 1.0 | Lot
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 3.3 ¦ Other items for above - FLP Double compression type SS cable glands - As required , Adaptor Plate for Radar Gauge 4"/6",300# (SS316) for Radar tags - 1 no , Adaptor Plate for Temperature Probes 2",300# (SS316) - 4 nos , Fabricated Adaptor Chamber for Servo Gauge 2"X 4" X 6"300# (MOC CS) with pressure gauge, needle valve & pressure relief valve for Servo Tags , Studs as per SA 320 Gr. L7 & Bolts Nuts as per SA 194 Gr. 7 , Gaskets ( 6",4", 2") Spiral wound Metallic AISI 304, asbestos filled as per API 601 , fabricated cable for CIU & PC - As required ,fabrication of manifold for ionstllation of local indicator (radar /servo)- as required, Cables for communication of Servo , Radar / Servo / field Instruments to CIU (FRLS Cable for data communicatin) - As required , All software and Hardware shall be included as required , Bidder shall consider Process PLC & Tank Gauging system interface on redundant Modbus Communication , Any other item to achieve complete system to successful functioning and integration with other system as required are included. | other items for above |  |  | flp (flameproof) double compression type ss (stainless steel) cable glands: as required, adaptor plate for radar gauge: 4"/6", 300# (ss316), quantity: 1 no, adaptor plate for temperature probes: 2", 300# (ss316), quantity: 4 nos, fabricated adaptor chamber for servo gauge: 2"x4"x6" 300# (moc cs(carbon steel)), with pressure gauge, needle valve & pressure relief valve for servo tags, studs: sa 320 gr. l7, bolts nuts: sa 194 gr. 7, gaskets: (6",4",2") spiral wound metallic aisi 304, asbestos filled as per api 601, fabricated cable for ciu & pc: as required, fabrication of manifold for installation of local indicator (radar or servo): as required, cables for communication of servo, radar or servo or field instruments to ciu (frls (fire retardant low smoke) cable for data communication): as required, all software and hardware: included as required, process plc (programmable logic controller) & tank gauging system interface: redundant modbus communication, any other item: to achieve complete system to successful functioning and integration with other system as required | 1.0 | Lot
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 4.1.1 ¦ Supply of Flameproof cum weather proof smart type Grounding unit with one green indicating lamp and dual output for safety earthing of tank trucks, suitable for giving safety interlocking signal to PLC all complete as per specifications | smart type grounding unit |  |  | protection: flameproof, weatherproof, indicator: one green indicating lamp, output: dual, application: safety earthing of tank trucks, interlocking signal: plc (programmable logic controller), completeness: all as per specifications | 2.0 | Nos.
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 4.2.1 ¦ Supply of Dual redundant (Parallel/ Hot Standby) Programmable Logic Controller (Process PLC) along with PLC Panels, Marshalling Panels, Input Output modules, Power supply units, Relays with base, barriers, TBs, Dual Ethernet ports per processors, Serial Interface Modules, HMI console, wirings, glands, plugs, other modules/ hardwares required for interfacing all the required field and Central Monitoring Hub (CMH) equipments including spare requirements, licenses, tags, GUI, softwares etc complete as per specification and tender document. AI -25 Nos DI -96 Nos DO -80 Nos Serial Interface Ports: 28 Minimum 20% spare IO to be supplied as per tender specification. Count of PLC panel shall be optimized to accomodate all the signals in one panel only. | programmable logic controller | plc | ai: 25 nos, di: 96 nos, do: 80 nos, serial interface ports: 28, spare io: minimum 20% | redundancy: dual redundant (parallel/hot standby), panels: plc panels, marshalling panels, modules: input output, power supply units, relays with base, barriers, tbs (terminal blocks), dual ethernet ports per processor, serial interface modules, hmi (human machine interface) console, wirings, glands, plugs, other modules/hardwares: required for interfacing all required field and cmh (central monitoring hub) equipments, spare requirements: included, licenses: included, tags: included, gui: included, softwares: included, specification: as per tender document, plc panel count: optimized to accommodate all signals in one panel only | 1.0 | Lot