## Sheet1
0 | 1 | 2 | 3
1 | H POLE STRUCTURE
1.1 | Design and supply of H-pole Structure for 11 KV Incoming Power Supply with Gang operated isolator, D.O. fuse with base, lightning arrestors, Insulator, earthing, construction of earth Pits, fencing, gate, gravel laying, padlocking, signages including all civil works for 11 KV Supply. The design shall be in line with Electricity board guidelines. | Set | 1
2 | 11 KV indoor VCB Panel
2.1 | 11 KV, 630 A, VCB panel indoor type comprising of metering and protection system including numerical relay, auxiliary relay, CTs, PTs , indication lamp, switches along with Weather proof double compression Ni plated brass cable gland and crimping type cable lugs for all incoming and outgoing cables and as per specfication.. | No. | 1
3 | POWER TRANSFORMER AND LIGHTING TRANSFORMER
3.1 | 500 KVA, 11KV/433V, Dyn11, AN type with off load tap changer power transformer complete with all accessories as per attached specifications & DS. | No. | 1
3.2 | 200KVA, 415V/433V, Dyn1, natural air cooled Dry type Lighting transformer as per attached specifications & DS. | No. | 1
4 | MV/LV SWITCH BOARDS/ PANELS
4.1 | PMCC: 415V, 3phase, 4 wire, 50 Hz, 800A, 50 KA for 1second, double front fully draw out type PMCC comprising of ACBs, CTs/PTs, relays, indicating lamps etc. as per attached SLDs, specifications & DS. | No. | 1
4.2 | MLDB: 415V, 3phase, 4 wire, 50 Hz, 400A, 25KA for 1second MLDB including as per attached SLD, specifications & DS. | No. | 1
4.3 | Fire water MCC: 415V, 3phase, 4 wire, 50 Hz, 400A, 50KA for 1second MCC including as per attached SLD, specifications & DS. | No. | 1
4.4 | CAPACITOR PANEL : 415V, 3Ph-N, 50Hz, 50KA for 1second, 250KVAR capacitor panel with capacitors 2X75, 1X50, 2X25 KVAR) and APFC relay, protections, filters etc. as per attached SLD, specifications & DS including weather proof double compression Ni plated brass cable glands and lugs for all incoming and outgoing feeders. | No. | 1
5 | LDB and SUB-LDB
5.1 | LDB / LP, W eatherproof, IP 65, incomer 63A, 3 Phase, 4 wire, 3 Way LDB, 10kA for 1 sec with RCBO | No. | 1
5.2 | LDB / LP, W eatherproof, IP 65, incomer 63A, 3 Phase, 4 wire, 6 Way LDB, 10kA for 1 sec with RCBO | No. | 1
5.3 | LDB / LP, Outdoor type, Flame proof (FLP) Type, IP class suitable for FLP and minimum protection shall be IP-65, incomer 63A, 3 Phase, 4 wire, 3 Way LDB, 10kA for 1 sec with RCBO | No. | 5
5.4 | LDB / LP, Outdoor type, Flame proof (FLP) Type, IP class suitable for FLP and minimum protection shall be IP-65 , incomer 63A, 3 Phase, 4 wire, 6 Way LDB, 10kA for 1 sec with RCBO | No. | 1
5.5 | UPS DB - 230V, 50Hz,Outdoor type, Flame proof (FLP) Type, IP class suitable for FLP and minimum protection shall be IP-65, incomer 63A, 3 Phase, 4 wire, 3 Way LDB, 10kA for 1 sec with RCBO | No. | 1
5.6 | Feeder Pillar for street Lighting . 415V, 3Ph, 50Hz, Flame proof (IP class suitable for FLP and minimum protection shall be IP-65) sheet steel enclosure column/structural mounted, with photovoltic cell based control with A/M selector switch, start/stop PB, indicating lamps etc. with 3mm thick FRP canopy and side cover of the following incoming and outgoing feeders: i) 1no.-Incomer 63A, 3 phase RCBO 30 mA ii) 3nos.-O/G 16A TPN MCB | No. | 1
5.7 | PDB at outdoor location . 415V, 3Ph, 50Hz, W eatherproof and Flame proof (IP class suitable for FLP and minimum protection shall be IP-65) sheet steel enclosure column/structural mounted, start/stop PB, indicating lamps etc. with 3mm thick FRP canopy and side cover of the following incoming and outgoing feeders: i) 1no.-Incomer 100A TPN MCCB ii) 5nos.-O/G 32A TPN MCCB One outgoing shall be provided with photovoltic cell based control with A/M selector switch, start/stop PB, indicating lamps etc to feed the street light. | No. | 1
6 | BATTERY CHARGER WITH BATTERY & DC DB
6.1 | 110V, 10A BATTERY CHARGER consisting of dual float cum boost charger and Ni-Cd type battery (43AH) with two hour back up capacity as per attached specifications & DS. | No. | 1
6.2 | DC DISTRIBUTION BOARD: 110V DC, 2 wire 63A DC Distribution Board fed by duel float cum boost charger as per attached SLD, specifications & DS. Incomer: 63A DP MCB Outgoing: 15nos. 16A DP MCB | No. | 1
7 | LIGHTING FIXTURES & ACCESSORIES
7.1 | Supply of Flameproof lighting fixtures, Lamps & Accessories as per attached specification. (All Lighting fixtures shall be provided with required no. of FLP double compression stainless steel cable glands and FLP stopping plug and control gear boxes etc. All fixtures shall have inbuilt JBs for loop in loop out facility of 3Cx2.5 sqmm Cu lighting cables)
| 230 Volt AC, 40W Well glass Flameproof Ex'd',LED lighting fixtures and all other accessories | Nos. | 135
7.2 | Supply of weatherproof lighting fixtures, Lamps & Accessories as per attached specification. (All Lighting fixtures shall be provided with required no. of double compression stainless steel cable glands and stopping plug. All control gear boxes shall be provided with 3mm thick FRP canopy with side cover. .All fixtures shall have inbuilt JBs for loop in loop out facility of 3Cx2.5 sqmm Cu lighting cables)
| 230 Volt AC, 40W Well glass weatherproof ,LED lighting fixtures and all other accessories | Nos. | 22
8 | JUNCTION BOX
8.1 | 240 Volt AC, 16 A, Cast Aluminium Flameproof Ex'd' (Zone-1, IIA / IIB) 4-way, 125 mm (minimum) internal dimensions junction box with terminals block suitable for 2.5 sq.mm along with flameproof double compression Ni plated brass cables glands for all incoming and outgoing cables,PVC shroud and other accessories. | Nos. | 45
8.2 | 240 Volt AC, 16 A, Cast Aluminium weatherproof 4-way, 125 mm (minimum) internal dimensions junction box with terminals block suitable for 2.5 sq.mm along with weatherproof double compression Ni plated brass cables glands for all incoming and outgoing cables,PVC shroud and other accessories. | Nos. | 18
8.3 | JUNCTION BOXES FOR PUMP MOTOR (WEATHER PROOF, FLAME PROOF): Design, Supply, Installation, Testing and Commissionong of following 415V, 3P, Industrial type, W eatherproof, Flame proof “Ex-d” (suitable for hazardous area of gas group IIA/IIB, temperature class T3 and Zone-1), IP 65 suitable for Wall / Column / Structure mounting Including cabling from JB to terminal box for Star-Delta pump motor having different terminal for star and delta connection. All JBs shall be made up of cast Aluminium alloy (LM6 grade) with Canopy of 14 gauge CRCA sheet with side cover. JBs shall confirm to specification/data sheet of tender document. Junction Boxes shall be complete with busbar of suitable rating, support insulator, suitable for 2 nos. of 1RX 3.5 C X 150 Sqmm of Incoming cable size and 2 nos. of 1RX 3.5 C X 95 Sqmm of outgoing cable size XLPE insulated, extruded PVC inner & outer sheathed, FRLS, Armoured cables & shall be supplied along with FLP type double compression, Ni plated brass cable glands, lugs & plugs. However, exact cable sizes shall be indicated during drawing approval only. | Nos. | 1
9 | RECEPTACLES
9.1 | Supply of flameproof Interlocking type switch sockets and plugs of following ratings as per attached specifications. All switch sockets shall be provided with 3mm thick FRP canopy with side cover and required no. of FLP double compression stainless steel cable glands and FLP stopping plug.
| i) 415V, 5-pin, 63A flame proof switch socket and plug | Nos. | 4
| ii) 240V, 3-pin, 16A/5A flame proof switch socket and plug | Nos. | 6
9.2 | Supply of weatherproof Interlocking type switch sockets and plugs of following ratings as per attached specifications. All switch sockets shall be provided with 3mm thick FRP canopy with side cover and required no. of double compression stainless steel cable glands and stopping plug.
| i) 415V, 5-pin, 63A weatherproof switch socket and plug | Nos. | 2
| ii) 240V, 3-pin, 16A/5A weatherproof switch socket and plug | Nos. | 2
10 | RIGID/ FLEXIBLE CONDUIT
Supply of PVC rigid conduit of min. 2mm thick wall, heavy duty type as per IS (with bends, reducers, couplers etc.) of following sizes:-
10.1 | 25 mm Dia. PVC Rigid Conduit | m | 50
10.2 | 50 mm Dia. PVC Rigid Conduit | m | 150
10.3 | 75 mm Dia. PVC Rigid Conduit | m | 50
Supply of following PVC flexible conduit of min. 2mm thick wall, heavy duty type & as per IS: 2509.
10.4 | 25 mm Dia PVC Flexible Conduit | m | 425
11 | Lighting Cable
| 0.6/1 kV grade 3C X 2.5 Sqmm Cu XLPE insulated FRLS PVC sheathed Lighting Cable | m | 1800
12 | LIGHTING POLES
| Supply of 9.5 Mtr lighting pole (polygonal type) for base mounting complete with all accessories like MCB & terminal block, JB (as applicable), Zinc passivated hardware for fixtures support & pole support, cable protection pipe with earthing rod/ wire as applicable, clamps, nuts, bolts, etc. | Nos. | 6
13 | HIGH MAST LIGHTING TOWER
| Civil & Structural design, engineering & supply of hot dip galvanised High Mast lighting tower (30 m height) including all accessories for High Mast like 24 nos. of High mast lantern Carraige, 16 nos. of 350 watt LED fixture with lamp, head frame, stainless steel rope, double drum winch, Flameproof junction boxes, Flameproof plugs and sockets, Flameproof feeder pillar, galvanised lantern carrier arrangement, cables and cable accessories control panel for feeder pillar etc. as per specification, data sheet and direction of Engineer- in-charge ingincluding supply of commissioning and 2 years O&M spares. | Nos. | 4
14 | SUPPLY OF HT/ LT CABLES AS PER ENCLOSED SPECIFICATION
11 KV(UE) Grade Cables as per typical specifications ; XLPE insulated; PVC Sheathed; Armoured Aluminium Conductor Cables of Following Sizes As Per Is:1554 (Part-I), IS 7098 Part I & IS 1225-Latest Version and Sealed properly with Pvc Caps of following size:-
14.1 | 3C x 240 sqmm (AL) | m | 250
1.1KV(E) XLPE insulated, FRLS, PVC sheathed aluminium/copper conductor, 1.1 kV grade armoured cable conforming to IS:7098, as per approved make AS PER ENCLOSED SPECIFICATIONS
14.2 | 1C x 400, Sqmm XLPE AL | m | 1010
14.3 | 3.5C x 150, Sqmm XLPE AL | m | 100
14.4 | 3.5C x 95, Sqmm XLPE AL | m | 500
14.5 | 3.5C X 50, Sqmm XLPE AL | m | 3000
14.6 | 4C X 25, Sqmm XLPE AL | m | 6800
14.7 | 4C X 16, Sqmm XLPE AL | m | 600
14.8 | 4C X 10, Sqmm XLPE AL | m | 100
14.9 | 4C X 6, Sqmm XLPE AL | m | 8000
14.1 | 4C X 4, Sqmm XLPE AL | m | 3100
14.11 | 4C X 2.5, Sqmm XLPE AL | m | 2200
14.12 | 3C X 6, Sqmm XLPE AL | m | 400
14.13 | 3C X 2.5, Sqmm XLPE AL | m | 100
14.14 | 2C X 4, Sqmm XLPE AL | m | 200
14.15 | 2C X 16, Sqmm XLPE AL | m | 900
1.1KV(E) armoured XLPE, FRLS Control Cable of following size:-
14.16 | 7C x 2.5 SQMM CU | m | 27000
14.17 | 3C x 2.5 SQMM CU | m | 800
15 | CABLE GLANDS
Supply of Flameproof double compression stainless steel cable gland suitable for following XLPE , FRLS cable sizes & as per relevant IS for hazardous area.
15.1 | 3.5C x 150, Sqmm XLPE AL | Nos. | 5
15.2 | 3.5C x 95, Sqmm XLPE AL | Nos. | 5
15.3 | 3.5C X 50, Sqmm XLPE AL | Nos. | 20
15.4 | 4C X 25, Sqmm XLPE AL | Nos. | 50
15.5 | 4C X 16, Sqmm XLPE AL | Nos. | 50
15.6 | 4C X 10, Sqmm XLPE AL | Nos. | 4
15.7 | 4C X 6, Sqmm XLPE AL | Nos. | 60
15.8 | 4C X 4, Sqmm XLPE AL | Nos. | 15
15.9 | 4C X 2.5, Sqmm XLPE AL | Nos. | 16
15.1 | 3C X 2.5, Sqmm XLPE AL | Nos. | 5
15.11 | 3C X 6, Sqmm XLPE AL | Nos. | 10
15.12 | 2C X 4, Sqmm XLPE AL | Nos. | 4
15.13 | 2C X 16, Sqmm XLPE AL | Nos. | 4
15.14 | 7C x 2.5 SQMM CU | Nos. | 70
15.15 | 3C x 2.5 SQMM CU | Nos. | 10
Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use.
15.16 | 1C x 400, Sqmm XLPE AL | Nos. | 60
15.17 | 3.5C x 150, Sqmm XLPE AL | Nos. | 6
15.18 | 3.5C x 95, Sqmm XLPE AL | Nos. | 5
15.19 | 3.5C X 50, Sqmm XLPE AL | Nos. | 22
15.2 | 4C X 25, Sqmm XLPE AL | Nos. | 50
15.21 | 4C X 16, Sqmm XLPE AL | Nos. | 50
15.22 | 4C X 10, Sqmm XLPE AL | Nos. | 4
15.23 | 4C X 6, Sqmm XLPE AL | Nos. | 60
15.24 | 4C X 4, Sqmm XLPE AL | Nos. | 15
15.25 | 4C X 2.5, Sqmm XLPE AL | Nos. | 16
15.26 | 3C X 2.5, Sqmm XLPE AL | Nos. | 5
15.27 | 3C X 6, Sqmm XLPE AL | Nos. | 10
15.28 | 2C X 4, Sqmm XLPE AL | Nos. | 4
15.29 | 2C X 16, Sqmm XLPE AL | Nos. | 4
15.3 | 7C x 2.5 SQMM CU | Nos. | 70
15.31 | 3C x 2.5 SQMM CU | Nos. | 10
END TERMINATION KIT
15.32 | Supply of Raychem make heat shrinkable end termination kit suitable for 11 KV (UE) XLPE, FRLS cables of following sizes.
15.33 | 3C x 240 sqmm (AL) ( suitable for outdoor purpose) | Nos. | 1
15.34 | 3C x 240 sqmm (AL) ( suitable for indoor purpose) | Nos. | 3
16 | CABLE LUGS
Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:-
16.1 | 3.5C x 150, Sqmm XLPE AL | Nos. | 25
16.2 | 3.5C x 95, Sqmm XLPE AL | Nos. | 20
16.3 | 3.5C X 50, Sqmm XLPE AL | Nos. | 80
16.4 | 4C X 25, Sqmm XLPE AL | Nos. | 200
16.5 | 4C X 16, Sqmm XLPE AL | Nos. | 200
16.6 | 4C X 10, Sqmm XLPE AL | Nos. | 8
16.7 | 4C X 6, Sqmm XLPE AL | Nos. | 240
16.8 | 4C X 4, Sqmm XLPE AL | Nos. | 60
16.8 | 4C X 2.5, Sqmm XLPE AL | Nos. | 64
16.9 | 3C X 2.5, Sqmm XLPE AL | Nos. | 12
16.1 | 3C X 6, Sqmm XLPE AL | Nos. | 15
16.11 | 2C X 4, Sqmm XLPE AL | Nos. | 8
16.12 | 2C X 16, Sqmm XLPE AL | Nos. | 16
16.13 | 7C x 2.5 SQMM CU | Nos. | 500
16.14 | 3C x 2.5 SQMM CU | Nos. | 100
Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:-
16.15 | 1C x 400, Sqmm XLPE AL | Nos. | 60
16.16 | 3.5C x 150, Sqmm XLPE AL | Nos. | 25
16.17 | 3.5C x 95, Sqmm XLPE AL | Nos. | 20
16.18 | 3.5C X 50, Sqmm XLPE AL | Nos. | 80
16.19 | 4C X 25, Sqmm XLPE AL | Nos. | 200
16.2 | 4C X 16, Sqmm XLPE AL | Nos. | 200
16.21 | 4C X 10, Sqmm XLPE AL | Nos. | 8
16.22 | 4C X 6, Sqmm XLPE AL | Nos. | 240
16.23 | 4C X 4, Sqmm XLPE AL | Nos. | 60
16.24 | 4C X 2.5, Sqmm XLPE AL | Nos. | 64
16.25 | 3C X 2.5, Sqmm XLPE AL | Nos. | 12
16.26 | 3C X 6, Sqmm XLPE AL | Nos. | 15
16.27 | 2C X 4, Sqmm XLPE AL | Nos. | 8
16.28 | 2C X 16, Sqmm XLPE AL | Nos. | 16
16.29 | 7C x 2.5 SQMM CU | Nos. | 500
16.3 | 3C x 2.5 SQMM CU | Nos. | 100
17 | Cable Trays
17.1 | Ladder type GI cable tray (100mmx2mm, 3 Meter length) with minimum hot dip zinc coating 75 micron with accessories like coupler plates,bends, Stainless steels hardwares like nuts & bolts , bends, washers etc and as per IS & ES:8161.
a. | 750mm Wide | m | 40
b. | 600mm Wide | m | 300
c. | 300mm Wide | m | 200
d. | 150mm Wide | m | 228
e. | 50mm Wide | m | 100
17.2 | 90 deg Horizontal Bend Ladder type (shall be decided as per detail engineering)
a. | 750mm Wide | Nos. | 4
b. | 600mm Wide | Nos. | 16
c. | 300mm Wide | Nos. | 8
d. | 150mm Wide | Nos. | 5
17.3 | TEE Connection Ladder type (shall be decided as per detail engineering)
a. | 600mm Wide | Nos. | 16
b. | 300mm Wide | Nos. | 5
17.4 | 90 deg Vertical Bend (inside) Ladder (shall be decided as per detail engineering)
a. | 600mm Wide | Nos. | 10
b. | 300mm Wide | Nos. | 2
17.5 | 90 deg Vertical Bend (outside) Perforated (shall be decided as per detail engineering)
a. | 600mm Wide | Nos. | 10
b. | 300mm Wide | Nos. | 2
17.6 | G.I. Perforated Cable Trays , 100 mm deep, 3 mm thick G.I. perforated cable trays (Min. coating 100 microns of zinc) with bend, reducer, coupler plate and other hardware.
a. | 750mm Wide | m | 10
b. | 600mm Wide | m | 550
c. | 300mm Wide | m | 175
d. | 150mm Wide | m | 350
e. | 50mm Wide | m | 100
17.7 | 90 deg Horizontal Bend Perforated (shall be decided as per detail engineering)
a. | 750mm Wide | Nos. | 3
b. | 600mm Wide | Nos. | 20
c. | 300mm Wide | Nos. | 20
17.8 | 90 deg Vertical Bend (Inside) Perforated (shall be decided as per detail engineering)
a. | 600mm Wide | Nos. | 10
b. | 300mm Wide | Nos. | 4
c. | 150mm Wide | Nos. | 20
17.9 | 90 deg Vertical Bend (outside) Perforated (shall be decided as per detail engineering)
a. | 600mm Wide | Nos. | 10
b. | 300mm Wide | Nos. | 4
c. | 150mm Wide | Nos. | 20
17.1 | TEE Connection Perforated type (shall be decided as per detail engineering)
a. | 600mm Wide | Nos. | 8
18 | STEEL STRUCTURAL/ MS PLATE/ MS CHEQUARD PLATE
18.1 | Supply and Erection of MS Structural Steel: MS structural steel like ISMC , angles, flats etc conforming to IS-2062. : Structural steel work riveted,bolted or welded in built up sections, trusses & framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete: | Ton | 7
18.2 | Supplying and fixing of 6 mm thick chequered plate on cable trench inside swtich room, DG room, earthing pit including cutting, painting, lifting hooks, etc conforming to IS-3502. | Sqm | 100
18.3 | 3mm to 10mm thick MS plate conforming to IS-2062 | Ton | 1.5
19 | EARTHING & LIGHTNING
Supply of following Hot dip Galvanized earthing and lightning protection materials along with the accessories conforming to IS & drg. Attachment no.-29 (LPG.ENG.117.06.03.2001) of contract specification Specifications and .(Galvanisation is 910gms/sq. mtr)
19.1 | 50 x 6 mm GI Strip | m | 4400
19.2 | 35 x 6 mm GI Strip | m | 2400
19.3 | 25 x 6 mm GI Strip | m | 1100
19.4 | 1C x 150 mm2 PVC (Al) cable Green colour | m | 560
19.5 | 1C x 95 mm2 PVC (Al) cable Green colour | m | 670
19.6 | 1C x 35 mm2 PVC (Al) cable Green colour | m | 330
19.7 | 1C x 16 mm2 PVC (Al) cable Green colour | m | 850
19.8 | 1C x 2.5 mm2 PVC (Cul) cable Green colour | m | 150
19.8 | Hot dip Galvanized 10 Holes ∅13mm ground plate 550mmx50mmx6mm earth connection bar with fixing materials/ accessories , SS hardware etc. (min. coating 120 microns of zinc). | Nos | 70
19.9 | Flexible earth provision inclusive of flexible cable, hanger, grounding clip etc for LPG unloading tanker | Nos | 3
19.1 | 1000mm long,20 dia. Hot dipped GI air termination rod(lightning rod-120 Micron coating) with all fixing material,accessories as per IS:2309 | Nos | 3
20 | Earthing Lug
20.1 | 1C x 150 mm2 PVC (Al) cable Green colour | Nos | 60
20.2 | 1C x 95 mm2 PVC (Al) cable Green colour | Nos | 80
20.3 | 1C x 35 mm2 PVC (Al) cable Green colour | Nos | 65
20.4 | 1C x 16 mm2 PVC (Al) cable Green colour | Nos | 300
20.5 | 1C x 2.5 mm2 PVC (Cul) cable Green colour | Nos. | 850
20.5 | SQUARE TAPE CLAMP | Nos | 40
20.6 | TEST LINK | Nos | 10
20.7 | TAPE CLIP | Nos | 1000
20.8 | TEE JOINT | Nos | 700
20.9 | Earth Pit: Supply of Maintanance Free (chemical) Earth electrode with all parts including required hardware for earth pit (equipment earthing, Neutral earthing and for lightning protection) and required test link for checking earth connectivity.as per specification,Attachment-29 LPG.ENG.117.06.03.2001, IS and direction of Engineer-in-charge icludingincluding supply of commissioning and 2 years O&M spares.
a. | Earth pit for Body Earthing ( BEP) | Nos | 23
b. | Earth pit for Lightning Earthing ( LEP) | Nos | 31
c. | Earth pit for Neutral Earthing ( NEP) | Nos | 8
d. | Instrument earth pit (IEP) | Nos | 27
21 | Earth Pit: Supply of Maintanance Free (chemical) Earth electrode 4 mtr long, 100 mm dia suitable for rocky area with all parts including required hardware for earth pit as required as per IS 3043. The pipe shall be embedded as far as possible vertically into the ground, except when hard rock is encountered, where it may be burled inclined to the vertical, the inclination being limited to 30 degree from the vertical. The connection of MS flat to each electrode shall be made through MS links by bolted joints to enable isolation of the electrode for testing purposes. . This is included with excavation, restoration and removal extra earth/rock. and required test link for checking earth connectivity.as per specification,Attachment-29 LPG.ENG.117.06.03.2001, IS and direction of Engineer-in-charge icludingincluding supply of commissioning and 2 years O&M spares. | Nos | 8
22 | GENERAL SAFETY EQUIPMENT
22.1 | 11 kV, 900mm wide, electric grade floor rubber mat conforming to relevant IS. ISI mark shall be there on rubber mat. | m | 5
22.2 | 1.1 kV, 900mm wide, electric grade floor rubber mat (in pieces of length not less than 2 mtrs.) conforming to relevant IS. ISI mark shall be there on rubber mat. | m | 60
22.3 | Rubber Hand Gloves of 11 KV grade. | Pair | 4
22.4 | Rubber Hand Gloves of 415V grade. | Pair | 6
22.5 | First aid box of GI, 18 SWG sheet with necessary items. | No. | 8
22.6 | DANGER PLATE (As per IS 2551) | Nos. | 30
22.7 | CABLE ROUTE MARKER | Nos. | 200
22.8 | CO2 fire extinguishers 5kg with fixing bracket | Nos. | 18
22.9 | ABC Dry chemical powder (DCP) fire extinguishers 5kg with fixing bracket | Nos. | 18
21.1 | Shock treatment chart | Nos. | 40
21.11 | Fire buckets (4nos.) with sand & M.S. Hooks / stand | Set | 10
INST | CONTROL & INSTRUMENTATION WORKS
PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)
Note: 1. All items under this section shall be quoted for supply to site including charges towards packing and forwarding, loading, unloading, transportation, insurance etc. Third party inspection for the supply items shall be in tenderer's scope. Approval of TPI agency shall be obtained from IOCL/EPMC on award of contract & engaged for inspection & clearance of all materials as per agreed QAP to be firmed up after placement of order by IOCL/EPMC.
1 | FIRE DETECTION SYSTEM
1.1 | Presssure Transmitter & solenoid valve for Deluge valve
1.1.1 | Supply of pressure transmitter (24 V DC) Exd type, 2 nos. with each DV (1 nos. for air line & 1 no. for water line) Description:IP-66, EExia IIA IIB, T3 (ATEX /CENELEC),CCOE 4 ~ 20 mA +HART, Range: 0~7kg/cm2 (11 nos.) & 0~15kg/cm2 (11 Nos ), Acuracy:0.075% of span. Rangeability – 1:100 , service: water & Air, SS316 cable gland. refer tender specification for detail. | Nos. | 22
1.1.2 | Supply flameproof solenoid valve (24V DC) suitable for Hazardous area zone-1, IIA/IIB T3, 1/2" NPT connection as per specification (9 nos for DV+2 Nos spares) | Nos. | 9
1.2 | ESD PUSH BUTTON STATION
1.2.1 | Supply of ESD Push button station with all accessories like cables , glanding & termination etc. mounted on Exd JBs located at different areas - a)Filling Shed, b)Pump house, c)LPG Bullets, d)TLD , e)Central Monitoring Hub f) plant manager room g) Filled Cylinder Area | Nos. | 7
1.3 | SIREN
1.3.1 | Supply of electric siren at pump house/PMCC/Security room. Scope also includes: a) supply of necessory equipments/component/ accessories including siren controller required to complete system as per tender document. b) supply of any support required for siren & it's panel | Nos. | 1
1.3.2 | Supply of Hand operated siren for the location of LPG pump house, security room, TLD bay & Empty cum filling shed. | Nos. | 4
1.4 | Fire detection system & integrated local panels
1.4.1 | Supply of Fire Alarm System panel along with electronic card and other electrical accessories. All hardware and software to integrate all devices for successful functioning of the system included in the scope. All Fire Alarm Panel Panels shall be integrated through MODBUS / PROFIBUS / OEM RECOMMENDED SERIAL LINK COMMUNICATION. Common Fault Alarm shall be generated in Fire Alarm Panel to hook up through hardware cable to PLC / ESD located at CR. Associated electrical or electronics circuit connecting with the field devices of detection system requires high availability and reliability in confirmation to tender drawings and specification. Fire alarm system shall be UL listed. Fire Detection System Panel shall include below mentioned items: 1. Intelligent Analogue Addressable type non-ex-proof type Manual Call point (06 Nos), to be hooked up with Fire Alarm Panel at CMH, 2. Intelligent Analogue Addressable type Flame proof type Manual Call point (07 Nos), to be hooked up with Fire Alarm Panel at CMH, 3. Isolator Modules (03 Nos), to be hooked up with Fire Alarm Panel at CMH. 4. Control Modules (05 Nos), to be hooked up with Fire Alarm Panel at CMH. 5. Intelligent Analogue Addressable type Multi Criteria Detector (05 Nos) to be hooked up in Fire Alarm Panel of CMH). 6. Response Indicators (05 Nos), 7 Audio Visual Fire Alarm Siren (05 Nos). Above items shall be read in conjuction with Fire Detection drawing & ILSD drawing. | Lot | 1
1.4.2 | SUPPLY of DV Operation Panel integrating with PLC and with PB (with operation indicating lamp for "DV on Fire" and "DV Operated") for opening of Deluge Valve (09 nos+ 1 spare) . All hardware as required and software included. (1 No. DV panel shall be installed at fire water pump house, 1 No. at main gate security room.) | Lot | 2
2 | GAS MONITORING SYSTEM
2.1 | Gas detectors
2.1.1 | Supply of flameproof/EX -proof , IP-66 IR gas detector suitable to hazardous area Zone-1, IIA/B T3 . Canopy & any otther acessories required is included in scope | Nos. | 28
2.2 | Gas monitoring system
2.2.1 | Gas monitoring system: Supply of Dual redundant (Parallel/ Hot Standby) wall mounted Programmable Logic Controller (Process PLC) along with PLC Panels, Input Output modules, Power supply units, Relays with base, barriers, TBs, Dual Ethernet ports per processors, Serial Interface Modules, wirings, glands, plugs, other modules/ hardwares required for interfacing all the required field and Central Monitoring Hub (CMH) equipments including spare requirements, licenses, tags, softwares etc complete as per specification and tender document. AI -28 Nos DI -12 Nos DO -04 Nos Serial Interface Ports: 04 Additional 20% spare (min 1) qty to be supplied over the above mentioned I/O quantity.Size of the PLC panel shall be optimized mode to accomodate all the signals in wall mounted panel only. Gas monitoring system at Central Monitoring Hub (CMH) as per tender documents. the scope also includes supply of all componennt, accessories required for complete the system and customization of reports as detailed in specifications and tender documents. | Lot | 1
2.2.2 | Supply of weather proof Repeater panel at security room alongwith hooter & indication of Fault & LEL Alarm as per tender secifications. Panel to be hooked up with GMS at CMH. | Nos. | 1
2.2.3 | Supply of Flameproof/Ex-Proof cum weatherproof Repeater Panel alongwith Flameproof/Ex-proof Hooter & indication of Fault & LEL Alarm as per tender secifications. same to be hooked up with GMS at CR , All cabling & hardware included (Common repeater panel 1 no. in LPG Pump House room for TLD, LPG P/H & MSV's area gas detectors; 1 no for Filling shed & filled cylinder shed. ) | Nos. | 2
2.2.4 | Supply of sample gas cylinder for gas detectors sufficient to calibrate min. 21 nos. Gas detectors at a time. All asscessories needed for calibration are included in scope | Lot | 4
3 | TANK FARM MANAGEMENT SYSTEM
3.1 | Supply of Tank farm management (TFM) - accessories , all required components as per ITB Specifications and Documents/ Drg ,Technical discussions , correspondences , including Documentation , Testing, Inspection, packing , transportation to site, guarantee etc. - Radar gauges, Servo gauges, Pressure Transmitter, temperature transmitter, multi point TE RTD type on all MSV tank, backend system along with computer terminal, TFM (CIU), TFM panels, Redundant Server along with software, facility for printing in common network printer, communication system Ethernet base (TFM side) with communication cable to interface with PLC as per the quantities mentioned in tender documents/ drawings, Electrical accessories if required and any other modification, painting etc. All other hardware and software as per Specifications and drawings in tender documents.
3.1.1 | The followings shall be considered for above - i) Servo Gauge with Display , Accuracy +-1mm LAB conditions,Density Measurement - 1 no. for each MSV | Nos | 3
3.1.2 | ii) Pressure Tx with 2 valve manifold for vapour pressure measurement Range 0 -15 Kg/CM2 - 2 nos. for each MSV | Nos | 3
3.1.3 | iii) Radar Gauge with Display and - +/-1mm LAB condition with Display (Smart typeTank Side Indicator),Temperature sensor interface, Suitable for 6" Sch 10 Stilling pipe,1 Nos. SIL3 Relay Output & Analog Output - 1 no. for each MSV | Nos | 3
3.1.4 | iv) Vibration Fork type level switch with HH/LL set points - 1no. For each MSV | Nos | 3
3.1.5 | v) Smart type tank side indicator for Radar gauge at LPG pump house & interfacing with Radar gauge & Process PLC /safety PLC - 1 no. for each MSV | Nos | 3
3.1.6 | vi) Smart type tank side indicator for servo Gauge at LPG pump house & interfacing with servo gauge & Process PLC /safety PLC 1 no. for each MSV | Nos | 3
3.1.7 | vii) local indicator for pressure transmitter at LPG pump house - 1 no. for each MSV | Nos | 6
3.1.8 | viii) Interface (Radar & Servo) | Nos | 6
3.1.9 | ix) 9 Point temperature probe ( to be interface with Radar & Servo) | Nos | 3
2010-01-03 00:00:00 | x) Redundant CIU/FCU with all interfacing , 2 nos of Modbus ports for Process PLC and 2 nos of Modbus ports for TFMS connectivity as required - 1 set | Set | 1
2011-01-03 00:00:00 | xii) Verification pin set | Nos | 20
2012-01-03 00:00:00 | xiii)TFMS Software supplied by bidder shall be same make as radar manufacturer and compatible with servo gauges. Licence shall be 12 nos min. | Lot | 1
2013-01-03 00:00:00 | xiv) Junction Boxes - | Nos | 4
2014-01-03 00:00:00 | xv) PDB Panel for TFMS. | Nos | 2
2015-01-03 00:00:00 | xvi) Communication cable, RTD cable, Power cable for TFMS | Lot | 1
2016-01-03 00:00:00 | xvIi) Audio-Visual Annunciation Panel for annunciation at LPG Pump House, integrated with all Level Switches of MSVs (Single common Panel for all level switches) | Nos | 1
3.2 | Tank Farm Management Servers - Commodity Grade, working on redundant (Primary and Secondary) hot standby mode with software, including backlit LED Monitor, key board and mouse. Supply , Installation, erection and commissioning of Operator Interface Console Computer (OIC) with 22" colour LED monitor, standard keyboard etc. complete as per specifications at Central Monitoring Hub (CMH). | Lot | 1
3.3 | Other items for above - FLP Double compression type SS cable glands - As required , Adaptor Plate for Radar Gauge 4"/6",300# (SS316) for Radar tags - 1 no , Adaptor Plate for Temperature Probes 2",300# (SS316) - 4 nos , Fabricated Adaptor Chamber for Servo Gauge 2"X 4" X 6"300# (MOC CS) with pressure gauge, needle valve & pressure relief valve for Servo Tags , Studs as per SA 320 Gr. L7 & Bolts Nuts as per SA 194 Gr. 7 , Gaskets ( 6",4", 2") Spiral wound Metallic AISI 304, asbestos filled as per API 601 , fabricated cable for CIU & PC - As required ,fabrication of manifold for ionstllation of local indicator (radar /servo)- as required, Cables for communication of Servo , Radar / Servo / field Instruments to CIU (FRLS Cable for data communicatin) - As required , All software and Hardware shall be included as required , Bidder shall consider Process PLC & Tank Gauging system interface on redundant Modbus Communication , Any other item to achieve complete system to successful functioning and integration with other system as required are included. | Lot | 1
4 | AUTOMATION SYSTEM
4.1 | TLF/TLD GANTRY
4.1.1 | Supply of Flameproof cum weather proof smart type Grounding unit with one green indicating lamp and dual output for safety earthing of tank trucks, suitable for giving safety interlocking signal to PLC all complete as per specifications | Nos. | 2
4.2 | Central Monitoring Hub (CMH) INSTRUMENTATION
4.2.1 | Supply of Dual redundant (Parallel/ Hot Standby) Programmable Logic Controller (Process PLC) along with PLC Panels, Marshalling Panels, Input Output modules, Power supply units, Relays with base, barriers, TBs, Dual Ethernet ports per processors, Serial Interface Modules, HMI console, wirings, glands, plugs, other modules/ hardwares required for interfacing all the required field and Central Monitoring Hub (CMH) equipments including spare requirements, licenses, tags, GUI, softwares etc complete as per specification and tender document. AI -25 Nos DI -96 Nos DO -80 Nos Serial Interface Ports: 28 Minimum 20% spare IO to be supplied as per tender specification. Count of PLC panel shall be optimized to accomodate all the signals in one panel only. | Lot | 1