## Sheet1
section_context_for_this_product_block | full_product_description | core_product_name | acronymed_core_product_name | size | feature_or_specifications | quantity | unit | sheet_name
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 1.1 ¦ Design and supply of H-pole Structure for 11 KV Incoming Power Supply with Gang operated isolator, D.O. fuse with base, lightning arrestors, Insulator, earthing, construction of earth Pits, fencing, gate, gravel laying, padlocking, signages including all civil works for 11 KV Supply. The design shall be in line with Electricity board guidelines. | h-pole structure |  | supply voltage: 11 KV | feature: gang operated isolator, feature: d.o. (drop out) fuse with base, feature: lightning arrestors, feature: insulator, feature: earthing, feature: construction of earth pits, feature: fencing, feature: gate, feature: gravel laying, feature: padlocking, feature: signages, feature: all civil works, standard: electricity board guidelines | 1 | Set | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 2.1 ¦ 11 KV, 630 A, VCB panel indoor type comprising of metering and protection system including numerical relay, auxiliary relay, CTs, PTs , indication lamp, switches along with Weather proof double compression Ni plated brass cable gland and crimping type cable lugs for all incoming and outgoing cables and as per specfication.. | vcb panel | vcb panel (vacuum circuit breaker panel) | supply voltage: 11 KV, current: 630 A | type: indoor, feature: metering and protection system, feature: numerical relay, feature: auxiliary relay, feature: cts (current transformers), feature: pts (potential transformers), feature: indication lamp, feature: switches, feature: weather proof double compression ni (nickel) plated brass cable gland, feature: crimping type cable lugs for all incoming and outgoing cables, standard: as per specification | 1 | No. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 3.1 ¦ 500 KVA, 11KV/433V, Dyn11, AN type with off load tap changer power transformer complete with all accessories as per attached specifications & DS. | power transformer |  | capacity: 500 KVA, primary voltage: 11 KV, secondary voltage: 433 V | vector group: dyn11, cooling type: an (air natural), feature: off load tap changer, feature: complete with all accessories, standard: as per attached specifications & ds (data sheet) | 1 | No. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 3.2 ¦ 200KVA, 415V/433V, Dyn1, natural air cooled Dry type Lighting transformer as per attached specifications & DS. | lighting transformer |  | capacity: 200 KVA, primary voltage: 415 V, secondary voltage: 433 V | vector group: dyn1, cooling type: natural air cooled, type: dry type, standard: as per attached specifications & ds (data sheet) | 1 | No. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 4.1 ¦ PMCC: 415V, 3phase, 4 wire, 50 Hz, 800A, 50 KA for 1second, double front fully draw out type PMCC comprising of ACBs, CTs/PTs, relays, indicating lamps etc. as per attached SLDs, specifications & DS. | pmcc (power and motor control center) | pmcc | voltage: 415 V, phases: 3 phase, wires: 4 wire, frequency: 50 Hz, current: 800 A, short circuit withstand: 50 KA for 1 second | type: double front fully draw out, feature: acbs (air circuit breakers), feature: cts/pts (current transformers/potential transformers), feature: relays, feature: indicating lamps, standard: as per attached slds (single line diagrams), specifications & ds (data sheet) | 1 | No. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 4.2 ¦ MLDB: 415V, 3phase, 4 wire, 50 Hz, 400A, 25KA for 1second MLDB including as per attached SLD, specifications & DS. | mldb (main lighting distribution board) | mldb | voltage: 415 V, phases: 3 phase, wires: 4 wire, frequency: 50 Hz, current: 400 A, short circuit withstand: 25 KA for 1 second | standard: as per attached sld (single line diagram), specifications & ds (data sheet) | 1 | No. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 4.3 ¦ Fire water MCC: 415V, 3phase, 4 wire, 50 Hz, 400A, 50KA for 1second MCC including as per attached SLD, specifications & DS. | fire water mcc (motor control center) | mcc | voltage: 415 V, phases: 3 phase, wires: 4 wire, frequency: 50 Hz, current: 400 A, short circuit withstand: 50 KA for 1 second | standard: as per attached sld (single line diagram), specifications & ds (data sheet) | 1 | No. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 4.4 ¦ CAPACITOR PANEL : 415V, 3Ph-N, 50Hz, 50KA for 1second, 250KVAR capacitor panel with capacitors 2X75, 1X50, 2X25 KVAR) and APFC relay, protections, filters etc. as per attached SLD, specifications & DS including weather proof double compression Ni plated brass cable glands and lugs for all incoming and outgoing feeders. | capacitor panel |  | voltage: 415 V, phases: 3 phase-neutral, frequency: 50 Hz, short circuit withstand: 50 KA for 1 second, capacity: 250 KVAR (2X75, 1X50, 2X25 KVAR) | feature: apfc (automatic power factor correction) relay, feature: protections, feature: filters, standard: as per attached sld (single line diagram), specifications & ds (data sheet), feature: weather proof double compression ni (nickel) plated brass cable glands and lugs for all incoming and outgoing feeders | 1 | No. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 5.1 ¦ LDB / LP, W eatherproof, IP 65, incomer 63A, 3 Phase, 4 wire, 3 Way LDB, 10kA for 1 sec with RCBO | ldb (lighting distribution board) | ldb | incomer: 63 A, phases: 3 phase, wires: 4 wire, ways: 3 way, short circuit withstand: 10 KA for 1 sec | type: weatherproof, protection: ip 65, feature: rcbo (residual current circuit breaker with overcurrent protection) | 1 | No. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 5.2 ¦ LDB / LP, W eatherproof, IP 65, incomer 63A, 3 Phase, 4 wire, 6 Way LDB, 10kA for 1 sec with RCBO | ldb (lighting distribution board) | ldb | incomer: 63 A, phases: 3 phase, wires: 4 wire, ways: 6 way, short circuit withstand: 10 KA for 1 sec | type: weatherproof, protection: ip 65, feature: rcbo (residual current circuit breaker with overcurrent protection) | 1 | No. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 5.3 ¦ LDB / LP, Outdoor type, Flame proof (FLP) Type, IP class suitable for FLP and minimum protection shall be IP-65, incomer 63A, 3 Phase, 4 wire, 3 Way LDB, 10kA for 1 sec with RCBO | ldb (lighting distribution board) | ldb | incomer: 63 A, phases: 3 phase, wires: 4 wire, ways: 3 way, short circuit withstand: 10 KA for 1 sec | type: outdoor, type: flame proof (flp), protection: ip class suitable for flp, minimum protection: ip-65, feature: rcbo (residual current circuit breaker with overcurrent protection) | 5 | No. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 5.4 ¦ LDB / LP, Outdoor type, Flame proof (FLP) Type, IP class suitable for FLP and minimum protection shall be IP-65 , incomer 63A, 3 Phase, 4 wire, 6 Way LDB, 10kA for 1 sec with RCBO | ldb (lighting distribution board) | ldb | incomer: 63 A, phases: 3 phase, wires: 4 wire, ways: 6 way, short circuit withstand: 10 KA for 1 sec | type: outdoor, type: flame proof (flp), protection: ip class suitable for flp, minimum protection: ip-65, feature: rcbo (residual current circuit breaker with overcurrent protection) | 1 | No. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 5.5 ¦ UPS DB - 230V, 50Hz,Outdoor type, Flame proof (FLP) Type, IP class suitable for FLP and minimum protection shall be IP-65, incomer 63A, 3 Phase, 4 wire, 3 Way LDB, 10kA for 1 sec with RCBO | ups db (uninterruptible power supply distribution board) | ups db | voltage: 230 V, frequency: 50 Hz, incomer: 63 A, phases: 3 phase, wires: 4 wire, ways: 3 way, short circuit withstand: 10 KA for 1 sec | type: outdoor, type: flame proof (flp), protection: ip class suitable for flp, minimum protection: ip-65, feature: rcbo (residual current circuit breaker with overcurrent protection) | 1 | No. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 5.6 ¦ Feeder Pillar for street Lighting . 415V, 3Ph, 50Hz, Flame proof (IP class suitable for FLP and minimum protection shall be IP-65) sheet steel enclosure column/structural mounted, with photovoltic cell based control with A/M selector switch, start/stop PB, indicating lamps etc. with 3mm thick FRP canopy and side cover of the following incoming and outgoing feeders: i) 1no.-Incomer 63A, 3 phase RCBO 30 mA ii) 3nos.-O/G 16A TPN MCB | feeder pillar |  | voltage: 415 V, phases: 3 phase, frequency: 50 Hz, enclosure thickness: 3 mm, incomer: 63 A, outgoing: 3 x 16 A tpn mcb | type: flame proof (ip class suitable for flp), minimum protection: ip-65, enclosure: sheet steel, mounting: column/structural, feature: photovoltic cell based control, feature: a/m (auto/manual) selector switch, feature: start/stop pb (push button), feature: indicating lamps, feature: frp (fiber reinforced plastic) canopy and side cover, feature: rcbo 30 ma (residual current circuit breaker with overcurrent protection), feature: tpn mcb (triple pole and neutral miniature circuit breaker) | 1 | No. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 5.7 ¦ PDB at outdoor location . 415V, 3Ph, 50Hz, W eatherproof and Flame proof (IP class suitable for FLP and minimum protection shall be IP-65) sheet steel enclosure column/structural mounted, start/stop PB, indicating lamps etc. with 3mm thick FRP canopy and side cover of the following incoming and outgoing feeders: i) 1no.-Incomer 100A TPN MCCB ii) 5nos.-O/G 32A TPN MCCB One outgoing shall be provided with photovoltic cell based control with A/M selector switch, start/stop PB, indicating lamps etc to feed the street light. | pdb (power distribution board) | pdb | voltage: 415 V, phases: 3 phase, frequency: 50 Hz, enclosure thickness: 3 mm, incomer: 100 A tpn mccb, outgoing: 5 x 32 A tpn mccb | type: weatherproof, type: flame proof (ip class suitable for flp), minimum protection: ip-65, enclosure: sheet steel, mounting: column/structural, feature: start/stop pb (push button), feature: indicating lamps, feature: frp (fiber reinforced plastic) canopy and side cover, feature: photovoltic cell based control, feature: a/m (auto/manual) selector switch | 1 | No. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 6.1 ¦ 110V, 10A BATTERY CHARGER consisting of dual float cum boost charger and Ni-Cd type battery (43AH) with two hour back up capacity as per attached specifications & DS. | battery charger |  | voltage: 110 V, current: 10 A, battery capacity: 43 AH, backup time: 2 hours | feature: dual float cum boost charger, battery type: ni-cd (nickel-cadmium), standard: as per attached specifications & ds (data sheet) | 1 | No. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 6.2 ¦ DC DISTRIBUTION BOARD: 110V DC, 2 wire 63A DC Distribution Board fed by duel float cum boost charger as per attached SLD, specifications & DS. Incomer: 63A DP MCB Outgoing: 15nos. 16A DP MCB | dc distribution board |  | voltage: 110 V DC, wires: 2 wire, incomer: 63 A dp mcb, outgoing: 15 x 16 A dp mcb | fed by: dual float cum boost charger, standard: as per attached sld (single line diagram), specifications & ds (data sheet) | 1 | No. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 7.1 ¦ Supply of Flameproof lighting fixtures, Lamps & Accessories as per attached specification. (All Lighting fixtures shall be provided with required no. of FLP double compression stainless steel cable glands and FLP stopping plug and control gear boxes etc. All fixtures shall have inbuilt JBs for loop in loop out facility of 3Cx2.5 sqmm Cu lighting cables) 230 Volt AC, 40W Well glass Flameproof Ex'd',LED lighting fixtures and all other accessories | flameproof lighting fixtures |  | voltage: 230 V AC, power: 40 W | type: well glass, type: flameproof ex'd', type: led, feature: flp (flame proof) double compression stainless steel cable glands, feature: flp stopping plug, feature: control gear boxes, feature: inbuilt jbs (junction boxes) for loop in loop out facility of 3cx2.5 sqmm cu (copper) lighting cables, standard: as per attached specification | 135 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 7.2 ¦ Supply of weatherproof lighting fixtures, Lamps & Accessories as per attached specification. (All Lighting fixtures shall be provided with required no. of double compression stainless steel cable glands and stopping plug. All control gear boxes shall be provided with 3mm thick FRP canopy with side cover. .All fixtures shall have inbuilt JBs for loop in loop out facility of 3Cx2.5 sqmm Cu lighting cables) 230 Volt AC, 40W Well glass weatherproof ,LED lighting fixtures and all other accessories | weatherproof lighting fixtures |  | voltage: 230 V AC, power: 40 W | type: well glass, type: weatherproof, type: led, feature: double compression stainless steel cable glands, feature: stopping plug, feature: control gear boxes with 3 mm thick frp (fiber reinforced plastic) canopy with side cover, feature: inbuilt jbs (junction boxes) for loop in loop out facility of 3cx2.5 sqmm cu (copper) lighting cables, standard: as per attached specification | 22 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 8.1 ¦ 240 Volt AC, 16 A, Cast Aluminium Flameproof Ex'd' (Zone-1, IIA / IIB) 4-way, 125 mm (minimum) internal dimensions junction box with terminals block suitable for 2.5 sq.mm along with flameproof double compression Ni plated brass cables glands for all incoming and outgoing cables,PVC shroud and other accessories. | junction box |  | voltage: 240 V AC, current: 16 A, ways: 4-way, internal dimensions: 125 mm (minimum) | material: cast aluminium, type: flameproof ex'd', zone: zone-1, gas group: iia or iib, terminal block suitability: 2.5 sq.mm, feature: flameproof double compression ni (nickel) plated brass cable glands for all incoming and outgoing cables, feature: pvc shroud, feature: other accessories | 45 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 8.2 ¦ 240 Volt AC, 16 A, Cast Aluminium weatherproof 4-way, 125 mm (minimum) internal dimensions junction box with terminals block suitable for 2.5 sq.mm along with weatherproof double compression Ni plated brass cables glands for all incoming and outgoing cables,PVC shroud and other accessories. | junction box |  | voltage: 240 V AC, current: 16 A, ways: 4-way, internal dimensions: 125 mm (minimum) | material: cast aluminium, type: weatherproof, terminal block suitability: 2.5 sq.mm, feature: weatherproof double compression ni (nickel) plated brass cable glands for all incoming and outgoing cables, feature: pvc shroud, feature: other accessories | 18 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 8.3 ¦ JUNCTION BOXES FOR PUMP MOTOR (WEATHER PROOF, FLAME PROOF): Design, Supply, Installation, Testing and Commissionong of following 415V, 3P, Industrial type, W eatherproof, Flame proof “Ex-d” (suitable for hazardous area of gas group IIA/IIB, temperature class T3 and Zone-1), IP 65 suitable for Wall / Column / Structure mounting Including cabling from JB to terminal box for Star-Delta pump motor having different terminal for star and delta connection. All JBs shall be made up of cast Aluminium alloy (LM6 grade) with Canopy of 14 gauge CRCA sheet with side cover. JBs shall confirm to specification/data sheet of tender document. Junction Boxes shall be complete with busbar of suitable rating, support insulator, suitable for 2 nos. of 1RX 3.5 C X 150 Sqmm of Incoming cable size and 2 nos. of 1RX 3.5 C X 95 Sqmm of outgoing cable size XLPE insulated, extruded PVC inner & outer sheathed, FRLS, Armoured cables & shall be supplied along with FLP type double compression, Ni plated brass cable glands, lugs & plugs. However, exact cable sizes shall be indicated during drawing approval only. | junction box |  | voltage: 415 V, phases: 3P, incoming cable size: 2 nos. of 1RX 3.5 C X 150 Sqmm, outgoing cable size: 2 nos. of 1RX 3.5 C X 95 Sqmm | type: weatherproof, type: flameproof ex-d, suitability: hazardous area of gas group iia or iib, temperature class: t3, zone: zone-1, protection: ip 65, mounting: wall or column or structure, feature: cabling from jb to terminal box for star-delta pump motor having different terminal for star and delta connection, material: cast aluminium alloy (lm6 grade), canopy: 14 gauge crca (cold rolled close annealed) sheet with side cover, feature: busbar of suitable rating, feature: support insulator, cable insulation: xlpe, cable sheath: extruded pvc inner and outer sheathed, cable type: frls (flame retardant low smoke), cable type: armoured, feature: flp (flameproof) type double compression ni (nickel) plated brass cable glands, feature: lugs and plugs, standard: as per specification/data sheet of tender document | 1 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 9 ¦ RECEPTACLES | receptacles | [5 empty] | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 9.1 ¦ Supply of flameproof Interlocking type switch sockets and plugs of following ratings as per attached specifications. All switch sockets shall be provided with 3mm thick FRP canopy with side cover and required no. of FLP double compression stainless steel cable glands and FLP stopping plug. i) 415V, 5-pin, 63A flame proof switch socket and plug | switch socket and plug |  | voltage: 415 V, pins: 5-pin, current: 63 A | type: flameproof, type: interlocking, canopy: 3mm thick frp (fiber reinforced plastic) with side cover, cable gland: flp (flameproof) double compression stainless steel, feature: flp stopping plug, standard: as per attached specifications | 4 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 9.1 ¦ Supply of flameproof Interlocking type switch sockets and plugs of following ratings as per attached specifications. All switch sockets shall be provided with 3mm thick FRP canopy with side cover and required no. of FLP double compression stainless steel cable glands and FLP stopping plug. ii) 240V, 3-pin, 16A/5A flame proof switch socket and plug | switch socket and plug |  | voltage: 240 V, pins: 3-pin, current: 16 A or 5 A | type: flameproof, type: interlocking, canopy: 3mm thick frp (fiber reinforced plastic) with side cover, cable gland: flp (flameproof) double compression stainless steel, feature: flp stopping plug, standard: as per attached specifications | 6 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 9.2 ¦ Supply of weatherproof Interlocking type switch sockets and plugs of following ratings as per attached specifications. All switch sockets shall be provided with 3mm thick FRP canopy with side cover and required no. of double compression stainless steel cable glands and stopping plug. i) 415V, 5-pin, 63A weatherproof switch socket and plug | switch socket and plug |  | voltage: 415 V, pins: 5-pin, current: 63 A | type: weatherproof, type: interlocking, canopy: 3mm thick frp (fiber reinforced plastic) with side cover, cable gland: double compression stainless steel, feature: stopping plug, standard: as per attached specifications | 2 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 9.2 ¦ Supply of weatherproof Interlocking type switch sockets and plugs of following ratings as per attached specifications. All switch sockets shall be provided with 3mm thick FRP canopy with side cover and required no. of double compression stainless steel cable glands and stopping plug. ii) 240V, 3-pin, 16A/5A weatherproof switch socket and plug | switch socket and plug |  | voltage: 240 V, pins: 3-pin, current: 16 A or 5 A | type: weatherproof, type: interlocking, canopy: 3mm thick frp (fiber reinforced plastic) with side cover, cable gland: double compression stainless steel, feature: stopping plug, standard: as per attached specifications | 2 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 10 ¦ RIGID/ FLEXIBLE CONDUIT Supply of PVC rigid conduit of min. 2mm thick wall, heavy duty type as per IS (with bends, reducers, couplers etc.) of following sizes:- 10.1 ¦ 25 mm Dia. PVC Rigid Conduit | pvc rigid conduit |  | diameter: 25 mm, wall thickness: min. 2 mm | type: heavy duty, standard: is (indian standard), feature: with bends, reducers, couplers etc. | 50 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 10 ¦ RIGID/ FLEXIBLE CONDUIT Supply of PVC rigid conduit of min. 2mm thick wall, heavy duty type as per IS (with bends, reducers, couplers etc.) of following sizes:- 10.2 ¦ 50 mm Dia. PVC Rigid Conduit | pvc rigid conduit |  | diameter: 50 mm, wall thickness: min. 2 mm | type: heavy duty, standard: is (indian standard), feature: with bends, reducers, couplers etc. | 150 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 10 ¦ RIGID/ FLEXIBLE CONDUIT Supply of PVC rigid conduit of min. 2mm thick wall, heavy duty type as per IS (with bends, reducers, couplers etc.) of following sizes:- 10.3 ¦ 75 mm Dia. PVC Rigid Conduit | pvc rigid conduit |  | diameter: 75 mm, wall thickness: min. 2 mm | type: heavy duty, standard: is (indian standard), feature: with bends, reducers, couplers etc. | 50 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 10 ¦ RIGID/ FLEXIBLE CONDUIT Supply of following PVC flexible conduit of min. 2mm thick wall, heavy duty type & as per IS: 2509. 10.4 ¦ 25 mm Dia PVC Flexible Conduit | pvc flexible conduit |  | diameter: 25 mm, wall thickness: min. 2 mm | type: heavy duty, standard: is 2509 (indian standard 2509) | 425 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 11 ¦ Lighting Cable 0.6/1 kV grade 3C X 2.5 Sqmm Cu XLPE insulated FRLS PVC sheathed Lighting Cable | lighting cable |  | voltage grade: 0.6/1 kV, cores: 3C, conductor size: 2.5 Sqmm | conductor material: cu (copper), insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke) pvc (polyvinyl chloride) | 1800 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 12 ¦ LIGHTING POLES Supply of 9.5 Mtr lighting pole (polygonal type) for base mounting complete with all accessories like MCB & terminal block, JB (as applicable), Zinc passivated hardware for fixtures support & pole support, cable protection pipe with earthing rod/ wire as applicable, clamps, nuts, bolts, etc. | lighting pole |  | height: 9.5 mtr | type: polygonal, mounting: base, accessories: mcb (miniature circuit breaker) and terminal block, jb (junction box) as applicable, hardware: zinc passivated for fixtures support and pole support, cable protection: pipe with earthing rod or wire as applicable, accessories: clamps, nuts, bolts, etc. | 6 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 13 ¦ HIGH MAST LIGHTING TOWER Civil & Structural design, engineering & supply of hot dip galvanised High Mast lighting tower (30 m height) including all accessories for High Mast like 24 nos. of High mast lantern Carraige, 16 nos. of 350 watt LED fixture with lamp, head frame, stainless steel rope, double drum winch, Flameproof junction boxes, Flameproof plugs and sockets, Flameproof feeder pillar, galvanised lantern carrier arrangement, cables and cable accessories control panel for feeder pillar etc. as per specification, data sheet and direction of Engineer- in-charge ingincluding supply of commissioning and 2 years O&M spares. | high mast lighting tower |  | height: 30 m | finish: hot dip galvanised, accessories: 24 nos. high mast lantern carriage, 16 nos. 350 watt led fixture with lamp, head frame, stainless steel rope, double drum winch, flameproof junction boxes, flameproof plugs and sockets, flameproof feeder pillar, galvanised lantern carrier arrangement, cables and cable accessories, control panel for feeder pillar, feature: as per specification, data sheet and direction of engineer-in-charge, feature: supply of commissioning and 2 years o&m (operation and maintenance) spares | 4 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14 ¦ SUPPLY OF HT/ LT CABLES AS PER ENCLOSED SPECIFICATION 11 KV(UE) Grade Cables as per typical specifications ; XLPE insulated; PVC Sheathed; Armoured Aluminium Conductor Cables of Following Sizes As Per Is:1554 (Part-I), IS 7098 Part I & IS 1225-Latest Version and Sealed properly with Pvc Caps of following size:- 14.1 ¦ 3C x 240 sqmm (AL) | armoured aluminium conductor cable |  | voltage grade: 11 kV(UE), cores: 3C, conductor size: 240 sqmm | insulation: xlpe (cross-linked polyethylene), sheath: pvc (polyvinyl chloride), type: armoured, conductor material: aluminium, standard: is 1554 (part-i), is 7098 part i, is 1225-latest version, feature: sealed properly with pvc caps | 250 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14 ¦ SUPPLY OF HT/ LT CABLES AS PER ENCLOSED SPECIFICATION 1.1KV(E) XLPE insulated, FRLS, PVC sheathed aluminium/copper conductor, 1.1 kV grade armoured cable conforming to IS:7098, as per approved make AS PER ENCLOSED SPECIFICATIONS 14.2 ¦ 1C x 400, Sqmm XLPE AL | armoured aluminium conductor cable |  | voltage grade: 1.1 kV(E), cores: 1C, conductor size: 400 sqmm | insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke) pvc (polyvinyl chloride), conductor material: aluminium or copper, type: armoured, standard: is 7098 (indian standard 7098), feature: as per approved make, feature: as per enclosed specifications | 1010 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14 ¦ SUPPLY OF HT/ LT CABLES AS PER ENCLOSED SPECIFICATION 1.1KV(E) XLPE insulated, FRLS, PVC sheathed aluminium/copper conductor, 1.1 kV grade armoured cable conforming to IS:7098, as per approved make AS PER ENCLOSED SPECIFICATIONS 14.3 ¦ 3.5C x 150, Sqmm XLPE AL | armoured aluminium conductor cable |  | voltage grade: 1.1 kV(E), cores: 3.5C, conductor size: 150 sqmm | insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke) pvc (polyvinyl chloride), conductor material: aluminium or copper, type: armoured, standard: is 7098 (indian standard 7098), feature: as per approved make, feature: as per enclosed specifications | 100 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14 ¦ SUPPLY OF HT/ LT CABLES AS PER ENCLOSED SPECIFICATION 1.1KV(E) XLPE insulated, FRLS, PVC sheathed aluminium/copper conductor, 1.1 kV grade armoured cable conforming to IS:7098, as per approved make AS PER ENCLOSED SPECIFICATIONS 14.4 ¦ 3.5C x 95, Sqmm XLPE AL | armoured aluminium conductor cable |  | voltage grade: 1.1 kV(E), cores: 3.5C, conductor size: 95 sqmm | insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke) pvc (polyvinyl chloride), conductor material: aluminium or copper, type: armoured, standard: is 7098 (indian standard 7098), feature: as per approved make, feature: as per enclosed specifications | 500 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14 ¦ SUPPLY OF HT/ LT CABLES AS PER ENCLOSED SPECIFICATION 1.1KV(E) XLPE insulated, FRLS, PVC sheathed aluminium/copper conductor, 1.1 kV grade armoured cable conforming to IS:7098, as per approved make AS PER ENCLOSED SPECIFICATIONS 14.5 ¦ 3.5C X 50, Sqmm XLPE AL | armoured aluminium conductor cable |  | voltage grade: 1.1 kV(E), cores: 3.5C, conductor size: 50 sqmm | insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke) pvc (polyvinyl chloride), conductor material: aluminium or copper, type: armoured, standard: is 7098 (indian standard 7098), feature: as per approved make, feature: as per enclosed specifications | 3000 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14.6 ¦ 4C X 25, Sqmm XLPE AL | armoured aluminium conductor cable |  | cores: 4C, conductor size: 25 sqmm | insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke) pvc (polyvinyl chloride), conductor material: aluminium, type: armoured | 6800 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14.7 ¦ 4C X 16, Sqmm XLPE AL | armoured aluminium conductor cable |  | cores: 4C, conductor size: 16 sqmm | insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke) pvc (polyvinyl chloride), conductor material: aluminium, type: armoured | 600 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14.8 ¦ 4C X 10, Sqmm XLPE AL | armoured aluminium conductor cable |  | cores: 4C, conductor size: 10 sqmm | insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke) pvc (polyvinyl chloride), conductor material: aluminium, type: armoured | 100 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14.9 ¦ 4C X 6, Sqmm XLPE AL | armoured aluminium conductor cable |  | cores: 4C, conductor size: 6 sqmm | insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke) pvc (polyvinyl chloride), conductor material: aluminium, type: armoured | 8000 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14.1 ¦ 4C X 4, Sqmm XLPE AL | armoured aluminium conductor cable |  | cores: 4C, conductor size: 4 sqmm | insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke) pvc (polyvinyl chloride), conductor material: aluminium, type: armoured | 3100 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14.11 ¦ 4C X 2.5, Sqmm XLPE AL | armoured aluminium conductor cable |  | cores: 4C, conductor size: 2.5 sqmm | insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke) pvc (polyvinyl chloride), conductor material: aluminium, type: armoured | 2200 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14.12 ¦ 3C X 6, Sqmm XLPE AL | armoured aluminium conductor cable |  | cores: 3C, conductor size: 6 sqmm | insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke) pvc (polyvinyl chloride), conductor material: aluminium, type: armoured | 400 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14.13 ¦ 3C X 2.5, Sqmm XLPE AL | armoured aluminium conductor cable |  | cores: 3C, conductor size: 2.5 sqmm | insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke) pvc (polyvinyl chloride), conductor material: aluminium, type: armoured | 100 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14.14 ¦ 2C X 4, Sqmm XLPE AL | armoured aluminium conductor cable |  | cores: 2C, conductor size: 4 sqmm | insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke) pvc (polyvinyl chloride), conductor material: aluminium, type: armoured | 200 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14.15 ¦ 2C X 16, Sqmm XLPE AL | armoured aluminium conductor cable |  | cores: 2C, conductor size: 16 sqmm | insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke) pvc (polyvinyl chloride), conductor material: aluminium, type: armoured | 900 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | nan ¦ 1.1KV(E) armoured XLPE, FRLS Control Cable of following size:- 14.16 ¦ 7C x 2.5 SQMM CU | armoured copper control cable |  | voltage grade: 1.1 kV(E), cores: 7C, conductor size: 2.5 sqmm | insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke), conductor material: copper, type: armoured | 27000 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | nan ¦ 1.1KV(E) armoured XLPE, FRLS Control Cable of following size:- 14.17 ¦ 3C x 2.5 SQMM CU | armoured copper control cable |  | voltage grade: 1.1 kV(E), cores: 3C, conductor size: 2.5 sqmm | insulation: xlpe (cross-linked polyethylene), sheath: frls (flame retardant low smoke), conductor material: copper, type: armoured | 800 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 15.16 ¦ 1C x 400, Sqmm XLPE AL | double compression stainless steel cable gland |  | suitable cable size: 1C x 400 sqmm | material: stainless steel, type: double compression, suitability: xlpe (cross-linked polyethylene) frls (flame retardant low smoke) cable, standard: is (indian standard), application: indoor use | 60 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 15.17 ¦ 3.5C x 150, Sqmm XLPE AL | double compression stainless steel cable gland |  | suitable cable size: 3.5C x 150 sqmm | material: stainless steel, type: double compression, suitability: xlpe (cross-linked polyethylene) frls (flame retardant low smoke) cable, standard: is (indian standard), application: indoor use | 6 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 15.18 ¦ 3.5C x 95, Sqmm XLPE AL | double compression stainless steel cable gland |  | suitable cable size: 3.5C x 95 sqmm | material: stainless steel, type: double compression, suitability: xlpe (cross-linked polyethylene) frls (flame retardant low smoke) cable, standard: is (indian standard), application: indoor use | 5 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 15.19 ¦ 3.5C X 50, Sqmm XLPE AL | double compression stainless steel cable gland |  | suitable cable size: 3.5C x 50 sqmm | material: stainless steel, type: double compression, suitability: xlpe (cross-linked polyethylene) frls (flame retardant low smoke) cable, standard: is (indian standard), application: indoor use | 22 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 15.2 ¦ 4C X 25, Sqmm XLPE AL | double compression stainless steel cable gland |  | suitable cable size: 4C x 25 sqmm | material: stainless steel, type: double compression, suitability: xlpe (cross-linked polyethylene) frls (flame retardant low smoke) cable, standard: is (indian standard), application: indoor use | 50 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 15.21 ¦ 4C X 16, Sqmm XLPE AL | double compression stainless steel cable gland |  | suitable cable size: 4C x 16 sqmm | material: stainless steel, type: double compression, suitability: xlpe (cross-linked polyethylene) frls (flame retardant low smoke) cable, standard: is (indian standard), application: indoor use | 50 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 15.22 ¦ 4C X 10, Sqmm XLPE AL | double compression stainless steel cable gland |  | suitable cable size: 4C x 10 sqmm | material: stainless steel, type: double compression, suitability: xlpe (cross-linked polyethylene) frls (flame retardant low smoke) cable, standard: is (indian standard), application: indoor use | 4 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 15.23 ¦ 4C X 6, Sqmm XLPE AL | double compression stainless steel cable gland |  | suitable cable size: 4C x 6 sqmm | material: stainless steel, type: double compression, suitability: xlpe (cross-linked polyethylene) frls (flame retardant low smoke) cable, standard: is (indian standard), application: indoor use | 60 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 15.24 ¦ 4C X 4, Sqmm XLPE AL | double compression stainless steel cable gland |  | suitable cable size: 4C x 4 sqmm | material: stainless steel, type: double compression, suitability: xlpe (cross-linked polyethylene) frls (flame retardant low smoke) cable, standard: is (indian standard), application: indoor use | 15 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 15.25 ¦ 4C X 2.5, Sqmm XLPE AL | double compression stainless steel cable gland |  | suitable cable size: 4C x 2.5 sqmm | material: stainless steel, type: double compression, suitability: xlpe (cross-linked polyethylene) frls (flame retardant low smoke) cable, standard: is (indian standard), application: indoor use | 16 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 15.26 ¦ 3C X 2.5, Sqmm XLPE AL | double compression stainless steel cable gland |  | suitable cable size: 3C x 2.5 sqmm | material: stainless steel, type: double compression, suitability: xlpe (cross-linked polyethylene) frls (flame retardant low smoke) cable, standard: is (indian standard), application: indoor use | 5 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 15.27 ¦ 3C X 6, Sqmm XLPE AL | double compression stainless steel cable gland |  | suitable cable size: 3C x 6 sqmm | material: stainless steel, type: double compression, suitability: xlpe (cross-linked polyethylene) frls (flame retardant low smoke) cable, standard: is (indian standard), application: indoor use | 10 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 15.28 ¦ 2C X 4, Sqmm XLPE AL | double compression stainless steel cable gland |  | suitable cable size: 2C x 4 sqmm | material: stainless steel, type: double compression, suitability: xlpe (cross-linked polyethylene) frls (flame retardant low smoke) cable, standard: is (indian standard), application: indoor use | 4 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 15.29 ¦ 2C X 16, Sqmm XLPE AL | double compression stainless steel cable gland |  | suitable cable size: 2C x 16 sqmm | material: stainless steel, type: double compression, suitability: xlpe (cross-linked polyethylene) frls (flame retardant low smoke) cable, standard: is (indian standard), application: indoor use | 4 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 15.3 ¦ 7C x 2.5 SQMM CU | double compression stainless steel cable gland |  | suitable cable size: 7C x 2.5 sqmm | material: stainless steel, type: double compression, suitability: xlpe (cross-linked polyethylene) frls (flame retardant low smoke) cable, standard: is (indian standard), application: indoor use | 70 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 15.31 ¦ 3C x 2.5 SQMM CU | double compression stainless steel cable gland |  | suitable cable size: 3C x 2.5 sqmm | material: stainless steel, type: double compression, suitability: xlpe (cross-linked polyethylene) frls (flame retardant low smoke) cable, standard: is (indian standard), application: indoor use | 10 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of Raychem make heat shrinkable end termination kit suitable for 11 KV (UE) XLPE, FRLS cables of following sizes. 15.33 ¦ 3C x 240 sqmm (AL) ( suitable for outdoor purpose) | heat shrinkable end termination kit |  | suitable cable size: 3C x 240 sqmm (al) | manufacturer: raychem, type: heat shrinkable, suitability: 11 kv (ue) xlpe (cross-linked polyethylene) frls (flame retardant low smoke) cable, application: outdoor purpose | 1 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of Raychem make heat shrinkable end termination kit suitable for 11 KV (UE) XLPE, FRLS cables of following sizes. 15.34 ¦ 3C x 240 sqmm (AL) ( suitable for indoor purpose) | heat shrinkable end termination kit |  | suitable cable size: 3C x 240 sqmm (al) | manufacturer: raychem, type: heat shrinkable, suitability: 11 kv (ue) xlpe (cross-linked polyethylene) frls (flame retardant low smoke) cable, application: indoor purpose | 3 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 16.1 ¦ 3.5C x 150, Sqmm XLPE AL | crimping type heavy duty long barrel tinned flameproof cable lugs |  | suitable cable size: 3.5C x 150 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, type: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable | 25 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 16.2 ¦ 3.5C x 95, Sqmm XLPE AL | crimping type heavy duty long barrel tinned flameproof cable lugs |  | suitable cable size: 3.5C x 95 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, type: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable | 20 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 16.3 ¦ 3.5C X 50, Sqmm XLPE AL | crimping type heavy duty long barrel tinned flameproof cable lugs |  | suitable cable size: 3.5C x 50 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, type: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable | 80 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 16.4 ¦ 4C X 25, Sqmm XLPE AL | crimping type heavy duty long barrel tinned flameproof cable lugs |  | suitable cable size: 4C x 25 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, type: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable | 200 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 16.5 ¦ 4C X 16, Sqmm XLPE AL | crimping type heavy duty long barrel tinned flameproof cable lugs |  | suitable cable size: 4C x 16 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, type: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable | 200 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 16.6 ¦ 4C X 10, Sqmm XLPE AL | crimping type heavy duty long barrel tinned flameproof cable lugs |  | suitable cable size: 4C x 10 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, type: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable | 8 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 16.7 ¦ 4C X 6, Sqmm XLPE AL | crimping type heavy duty long barrel tinned flameproof cable lugs |  | suitable cable size: 4C x 6 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, type: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable | 240 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 16.8 ¦ 4C X 4, Sqmm XLPE AL | crimping type heavy duty long barrel tinned flameproof cable lugs |  | suitable cable size: 4C x 4 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, type: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable | 60 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 16.8 ¦ 4C X 2.5, Sqmm XLPE AL | crimping type heavy duty long barrel tinned flameproof cable lugs |  | suitable cable size: 4C x 2.5 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, type: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable | 64 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 16.9 ¦ 3C X 2.5, Sqmm XLPE AL | crimping type heavy duty long barrel tinned flameproof cable lugs |  | suitable cable size: 3C x 2.5 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, type: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable | 12 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 16.1 ¦ 3C X 6, Sqmm XLPE AL | crimping type heavy duty long barrel tinned flameproof cable lugs |  | suitable cable size: 3C x 6 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, type: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable | 15 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 16.11 ¦ 2C X 4, Sqmm XLPE AL | crimping type heavy duty long barrel tinned flameproof cable lugs |  | suitable cable size: 2C x 4 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, type: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable | 8 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 16.12 ¦ 2C X 16, Sqmm XLPE AL | crimping type heavy duty long barrel tinned flameproof cable lugs |  | suitable cable size: 2C x 16 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, type: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable | 16 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 16.13 ¦ 7C x 2.5 SQMM CU | crimping type heavy duty long barrel tinned flameproof cable lugs |  | suitable cable size: 7C x 2.5 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, type: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable | 500 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 16.14 ¦ 3C x 2.5 SQMM CU | crimping type heavy duty long barrel tinned flameproof cable lugs |  | suitable cable size: 3C x 2.5 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, type: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable | 100 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 16.15 ¦ 1C x 400, Sqmm XLPE AL | crimping type heavy duty long barrel tinned cable lugs |  | suitable cable size: 1C x 400 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable, feature: indoor use | 60 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 16.16 ¦ 3.5C x 150, Sqmm XLPE AL | crimping type heavy duty long barrel tinned cable lugs |  | suitable cable size: 3.5C x 150 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable, feature: indoor use | 25 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 16.17 ¦ 3.5C x 95, Sqmm XLPE AL | crimping type heavy duty long barrel tinned cable lugs |  | suitable cable size: 3.5C x 95 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable, feature: indoor use | 20 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 16.18 ¦ 3.5C X 50, Sqmm XLPE AL | crimping type heavy duty long barrel tinned cable lugs |  | suitable cable size: 3.5C x 50 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable, feature: indoor use | 80 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 16.19 ¦ 4C X 25, Sqmm XLPE AL | crimping type heavy duty long barrel tinned cable lugs |  | suitable cable size: 4C x 25 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable, feature: indoor use | 200 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 16.2 ¦ 4C X 16, Sqmm XLPE AL | crimping type heavy duty long barrel tinned cable lugs |  | suitable cable size: 4C x 16 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable, feature: indoor use | 200 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 16.21 ¦ 4C X 10, Sqmm XLPE AL | crimping type heavy duty long barrel tinned cable lugs |  | suitable cable size: 4C x 10 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable, feature: indoor use | 8 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 16.22 ¦ 4C X 6, Sqmm XLPE AL | crimping type heavy duty long barrel tinned cable lugs |  | suitable cable size: 4C x 6 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable, feature: indoor use | 240 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 16.23 ¦ 4C X 4, Sqmm XLPE AL | crimping type heavy duty long barrel tinned cable lugs |  | suitable cable size: 4C x 4 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable, feature: indoor use | 60 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 16.24 ¦ 4C X 2.5, Sqmm XLPE AL | crimping type heavy duty long barrel tinned cable lugs |  | suitable cable size: 4C x 2.5 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable, feature: indoor use | 64 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 16.25 ¦ 3C X 2.5, Sqmm XLPE AL | crimping type heavy duty long barrel tinned cable lugs |  | suitable cable size: 3C x 2.5 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable, feature: indoor use | 12 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 16.26 ¦ 3C X 6, Sqmm XLPE AL | crimping type heavy duty long barrel tinned cable lugs |  | suitable cable size: 3C x 6 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable, feature: indoor use | 15 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 16.27 ¦ 2C X 4, Sqmm XLPE AL | crimping type heavy duty long barrel tinned cable lugs |  | suitable cable size: 2C x 4 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable, feature: indoor use | 8 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 16.28 ¦ 2C X 16, Sqmm XLPE AL | crimping type heavy duty long barrel tinned cable lugs |  | suitable cable size: 2C x 16 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable, feature: indoor use | 16 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 16.29 ¦ 7C x 2.5 SQMM CU | crimping type heavy duty long barrel tinned cable lugs |  | suitable cable size: 7C x 2.5 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable, feature: indoor use | 500 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 16.3 ¦ 3C x 2.5 SQMM CU | crimping type heavy duty long barrel tinned cable lugs |  | suitable cable size: 3C x 2.5 sqmm | type: crimping, type: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cable, feature: indoor use | 100 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.1 ¦ Ladder type GI cable tray (100mmx2mm, 3 Meter length) with minimum hot dip zinc coating 75 micron with accessories like coupler plates,bends, Stainless steels hardwares like nuts & bolts , bends, washers etc and as per IS & ES:8161. d. ¦ 150mm Wide | ladder type galvanized iron cable tray |  | tray size: 100mm x 2mm, tray length: 3 meter, width: 150mm | coating: hot dip zinc, coating thickness: 75 micron, accessories: coupler plates, accessories: bends, accessories: stainless steel hardware (nuts & bolts, washers), standard: indian standard & engineering standard 8161 | 228 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.1 ¦ Ladder type GI cable tray (100mmx2mm, 3 Meter length) with minimum hot dip zinc coating 75 micron with accessories like coupler plates,bends, Stainless steels hardwares like nuts & bolts , bends, washers etc and as per IS & ES:8161. e. ¦ 50mm Wide | ladder type galvanized iron cable tray |  | tray size: 100mm x 2mm, tray length: 3 meter, width: 50mm | coating: hot dip zinc, coating thickness: 75 micron, accessories: coupler plates, accessories: bends, accessories: stainless steel hardware (nuts & bolts, washers), standard: indian standard & engineering standard 8161 | 100 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.2 ¦ 90 deg Horizontal Bend Ladder type (shall be decided as per detail engineering) a. ¦ 750mm Wide | ladder type cable tray horizontal bend |  | width: 750mm | bend angle: 90 degree, type: ladder, feature: shall be decided as per detail engineering | 4 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.2 ¦ 90 deg Horizontal Bend Ladder type (shall be decided as per detail engineering) b. ¦ 600mm Wide | ladder type cable tray horizontal bend |  | width: 600mm | bend angle: 90 degree, type: ladder, feature: shall be decided as per detail engineering | 16 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.2 ¦ 90 deg Horizontal Bend Ladder type (shall be decided as per detail engineering) c. ¦ 300mm Wide | ladder type cable tray horizontal bend |  | width: 300mm | bend angle: 90 degree, type: ladder, feature: shall be decided as per detail engineering | 8 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.2 ¦ 90 deg Horizontal Bend Ladder type (shall be decided as per detail engineering) d. ¦ 150mm Wide | ladder type cable tray horizontal bend |  | width: 150mm | bend angle: 90 degree, type: ladder, feature: shall be decided as per detail engineering | 5 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.3 ¦ TEE Connection Ladder type (shall be decided as per detail engineering) a. ¦ 600mm Wide | ladder type cable tray tee connection |  | width: 600mm | feature: shall be decided as per detail engineering | 16 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.3 ¦ TEE Connection Ladder type (shall be decided as per detail engineering) b. ¦ 300mm Wide | ladder type cable tray tee connection |  | width: 300mm | feature: shall be decided as per detail engineering | 5 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.4 ¦ 90 deg Vertical Bend (inside) Ladder (shall be decided as per detail engineering) a. ¦ 600mm Wide | ladder type cable tray vertical bend (inside) |  | width: 600mm | bend angle: 90 degree, type: ladder, position: inside, feature: shall be decided as per detail engineering | 10 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.4 ¦ 90 deg Vertical Bend (inside) Ladder (shall be decided as per detail engineering) b. ¦ 300mm Wide | ladder type cable tray vertical bend (inside) |  | width: 300mm | bend angle: 90 degree, type: ladder, position: inside, feature: shall be decided as per detail engineering | 2 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.5 ¦ 90 deg Vertical Bend (outside) Perforated (shall be decided as per detail engineering) a. ¦ 600mm Wide | perforated cable tray vertical bend (outside) |  | width: 600mm | bend angle: 90 degree, type: perforated, position: outside, feature: shall be decided as per detail engineering | 10 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.5 ¦ 90 deg Vertical Bend (outside) Perforated (shall be decided as per detail engineering) b. ¦ 300mm Wide | perforated cable tray vertical bend (outside) |  | width: 300mm | bend angle: 90 degree, type: perforated, position: outside, feature: shall be decided as per detail engineering | 2 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.6 ¦ G.I. Perforated Cable Trays , 100 mm deep, 3 mm thick G.I. perforated cable trays (Min. coating 100 microns of zinc) with bend, reducer, coupler plate and other hardware. a. ¦ 750mm Wide | galvanized iron perforated cable tray |  | depth: 100 mm, thickness: 3 mm, width: 750mm | material: galvanized iron, coating: zinc, coating thickness: 100 microns, accessories: bend, accessories: reducer, accessories: coupler plate, accessories: other hardware | 10 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.6 ¦ G.I. Perforated Cable Trays , 100 mm deep, 3 mm thick G.I. perforated cable trays (Min. coating 100 microns of zinc) with bend, reducer, coupler plate and other hardware. b. ¦ 600mm Wide | galvanized iron perforated cable tray |  | depth: 100 mm, thickness: 3 mm, width: 600mm | material: galvanized iron, coating: zinc, coating thickness: 100 microns, accessories: bend, accessories: reducer, accessories: coupler plate, accessories: other hardware | 550 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.6 ¦ G.I. Perforated Cable Trays , 100 mm deep, 3 mm thick G.I. perforated cable trays (Min. coating 100 microns of zinc) with bend, reducer, coupler plate and other hardware. c. ¦ 300mm Wide | galvanized iron perforated cable tray |  | depth: 100 mm, thickness: 3 mm, width: 300mm | material: galvanized iron, coating: zinc, coating thickness: 100 microns, accessories: bend, accessories: reducer, accessories: coupler plate, accessories: other hardware | 175 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.6 ¦ G.I. Perforated Cable Trays , 100 mm deep, 3 mm thick G.I. perforated cable trays (Min. coating 100 microns of zinc) with bend, reducer, coupler plate and other hardware. d. ¦ 150mm Wide | galvanized iron perforated cable tray |  | depth: 100 mm, thickness: 3 mm, width: 150mm | material: galvanized iron, coating: zinc, coating thickness: 100 microns, accessories: bend, accessories: reducer, accessories: coupler plate, accessories: other hardware | 350 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.6 ¦ G.I. Perforated Cable Trays , 100 mm deep, 3 mm thick G.I. perforated cable trays (Min. coating 100 microns of zinc) with bend, reducer, coupler plate and other hardware. e. ¦ 50mm Wide | galvanized iron perforated cable tray |  | depth: 100 mm, thickness: 3 mm, width: 50mm | material: galvanized iron, coating: zinc, coating thickness: 100 microns, accessories: bend, accessories: reducer, accessories: coupler plate, accessories: other hardware | 100 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.7 ¦ 90 deg Horizontal Bend Perforated (shall be decided as per detail engineering) a. ¦ 750mm Wide | perforated cable tray horizontal bend |  | width: 750mm | bend angle: 90 degree, type: perforated, feature: shall be decided as per detail engineering | 3 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.7 ¦ 90 deg Horizontal Bend Perforated (shall be decided as per detail engineering) b. ¦ 600mm Wide | perforated cable tray horizontal bend |  | width: 600mm | bend angle: 90 degree, type: perforated, feature: shall be decided as per detail engineering | 20 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.7 ¦ 90 deg Horizontal Bend Perforated (shall be decided as per detail engineering) c. ¦ 300mm Wide | perforated cable tray horizontal bend |  | width: 300mm | bend angle: 90 degree, type: perforated, feature: shall be decided as per detail engineering | 20 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.8 ¦ 90 deg Vertical Bend (Inside) Perforated (shall be decided as per detail engineering) a. ¦ 600mm Wide | perforated cable tray vertical bend (inside) |  | width: 600mm | bend angle: 90 degree, type: perforated, position: inside, feature: shall be decided as per detail engineering | 10 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.8 ¦ 90 deg Vertical Bend (Inside) Perforated (shall be decided as per detail engineering) b. ¦ 300mm Wide | perforated cable tray vertical bend (inside) |  | width: 300mm | bend angle: 90 degree, type: perforated, position: inside, feature: shall be decided as per detail engineering | 4 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Cable Trays 17.8 ¦ 90 deg Vertical Bend (Inside) Perforated (shall be decided as per detail engineering) c. ¦ 150mm Wide | perforated cable tray vertical bend (inside) |  | width: 150mm | bend angle: 90 degree, type: perforated, position: inside, feature: shall be decided as per detail engineering | 20 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.9 ¦ 90 deg Vertical Bend (outside) Perforated (shall be decided as per detail engineering) a. ¦ 600mm Wide | perforated cable tray vertical bend (outside) |  | width: 600mm | bend angle: 90 degree, type: perforated, position: outside, feature: shall be decided as per detail engineering | 10 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.9 ¦ 90 deg Vertical Bend (outside) Perforated (shall be decided as per detail engineering) b. ¦ 300mm Wide | perforated cable tray vertical bend (outside) |  | width: 300mm | bend angle: 90 degree, type: perforated, position: outside, feature: shall be decided as per detail engineering | 4 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.9 ¦ 90 deg Vertical Bend (outside) Perforated (shall be decided as per detail engineering) c. ¦ 150mm Wide | perforated cable tray vertical bend (outside) |  | width: 150mm | bend angle: 90 degree, type: perforated, position: outside, feature: shall be decided as per detail engineering | 20 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.1 ¦ TEE Connection Perforated type (shall be decided as per detail engineering) a. ¦ 600mm Wide | perforated cable tray tee connection |  | width: 600mm | type: perforated, feature: shall be decided as per detail engineering | 8 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 18.1 ¦ Supply and Erection of MS Structural Steel: MS structural steel like ISMC , angles, flats etc conforming to IS-2062. : Structural steel work riveted,bolted or welded in built up sections, trusses & framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete: | ms structural steel supply and erection |  |  | material: ms(mild steel), includes: ISMC, angles, flats, standard: indian standard 2062, work: riveted, bolted or welded in built up sections, trusses & framed work, includes: cutting, hoisting, fixing in position, applying priming coat of approved steel primer | 7 | Ton | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 18.2 ¦ Supplying and fixing of 6 mm thick chequered plate on cable trench inside swtich room, DG room, earthing pit including cutting, painting, lifting hooks, etc conforming to IS-3502. | chequered plate supply and fixing |  | thickness: 6 mm | application: cable trench inside switch room, DG room, earthing pit, includes: cutting, painting, lifting hooks, standard: indian standard 3502 | 100 | Sqm | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 18.3 ¦ 3mm to 10mm thick MS plate conforming to IS-2062 | ms plate |  | thickness: 3mm to 10mm | material: ms(mild steel), standard: indian standard 2062 | 1.5 | Ton | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 19.1 ¦ 50 x 6 mm GI Strip | gi(galvanized iron) strip |  | dimensions: 50 x 6 mm |  | 4400 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 19.2 ¦ 35 x 6 mm GI Strip | gi(galvanized iron) strip |  | dimensions: 35 x 6 mm |  | 2400 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 19.3 ¦ 25 x 6 mm GI Strip | gi(galvanized iron) strip |  | dimensions: 25 x 6 mm |  | 1100 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 19.4 ¦ 1C x 150 mm2 PVC (Al) cable Green colour | pvc(aluminium) cable |  | core: 1C, area: 150 mm2 | colour: green | 560 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 19.5 ¦ 1C x 95 mm2 PVC (Al) cable Green colour | pvc(aluminium) cable |  | core: 1C, area: 95 mm2 | colour: green | 670 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 19.6 ¦ 1C x 35 mm2 PVC (Al) cable Green colour | pvc(aluminium) cable |  | core: 1C, area: 35 mm2 | colour: green | 330 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 19.7 ¦ 1C x 16 mm2 PVC (Al) cable Green colour | pvc(aluminium) cable |  | core: 1C, area: 16 mm2 | colour: green | 850 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 19.8 ¦ 1C x 2.5 mm2 PVC (Cul) cable Green colour | pvc(copper) cable |  | core: 1C, area: 2.5 mm2 | colour: green | 150 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 19.8 ¦ Hot dip Galvanized 10 Holes ∅13mm ground plate 550mmx50mmx6mm earth connection bar with fixing materials/ accessories , SS hardware etc. (min. coating 120 microns of zinc). | hot dip galvanized ground plate earth connection bar |  | holes: 10, hole diameter: 13mm, plate dimensions: 550mm x 50mm x 6mm | coating: hot dip galvanized, minimum coating: 120 microns of zinc, includes: fixing materials/accessories, ss(stainless steel) hardware | 70 | Nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 19.9 ¦ Flexible earth provision inclusive of flexible cable, hanger, grounding clip etc for LPG unloading tanker | flexible earth provision |  |  | includes: flexible cable, hanger, grounding clip, application: LPG unloading tanker | 3 | Nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 19.1 ¦ 1000mm long,20 dia. Hot dipped GI air termination rod(lightning rod-120 Micron coating) with all fixing material,accessories as per IS:2309 | gi(galvanized iron) air termination rod |  | length: 1000mm, diameter: 20mm | coating: hot dipped, coating thickness: 120 micron, includes: all fixing material, accessories, standard: indian standard 2309, type: lightning rod | 3 | Nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 20.1 ¦ 1C x 150 mm2 PVC (Al) cable Green colour | pvc(aluminium) cable |  | core: 1C, area: 150 mm2 | colour: green | 60 | Nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 20.2 ¦ 1C x 95 mm2 PVC (Al) cable Green colour | pvc(aluminium) cable |  | core: 1C, area: 95 mm2 | colour: green | 80 | Nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 20.3 ¦ 1C x 35 mm2 PVC (Al) cable Green colour | pvc(aluminium) cable |  | core: 1C, area: 35 mm2 | colour: green | 65 | Nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 20.4 ¦ 1C x 16 mm2 PVC (Al) cable Green colour | pvc(aluminium) cable |  | core: 1C, area: 16 mm2 | colour: green | 300 | Nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 20.5 ¦ 1C x 2.5 mm2 PVC (Cul) cable Green colour | pvc(copper) cable |  | core: 1C, area: 2.5 mm2 | colour: green | 850 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 20.5 ¦ SQUARE TAPE CLAMP | square tape clamp |  |  |  | 40 | Nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 20.6 ¦ TEST LINK | test link |  |  |  | 10 | Nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 20.7 ¦ TAPE CLIP | tape clip |  |  |  | 1000 | Nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 20.8 ¦ TEE JOINT | tee joint |  |  |  | 700 | Nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 20.9 ¦ Earth Pit: Supply of Maintanance Free (chemical) Earth electrode with all parts including required hardware for earth pit (equipment earthing, Neutral earthing and for lightning protection) and required test link for checking earth connectivity.as per specification,Attachment-29 LPG.ENG.117.06.03.2001, IS and direction of Engineer-in-charge icludingincluding supply of commissioning and 2 years O&M spares. ¦ a. ¦ Earth pit for Body Earthing ( BEP) | earth pit |  |  | type: maintenance free (chemical), included parts: all parts including required hardware for earth pit (equipment earthing, neutral earthing and for lightning protection), included: required test link for checking earth connectivity, specification: as per specification,Attachment-29 LPG.ENG.117.06.03.2001, standard: indian standard, included: supply of commissioning and 2 years o&m spares | 23 | Nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 20.9 ¦ Earth Pit: Supply of Maintanance Free (chemical) Earth electrode with all parts including required hardware for earth pit (equipment earthing, Neutral earthing and for lightning protection) and required test link for checking earth connectivity.as per specification,Attachment-29 LPG.ENG.117.06.03.2001, IS and direction of Engineer-in-charge icludingincluding supply of commissioning and 2 years O&M spares. ¦ b. ¦ Earth pit for Lightning Earthing ( LEP) | earth pit |  |  | type: maintenance free (chemical), included parts: all parts including required hardware for earth pit (equipment earthing, neutral earthing and for lightning protection), included: required test link for checking earth connectivity, specification: as per specification,Attachment-29 LPG.ENG.117.06.03.2001, standard: indian standard, included: supply of commissioning and 2 years o&m spares | 31 | Nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 20.9 ¦ Earth Pit: Supply of Maintanance Free (chemical) Earth electrode with all parts including required hardware for earth pit (equipment earthing, Neutral earthing and for lightning protection) and required test link for checking earth connectivity.as per specification,Attachment-29 LPG.ENG.117.06.03.2001, IS and direction of Engineer-in-charge icludingincluding supply of commissioning and 2 years O&M spares. ¦ c. ¦ Earth pit for Neutral Earthing ( NEP) | earth pit |  |  | type: maintenance free (chemical), included parts: all parts including required hardware for earth pit (equipment earthing, neutral earthing and for lightning protection), included: required test link for checking earth connectivity, specification: as per specification,Attachment-29 LPG.ENG.117.06.03.2001, standard: indian standard, included: supply of commissioning and 2 years o&m spares | 8 | Nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 20.9 ¦ Earth Pit: Supply of Maintanance Free (chemical) Earth electrode with all parts including required hardware for earth pit (equipment earthing, Neutral earthing and for lightning protection) and required test link for checking earth connectivity.as per specification,Attachment-29 LPG.ENG.117.06.03.2001, IS and direction of Engineer-in-charge icludingincluding supply of commissioning and 2 years O&M spares. ¦ d. ¦ Instrument earth pit (IEP) | earth pit |  |  | type: maintenance free (chemical), included parts: all parts including required hardware for earth pit (equipment earthing, neutral earthing and for lightning protection), included: required test link for checking earth connectivity, specification: as per specification,Attachment-29 LPG.ENG.117.06.03.2001, standard: indian standard, included: supply of commissioning and 2 years o&m spares | 27 | Nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 21 ¦ Earth Pit: Supply of Maintanance Free (chemical) Earth electrode 4 mtr long, 100 mm dia suitable for rocky area with all parts including required hardware for earth pit as required as per IS 3043. The pipe shall be embedded as far as possible vertically into the ground, except when hard rock is encountered, where it may be burled inclined to the vertical, the inclination being limited to 30 degree from the vertical. The connection of MS flat to each electrode shall be made through MS links by bolted joints to enable isolation of the electrode for testing purposes. . This is included with excavation, restoration and removal extra earth/rock. and required test link for checking earth connectivity.as per specification,Attachment-29 LPG.ENG.117.06.03.2001, IS and direction of Engineer-in-charge icludingincluding supply of commissioning and 2 years O&M spares. | earth pit |  | length: 4 mtr, diameter: 100 mm | type: maintenance free (chemical), suitable for: rocky area, included parts: all parts including required hardware for earth pit, standard: indian standard 3043, installation: embedded vertically or inclined up to 30 degree from vertical, connection: ms(mild steel) flat to each electrode through ms links by bolted joints, included: enable isolation of the electrode for testing purposes, included: excavation, restoration and removal extra earth/rock, included: required test link for checking earth connectivity, specification: as per specification,Attachment-29 LPG.ENG.117.06.03.2001, standard: indian standard, included: supply of commissioning and 2 years o&m spares | 8 | Nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 22 ¦ GENERAL SAFETY EQUIPMENT | general safety equipment | [5 empty] | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 22.1 ¦ 11 kV, 900mm wide, electric grade floor rubber mat conforming to relevant IS. ISI mark shall be there on rubber mat. | floor rubber mat |  | width: 900mm | voltage: 11 kv(kilovolt), grade: electric, standard: indian standard, certification: isi(indian standards institute) mark | 5 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 22.2 ¦ 1.1 kV, 900mm wide, electric grade floor rubber mat (in pieces of length not less than 2 mtrs.) conforming to relevant IS. ISI mark shall be there on rubber mat. | floor rubber mat |  | width: 900mm, length: not less than 2 mtrs. | voltage: 1.1 kv(kilovolt), grade: electric, standard: indian standard, certification: isi(indian standards institute) mark | 60 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 22.3 ¦ Rubber Hand Gloves of 11 KV grade. | rubber hand gloves |  |  | voltage: 11 kv(kilovolt), grade: - | 4 | Pair | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 22.4 ¦ Rubber Hand Gloves of 415V grade. | rubber hand gloves |  |  | voltage: 415 v(volt), grade: - | 6 | Pair | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 22.5 ¦ First aid box of GI, 18 SWG sheet with necessary items. | first aid box |  | sheet thickness: 18 swg(standard wire gauge) | material: gi(galvanized iron), included: necessary items | 8 | No. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 22.6 ¦ DANGER PLATE (As per IS 2551) | danger plate |  |  | standard: indian standard 2551 | 30 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 22.7 ¦ CABLE ROUTE MARKER | cable route marker |  |  |  | 200 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 22.8 ¦ CO2 fire extinguishers 5kg with fixing bracket | co2 fire extinguisher |  | capacity: 5kg | included: fixing bracket | 18 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 22.9 ¦ ABC Dry chemical powder (DCP) fire extinguishers 5kg with fixing bracket | abc dry chemical powder fire extinguisher | dcp fire extinguisher | capacity: 5kg | included: fixing bracket | 18 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 21.1 ¦ Shock treatment chart | shock treatment chart |  |  |  | 40 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 21.11 ¦ Fire buckets (4nos.) with sand & M.S. Hooks / stand | fire bucket |  | quantity per set: 4nos. | included: sand & ms(mild steel) hooks / stand | 10 | Set | Table 1
['INST', 'CONTROL & INSTRUMENTATION WORKS', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 1 ¦ FIRE DETECTION SYSTEM | fire detection system | [5 empty] | Table 1
['INST', 'CONTROL & INSTRUMENTATION WORKS', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 1.1 ¦ Presssure Transmitter & solenoid valve for Deluge valve | pressure transmitter and solenoid valve |  |  | application: deluge valve |  |  | Table 1
['INST', 'CONTROL & INSTRUMENTATION WORKS', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 1.1.1 ¦ Supply of pressure transmitter (24 V DC) Exd type, 2 nos. with each DV (1 nos. for air line & 1 no. for water line) Description:IP-66, EExia IIA IIB, T3 (ATEX /CENELEC),CCOE 4 ~ 20 mA +HART, Range: 0~7kg/cm2 (11 nos.) & 0~15kg/cm2 (11 Nos ), Acuracy:0.075% of span. Rangeability – 1:100 , service: water & Air, SS316 cable gland. refer tender specification for detail. | pressure transmitter |  | range: 0~7kg/cm2 (11 nos.) & 0~15kg/cm2 (11 Nos ) | voltage: 24 v dc(direct current), type: exd, included: 2 nos. with each dv(deluge valve) (1 nos. for air line & 1 no. for water line), protection: ip-66, certification: eexia iia iib, t3 (atex /cenelec), ccoe, output: 4 ~ 20 ma +hart, accuracy: 0.075% of span, rangeability: 1:100, service: water & air, cable gland: ss316(stainless steel 316) | 22 | Nos. | Table 1
['INST', 'CONTROL & INSTRUMENTATION WORKS', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 1.1.2 ¦ Supply flameproof solenoid valve (24V DC) suitable for Hazardous area zone-1, IIA/IIB T3, 1/2" NPT connection as per specification (9 nos for DV+2 Nos spares) | solenoid valve |  | connection: 1/2" npt(national pipe thread) | type: flameproof, voltage: 24v dc(direct current), suitable for: hazardous area zone-1, certification: iia/iib t3, included: 9 nos for dv(deluge valve)+2 nos spares | 9 | Nos. | Table 1
['INST', 'CONTROL & INSTRUMENTATION WORKS', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 1.2 ¦ ESD PUSH BUTTON STATION | esd push button station | [5 empty] | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 1.2.1 ¦ Supply of ESD Push button station with all accessories like cables , glanding & termination etc. mounted on Exd JBs located at different areas - a)Filling Shed, b)Pump house, c)LPG Bullets, d)TLD , e)Central Monitoring Hub f) plant manager room g) Filled Cylinder Area | esd push button station |  |  | accessories: cables, glanding, termination, mounting: exd (explosion proof) junction boxes, location: filling shed, pump house, lpg bullets, tld, central monitoring hub, plant manager room, filled cylinder area | 7 | Nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 1.3.1 ¦ Supply of electric siren at pump house/PMCC/Security room. Scope also includes: a) supply of necessory equipments/component/ accessories including siren controller required to complete system as per tender document. b) supply of any support required for siren & it's panel | electric siren |  |  | location: pump house, pmcc (power and motor control center), security room, accessories: siren controller, necessary equipment, components, support for siren and panel, as per tender document | 1 | Nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 1.3.2 ¦ Supply of Hand operated siren for the location of LPG pump house, security room, TLD bay & Empty cum filling shed. | hand operated siren |  |  | location: lpg pump house, security room, tld bay, empty cum filling shed | 4 | Nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 1.4.1 ¦ Supply of Fire Alarm System panel along with electronic card and other electrical accessories. All hardware and software to integrate all devices for successful functioning of the system included in the scope. All Fire Alarm Panel Panels shall be integrated through MODBUS / PROFIBUS / OEM RECOMMENDED SERIAL LINK COMMUNICATION. Common Fault Alarm shall be generated in Fire Alarm Panel to hook up through hardware cable to PLC / ESD located at CR. Associated electrical or electronics circuit connecting with the field devices of detection system requires high availability and reliability in confirmation to tender drawings and specification. Fire alarm system shall be UL listed. Fire Detection System Panel shall include below mentioned items: 1. Intelligent Analogue Addressable type non-ex-proof type Manual Call point (06 Nos), to be hooked up with Fire Alarm Panel at CMH, 2. Intelligent Analogue Addressable type Flame proof type Manual Call point (07 Nos), to be hooked up with Fire Alarm Panel at CMH, 3. Isolator Modules (03 Nos), to be hooked up with Fire Alarm Panel at CMH. 4. Control Modules (05 Nos), to be hooked up with Fire Alarm Panel at CMH. 5. Intelligent Analogue Addressable type Multi Criteria Detector (05 Nos) to be hooked up in Fire Alarm Panel of CMH). 6. Response Indicators (05 Nos), 7 Audio Visual Fire Alarm Siren (05 Nos). Above items shall be read in conjuction with Fire Detection drawing & ILSD drawing. | fire alarm system panel |  |  | accessories: electronic card, electrical accessories, hardware, software, integration: modbus, profibus, oem recommended serial link communication, common fault alarm, connection: plc (programmable logic controller), esd (emergency shutdown device) at cr (control room), standard: ul (underwriters laboratories) listed, includes: manual call points (non-ex-proof and flame proof), isolator modules, control modules, multi criteria detector, response indicators, audio visual fire alarm siren, reference: fire detection drawing, ilsd (integrated leak detection system) drawing | 1 | Lot | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 1.4.2 ¦ SUPPLY of DV Operation Panel integrating with PLC and with PB (with operation indicating lamp for "DV on Fire" and "DV Operated") for opening of Deluge Valve (09 nos+ 1 spare) . All hardware as required and software included. (1 No. DV panel shall be installed at fire water pump house, 1 No. at main gate security room.) | dv operation panel |  |  | integration: plc (programmable logic controller), pb (push button), indicating lamp: dv on fire, dv operated, for: deluge valve (9 nos + 1 spare), installation: fire water pump house, main gate security room, hardware and software included | 2 | Lot | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 2.1.1 ¦ Supply of flameproof/EX -proof , IP-66 IR gas detector suitable to hazardous area Zone-1, IIA/B T3 . Canopy & any otther acessories required is included in scope | ir gas detector |  |  | type: flameproof, ex-proof (explosion proof), ingress protection: ip-66, area suitability: hazardous area zone-1, iia/b t3, accessories: canopy, other accessories included | 28 | Nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 2.2.1 ¦ Gas monitoring system: Supply of Dual redundant (Parallel/ Hot Standby) wall mounted Programmable Logic Controller (Process PLC) along with PLC Panels, Input Output modules, Power supply units, Relays with base, barriers, TBs, Dual Ethernet ports per processors, Serial Interface Modules, wirings, glands, plugs, other modules/ hardwares required for interfacing all the required field and Central Monitoring Hub (CMH) equipments including spare requirements, licenses, tags, softwares etc complete as per specification and tender document. AI -28 Nos DI -12 Nos DO -04 Nos Serial Interface Ports: 04 Additional 20% spare (min 1) qty to be supplied over the above mentioned I/O quantity.Size of the PLC panel shall be optimized mode to accomodate all the signals in wall mounted panel only. Gas monitoring system at Central Monitoring Hub (CMH) as per tender documents. the scope also includes supply of all componennt, accessories required for complete the system and customization of reports as detailed in specifications and tender documents. | gas monitoring system |  | ai: 28 nos, di: 12 nos, do: 4 nos, serial interface ports: 4 | redundancy: dual redundant (parallel/hot standby), mounting: wall mounted, controller: programmable logic controller (plc), accessories: plc panels, input output modules, power supply units, relays with base, barriers, tbs (terminal blocks), dual ethernet ports per processor, serial interface modules, wirings, glands, plugs, other modules/hardwares, spare requirements, licenses, tags, software, optimized plc panel size, customization of reports, as per specification and tender document | 1 | Lot | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 2.2.2 ¦ Supply of weather proof Repeater panel at security room alongwith hooter & indication of Fault & LEL Alarm as per tender secifications. Panel to be hooked up with GMS at CMH. | weather proof repeater panel |  |  | location: security room, accessories: hooter, indication of fault & lel (lower explosive limit) alarm, connection: gms (gas monitoring system) at cmh (central monitoring hub), as per tender specifications | 1 | Nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 2.2.3 ¦ Supply of Flameproof/Ex-Proof cum weatherproof Repeater Panel alongwith Flameproof/Ex-proof Hooter & indication of Fault & LEL Alarm as per tender secifications. same to be hooked up with GMS at CR , All cabling & hardware included (Common repeater panel 1 no. in LPG Pump House room for TLD, LPG P/H & MSV's area gas detectors; 1 no for Filling shed & filled cylinder shed. ) | flameproof cum weatherproof repeater panel |  |  | accessories: flameproof/ex-proof hooter, indication of fault & lel (lower explosive limit) alarm, connection: gms (gas monitoring system) at cr (control room), cabling & hardware included, installation: lpg pump house room for tld, lpg p/h & msv's area gas detectors, filling shed & filled cylinder shed, as per tender specifications | 2 | Nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 2.2.4 ¦ Supply of sample gas cylinder for gas detectors sufficient to calibrate min. 21 nos. Gas detectors at a time. All asscessories needed for calibration are included in scope | sample gas cylinder for gas detectors |  | calibration capacity: minimum 21 gas detectors at a time | accessories: all needed for calibration included | 4 | Lot | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 3.1.1 ¦ The followings shall be considered for above - i) Servo Gauge with Display , Accuracy +-1mm LAB conditions,Density Measurement - 1 no. for each MSV | servo gauge with display |  |  | accuracy: ±1mm lab conditions, density measurement: included, quantity per msv: 1 | 3 | Nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 3.1.2 ¦ ii) Pressure Tx with 2 valve manifold for vapour pressure measurement Range 0 -15 Kg/CM2 - 2 nos. for each MSV | pressure transmitter with 2 valve manifold |  |  | measurement: vapour pressure, range: 0-15 kg/cm2, quantity per msv: 2 | 3 | Nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 3.1.3 ¦ iii) Radar Gauge with Display and - +/-1mm LAB condition with Display (Smart typeTank Side Indicator),Temperature sensor interface, Suitable for 6" Sch 10 Stilling pipe,1 Nos. SIL3 Relay Output & Analog Output - 1 no. for each MSV | radar gauge with display |  | stilling pipe suitability: 6" sch 10 | accuracy: ±1mm lab condition, display: smart type tank side indicator, temperature sensor interface: included, relay output: sil3, analog output: included, quantity per msv: 1 | 3 | Nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 3.1.4 ¦ iv) Vibration Fork type level switch with HH/LL set points - 1no. For each MSV | vibration fork type level switch |  |  | set points: hh/ll (high high/low low), quantity per msv: 1 | 3 | Nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 3.1.5 ¦ v) Smart type tank side indicator for Radar gauge at LPG pump house & interfacing with Radar gauge & Process PLC /safety PLC - 1 no. for each MSV | smart type tank side indicator for radar gauge |  |  | location: lpg pump house, interfacing: radar gauge, process plc (programmable logic controller), safety plc, quantity per msv: 1 | 3 | Nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 3.1.6 ¦ vi) Smart type tank side indicator for servo Gauge at LPG pump house & interfacing with servo gauge & Process PLC /safety PLC 1 no. for each MSV | smart type tank side indicator for servo gauge |  |  | location: lpg pump house, interfacing: servo gauge, process plc (programmable logic controller), safety plc, quantity per msv: 1 | 3 | Nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 3.1.7 ¦ vii) local indicator for pressure transmitter at LPG pump house - 1 no. for each MSV | local indicator for pressure transmitter |  |  | location: lpg pump house, quantity per msv: 1 | 6 | Nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 3.1.8 ¦ viii) Interface (Radar & Servo) | interface for radar and servo |  |  |  | 6 | Nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 3.1.9 ¦ ix) 9 Point temperature probe ( to be interface with Radar & Servo) | 9 point temperature probe |  | points: 9 | interface: radar & servo | 3 | Nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 2010-01-03 00:00:00 ¦ x) Redundant CIU/FCU with all interfacing , 2 nos of Modbus ports for Process PLC and 2 nos of Modbus ports for TFMS connectivity as required - 1 set | redundant ciu/fcu |  | modbus ports for process plc: 2, modbus ports for tfms: 2 | interfacing: all required, set: 1 | 1 | Set | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 2011-01-03 00:00:00 ¦ xii) Verification pin set | verification pin set |  |  |  | 20 | Nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 2012-01-03 00:00:00 ¦ xiii)TFMS Software supplied by bidder shall be same make as radar manufacturer and compatible with servo gauges. Licence shall be 12 nos min. | tfms software |  | licence: minimum 12 nos | make: same as radar manufacturer, compatibility: servo gauges | 1 | Lot | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 2013-01-03 00:00:00 ¦ xiv) Junction Boxes - | junction boxes |  |  |  | 4 | Nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 2014-01-03 00:00:00 ¦ xv) PDB Panel for TFMS. | pdb panel for tfms |  |  |  | 2 | Nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 2015-01-03 00:00:00 ¦ xvi) Communication cable, RTD cable, Power cable for TFMS | communication cable, rtd (resistance temperature detector) cable, power cable for tfms |  |  |  | 1 | Lot | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 2016-01-03 00:00:00 ¦ xvIi) Audio-Visual Annunciation Panel for annunciation at LPG Pump House, integrated with all Level Switches of MSVs (Single common Panel for all level switches) | audio-visual annunciation panel |  |  | location: lpg pump house, integration: all level switches of msvs (motorised shutoff valves), panel type: single common panel for all level switches | 1 | Nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 3.2 ¦ Tank Farm Management Servers - Commodity Grade, working on redundant (Primary and Secondary) hot standby mode with software, including backlit LED Monitor, key board and mouse. Supply , Installation, erection and commissioning of Operator Interface Console Computer (OIC) with 22" colour LED monitor, standard keyboard etc. complete as per specifications at Central Monitoring Hub (CMH). | tank farm management servers |  | monitor: 22" colour led | grade: commodity, redundancy: primary and secondary hot standby, software: included, accessories: backlit led monitor, keyboard, mouse, supply, installation, erection, commissioning: included, operator interface console computer (oic): included, location: central monitoring hub (cmh) | 1 | Lot | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 3.3 ¦ Other items for above - FLP Double compression type SS cable glands - As required , Adaptor Plate for Radar Gauge 4"/6",300# (SS316) for Radar tags - 1 no , Adaptor Plate for Temperature Probes 2",300# (SS316) - 4 nos , Fabricated Adaptor Chamber for Servo Gauge 2"X 4" X 6"300# (MOC CS) with pressure gauge, needle valve & pressure relief valve for Servo Tags , Studs as per SA 320 Gr. L7 & Bolts Nuts as per SA 194 Gr. 7 , Gaskets ( 6",4", 2") Spiral wound Metallic AISI 304, asbestos filled as per API 601 , fabricated cable for CIU & PC - As required ,fabrication of manifold for ionstllation of local indicator (radar /servo)- as required, Cables for communication of Servo , Radar / Servo / field Instruments to CIU (FRLS Cable for data communicatin) - As required , All software and Hardware shall be included as required , Bidder shall consider Process PLC & Tank Gauging system interface on redundant Modbus Communication , Any other item to achieve complete system to successful functioning and integration with other system as required are included. | other items for above |  |  | flp (flameproof) double compression type ss (stainless steel) cable glands: as required, adaptor plate for radar gauge: 4"/6", 300# (ss316), quantity: 1 no, adaptor plate for temperature probes: 2", 300# (ss316), quantity: 4 nos, fabricated adaptor chamber for servo gauge: 2"x4"x6" 300# (moc cs(carbon steel)), with pressure gauge, needle valve & pressure relief valve for servo tags, studs: sa 320 gr. l7, bolts nuts: sa 194 gr. 7, gaskets: (6",4",2") spiral wound metallic aisi 304, asbestos filled as per api 601, fabricated cable for ciu & pc: as required, fabrication of manifold for installation of local indicator (radar or servo): as required, cables for communication of servo, radar or servo or field instruments to ciu (frls (fire retardant low smoke) cable for data communication): as required, all software and hardware: included as required, process plc (programmable logic controller) & tank gauging system interface: redundant modbus communication, any other item: to achieve complete system to successful functioning and integration with other system as required | 1 | Lot | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 4.1.1 ¦ Supply of Flameproof cum weather proof smart type Grounding unit with one green indicating lamp and dual output for safety earthing of tank trucks, suitable for giving safety interlocking signal to PLC all complete as per specifications | smart type grounding unit |  |  | protection: flameproof, weatherproof, indicator: one green indicating lamp, output: dual, application: safety earthing of tank trucks, interlocking signal: plc (programmable logic controller), completeness: all as per specifications | 2 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 4.2.1 ¦ Supply of Dual redundant (Parallel/ Hot Standby) Programmable Logic Controller (Process PLC) along with PLC Panels, Marshalling Panels, Input Output modules, Power supply units, Relays with base, barriers, TBs, Dual Ethernet ports per processors, Serial Interface Modules, HMI console, wirings, glands, plugs, other modules/ hardwares required for interfacing all the required field and Central Monitoring Hub (CMH) equipments including spare requirements, licenses, tags, GUI, softwares etc complete as per specification and tender document. AI -25 Nos DI -96 Nos DO -80 Nos Serial Interface Ports: 28 Minimum 20% spare IO to be supplied as per tender specification. Count of PLC panel shall be optimized to accomodate all the signals in one panel only. | programmable logic controller | plc | ai: 25 nos, di: 96 nos, do: 80 nos, serial interface ports: 28, spare io: minimum 20% | redundancy: dual redundant (parallel/hot standby), panels: plc panels, marshalling panels, modules: input output, power supply units, relays with base, barriers, tbs (terminal blocks), dual ethernet ports per processor, serial interface modules, hmi (human machine interface) console, wirings, glands, plugs, other modules/hardwares: required for interfacing all required field and cmh (central monitoring hub) equipments, spare requirements: included, licenses: included, tags: included, gui: included, softwares: included, specification: as per tender document, plc panel count: optimized to accommodate all signals in one panel only | 1 | Lot | Table 1
| 4.2.2 ¦ Supply of Terminal Automation Software for Operator Stations with dongle/key, licenses, media, documentation etc., complete as per specifications / documents. TAS is the front end for all sub systems, hence below subsystems shall be interfaced with TAS for Monitoring, Logging, Reporting and Controls-Interlocks etc. System Interfaces: (Based on functional requirement for interfacing of the available sub systems at the Locations).System stated below with TAS & its commissioning with TAS for Alarms,archiving & events logging - SAP for TAS (TT & packed truck loading & unloading & sub systems covered in the work) - MCC, VFD, DG Sets, UPS etc. Interface - PLC & ESD ROV etc. - TFMS Interface including SAP - SAP-TFMS Interface - PAGA Interface - FAS Interface, - Fire Fighting System, - CCTV systems - DV Operational Panel - GMS Repeater Panel | terminal automation software |  |  | feature: operator stations, feature: dongle/key, feature: licenses, feature: media, feature: documentation, feature: system interfaces for monitoring, logging, reporting, controls-interlocks, feature: interface with SAP (systems, TT & packed truck loading & unloading), MCC (motor control center), VFD (variable frequency drive), DG sets (diesel generator sets), UPS (uninterruptible power supply), PLC (programmable logic controller), ESD (emergency shutdown), ROV (remote operated valve), TFMS (tank farm management system), PAGA (public address and general alarm), FAS (fire alarm system), fire fighting system, CCTV (closed circuit television) systems, DV operational panel, GMS (gas monitoring system) repeater panel, feature: alarms, archiving, events logging | 1 | Lot | Table 2
| 4.2.3 ¦ Supply of SCADA Software with 100% spare tags alongwith dongle/key, licenses, media, documentation etc. complete as per specifications / documents. | scada software | scada software |  | feature: 100% spare tags, feature: dongle/key, feature: licenses, feature: media, feature: documentation | 1 | Lot | Table 2
| 4.2.4 ¦ Supply of Operator Interface Console Computer (OIC)/EWS with 22" colour LED monitor , standard keyboard etc. complete as per specifications and tender drawing: -CAROUSAL -EWS/OWS -GMS -WEIGH BRIDGE -CYLINDER INVENTORY | operator interface console computer | oic | monitor size: 22 inch | feature: colour led monitor, feature: standard keyboard, feature: carousal, feature: ews (engineering workstation)/ows (operator workstation), feature: gms (gas monitoring system), feature: weigh bridge, feature: cylinder inventory | 5 | Nos. | Table 2
| 4.2.5 ¦ Supply of computer with 22" LED colour monitor, standard keyboard for SAP terminal for generating printing invoice, complete as per specifications. | computer |  | monitor size: 22 inch | feature: led colour monitor, feature: standard keyboard, feature: for sap terminal, feature: for generating printing invoice | 1 | Nos. | Table 2
| 4.2.6 ¦ Supply of 24 port Redundant Managed L2 Ethernet Switch (10/100/1000 MBPS) for connecting LED Display etc. complete as per specification. [Number of Port shall be as per site Requirment with 20% spare ports] | ethernet switch |  | number of ports: 24 | feature: redundant, feature: managed, feature: l2, feature: 10/100/1000 mbps, feature: for connecting led display, feature: 20% spare ports | 4 | Set | Table 2
| 4.2.7 ¦ Supply of color laser printer of approved make (latest model with added feature is also acceptable) complete as per specifications. A- 4 size @ Security Room. | color laser printer |  | paper size: a-4 | feature: approved make, feature: latest model, feature: added feature acceptable, location: security room | 1 | Nos. | Table 2
| 4.2.8 ¦ Supply of color laser printer of approved make (latest model with added feature is also acceptable) complete as per specifications. A- 3 size @ Central Monitoring Hub (CMH. | color laser printer |  | paper size: a-3 | feature: approved make, feature: latest model, feature: added feature acceptable, location: central monitoring hub (cmh) | 1 | Nos. | Table 2
| 4.2.9 ¦ Supply of heavy duty high speed dot matrix network printer with minimum 550 CPS at 10 CPI for invoice printing in 01 Nos Security room & 01 Nos in CHM Room, complete as per specifications and tender document. | dot matrix network printer |  |  | feature: heavy duty, feature: high speed, speed: minimum 550 cps (characters per second), pitch: 10 cpi (characters per inch), feature: for invoice printing, location: security room and chm room | 2 | Nos. | Table 2
| 2010-02-04 00:00:00 ¦ Supply of GSM modem for auto SMS for transmission after each stage of loading process for ESD as per specification. | gsm modem | gsm modem |  | feature: auto sms for transmission after each stage of loading process, feature: for esd (emergency shutdown) | 2 | Lot | Table 2
| 2011-02-04 00:00:00 ¦ Supply of 65" LED monitor of reputated make to be installed at driver rest room for display of safety videos & slogans. | led monitor |  | screen size: 65 inch | feature: reputed make, location: driver rest room, feature: for display of safety videos & slogans | 1 | Nos. | Table 2
| 2012-02-04 00:00:00 ¦ Supply of 55" LED monitor of reputated make to be installed at admistrative building Lobby area for plant & safety monitoring & instruction shall be in scope. Scope also includes interfacing with OIC, PAGA & TAS server including cable supply,laying and termination as needed. | led monitor |  | screen size: 55 inch | feature: reputed make, location: administrative building lobby area, feature: for plant & safety monitoring, feature: interfacing with oic (operator interface console), paga (public address and general alarm), tas (terminal automation software) server, feature: cable supply, laying and termination | 1 | Nos. | Table 2
| 2013-02-04 00:00:00 ¦ Supply of UPS Power Distribution Panel for powering PLC Panel, ESD System Panel, LRCS, OIC & EWS stations, TFMS System, TTES, Bay Instruments , Tank Farm Instruments , CCTV system , local control panels, Fire Detection System,fire alarm panels, Access control system, pnuematic, header line instruments and other TAS equipments where UPS power are required for smooth un- interrupted operation as per OEMs recommendation. Miscellaneous Instrumentation comprising of suitable MCCBs for Isolation etc to be provided. The panel shall be complete in all respects with necessary indication lamps for powering, necessary control wiring voltmeter, ammeter etc & as per specifications and tender document. Note: Minimum 20% spare power points to be made available for future use. | ups power distribution panel | ups power distribution panel |  | feature: for powering plc (programmable logic controller) panel, esd (emergency shutdown) system panel, lrcs, oic (operator interface console) & ews (engineering workstation) stations, tfms (tank farm management system) system, ttes, bay instruments, tank farm instruments, cctv (closed circuit television) system, local control panels, fire detection system, fire alarm panels, access control system, pneumatic, header line instruments, tas (terminal automation software) equipments, feature: for uninterrupted operation, feature: as per oem recommendation, feature: suitable mccbs (molded case circuit breakers) for isolation, feature: indication lamps, feature: control wiring, voltmeter, ammeter, feature: minimum 20% spare power points | 1 | Lot | Table 2
| 2014-02-04 00:00:00 ¦ Supply of Open desk operator consoles in CMH room: -CAROUSAL -SAP -ACS -EWS/OWS -TFMS -GMS -CCTV Supply of Open desk operator consoles in Security Room: -WEIGH BRIDGE -CYLINDER INVETORY -CCTV Each console will consists of nessary electrical wirring, 2 Nos. Sockets, 2 Nos. buttons, MCBs as required, LIght, Louvers & FAN number as required.) | open desk operator console |  |  | location: cmh (central monitoring hub) room, feature: carousal, sap (systems, applications, and products), acs (access control system), ews (engineering workstation)/ows (operator workstation), tfms (tank farm management system), gms (gas monitoring system), cctv (closed circuit television), location: security room, feature: weigh bridge, cylinder inventory, cctv, feature: electrical wiring, sockets: 2 nos., buttons: 2 nos., mcbs (miniature circuit breakers) as required, light, louvers, fan number as required | 10 | Nos. | Table 2
| 2015-02-04 00:00:00 ¦ Supply of Computer chairs (Make: Godrej or equivalent) - -03 Nos for Central Monitoring Hub (CMH) -02 Nos for Security Room | computer chair |  |  | manufacturer: godrej or equivalent, quantity for cmh: 3 nos., quantity for security room: 2 nos. | 5 | Nos. | Table 2
| 2016-02-04 00:00:00 ¦ Supply of Table (Make: Godrej or equivalent) for printer in security room/ Central Monitoring Hub (CMH) - 1 nos. for security room (main gate) & 1no.in CMH Room. | table |  |  | manufacturer: godrej or equivalent, location: security room (main gate), location: cmh (central monitoring hub) room, for printer | 2 | Nos. | Table 2
SECURITY GATES & TRUCK PARKING AREA | 5.1 ¦ Supply of electrically operated barrier gates(boom length to sute the site requirement, approx. 4 mtr.) with detection mechanism, manual bypass control with EX-proof motor, Exproof Traffic lamp & electronics etc. with configurable closing & opening time with sensors for detection of vehicle crossing the barrier etc. complete with supporting structure, fittings, cable supports complete as per specification. The gates are required for Security Entry and exit at licence area. 1 set. for packed truck Entry (4 m), 1 set for packed truck Exit (4 m). | electrically operated barrier gate |  | boom length: approx. 4 m | feature: detection mechanism, feature: manual bypass control, feature: ex-proof (explosion proof) motor, feature: exproof traffic lamp, feature: electronics, feature: configurable closing & opening time, feature: sensors for detection of vehicle crossing, feature: supporting structure, fittings, cable supports, location: security entry and exit at licence area, packed truck entry and exit | 2 | Set | Table 2
SECURITY GATES & TRUCK PARKING AREA | 5.2 ¦ Supply of electrically operated barrier gates(boom length to sute the site requirement, approx. 7 mtr.) with detection mechanism, manual bypass control with EX-proof motor, Exproof Traffic lamp & electronics etc. with configurable closing & opening time with sensors for detection of vehicle crossing the barrier etc. complete with supporting structure, fittings, cable supports complete as per specification. The gates are required for Security Entry and exit at licence area. 1 no. at bulk truck Entry/EXIT (7 m). | electrically operated barrier gate |  | boom length: approx. 7 m | feature: detection mechanism, feature: manual bypass control, feature: ex-proof (explosion proof) motor, feature: exproof traffic lamp, feature: electronics, feature: configurable closing & opening time, feature: sensors for detection of vehicle crossing, feature: supporting structure, fittings, cable supports, location: security entry and exit at licence area, bulk truck entry/exit | 1 | Set | Table 2
ACCESS CONTROL SYSTEM: | 6.1 ¦ Supply of Biometric fingerprint cum contactless type smart card reader (entry side, inside Central Monitoring Hub (CMH)) along with ectromagnetic door lock 600 lb, panic bar for fire exit doors, door position magnetic contact with buzzer as per specifications. One more magnetic latch along with push button shall be provided for emergency exit door, Main security room. | biometric fingerprint cum contactless type smart card reader |  |  | location: entry side, inside central monitoring hub (cmh), feature: electromagnetic door lock 600 lb, feature: panic bar for fire exit doors, feature: door position magnetic contact with buzzer, feature: magnetic latch with push button for emergency exit door, main security room | 1 | Nos. | Table 2
ACCESS CONTROL SYSTEM: | 6.2 ¦ Supply of Biometric fingerprint cum contactless type smart card reader (Outdoor) along with accessories including controller, software and programming kit as per specification. (Entry & Exit both side) | biometric fingerprint cum contactless type smart card reader |  |  | location: outdoor, feature: accessories including controller, software, programming kit, entry & exit both side | 3 | Nos. | Table 2
ACCESS CONTROL SYSTEM: | 6.3 ¦ Supply of Access Control System Software for setup, configuration, operation, events, history and archiving, alarm monitoring, recording, printing, time and attendance etc. complete as per specification and tender specifications including ESD input from PLC. | access control system software | acs software |  | feature: setup, configuration, operation, events, history, archiving, alarm monitoring, recording, printing, time and attendance, feature: esd (emergency shutdown) input from plc (programmable logic controller) | 1 | LS | Table 2
ACCESS CONTROL SYSTEM: | 6.4 ¦ Supply of Visitor Management Software complete as per specificationand tender specifications. | visitor management software |  |  |  | 1 | Set | Table 2
ACCESS CONTROL SYSTEM: | 6.5 ¦ Supply of ACS server computer with 22"color led monitor , standard keyboard, video camera loaded with ACS software for CMH room etc. complete as per specifications. | acs server computer | acs server computer | monitor size: 22 inch | feature: color led monitor, feature: standard keyboard, feature: video camera, feature: loaded with acs (access control system) software, location: cmh (central monitoring hub) room | 1 | Set | Table 2
ACCESS CONTROL SYSTEM: | 6.6 ¦ Supply of Client Computer of ACS / Visitor Management with 22"color led monitor, standardkeyboard, OS, Antivirus, video camera etc including installation of ACS software for ID badging & issuing of Visitor pass at security Room etc. complete as per specifications. | client computer |  | monitor size: 22 inch | feature: for acs (access control system) / visitor management, feature: color led monitor, feature: standard keyboard, feature: os (operating system), feature: antivirus, feature: video camera, feature: installation of acs software for id badging & issuing of visitor pass, location: security room | 1 | Set | Table 2
ACCESS CONTROL SYSTEM: | 6.7 ¦ Supply of the multizone door frame metallic detector as per specification. | multizone door frame metallic detector |  |  |  | 2 | Nos. | Table 2
ACCESS CONTROL SYSTEM: | 6.8 ¦ Supply of smart cards for Biometric fingerprint cum contactless type smart card reader as per the specification and tender document. | smart card |  |  | for biometric fingerprint cum contactless type smart card reader | 50 | Nos. | Table 2
ACCESS CONTROL SYSTEM: | 6.9 ¦ Supply of half height turnstile (tripod) as per specification. | half height turnstile |  |  | type: tripod | 3 | Nos. | Table 2
ACCESS CONTROL SYSTEM: | 6.1 ¦ Supply of SS 304 guiding rail as per specification. | guiding rail |  |  | material: ss 304 (stainless steel 304) | 30 | RM | Table 2
| 7.1 ¦ Supply of Static Weighing bridge (50 MT) located at near to Central Monitoring Hub (CMH) with load cells with all accessories (load cells, like cable from field to Central Monitoring Hub (CMH), JB, instruments, Jumbo Display for TT etc.) The rate shall include Static weighing bridges local marshalling / control panel . Vendor to provide Static Weighing bridge local marshalling/ control panel protocol free of cost to M/s IOCL. Supply & installation of Jumbo display for TTs is also included. | static weighing bridge |  | capacity: 50 MT | location: near to central monitoring hub (CMH), accessories: load cells, cable from field to central monitoring hub (CMH), JB (junction box), instruments, jumbo display for TT, includes: static weighing bridges local marshalling/control panel, protocol: local marshalling/control panel protocol free of cost to M/s IOCL, supply & installation: jumbo display for TTs included | 1 | Set | Table 2
FIELD INSTRUMENTS | 8.1.1 ¦ supply of bourdon type pressure gauge with range 0~ 25kg/cm2. Pressure gauge- IP-66 , SS316 bourdon,zero adjustment facility, micrometer screw type pointer, ±1% accuracy with all accessories. | pressure gauge |  | range: 0~25 kg/cm2 | type: bourdon, protection: IP-66, bourdon material: ss316 (stainless steel 316), feature: zero adjustment facility, pointer: micrometer screw type, accuracy: ±1%, accessories: all accessories | 4 | Nos. | Table 2
FIELD INSTRUMENTS | 8.1.2 ¦ supply of bourdon type pressure gauge with range 0~ 16kg/cm2. Pressure gauge- IP-66 , SS316 bourdon,zero adjustment facility, micrometer screw type pointer, ±1% accuracy with all accessories. | pressure gauge |  | range: 0~16 kg/cm2 | type: bourdon, protection: IP-66, bourdon material: ss316 (stainless steel 316), feature: zero adjustment facility, pointer: micrometer screw type, accuracy: ±1%, accessories: all accessories | 24 | Nos. | Table 2
FIELD INSTRUMENTS | 8.1.3 ¦ supply of bourdon type pressure gauge with range 0~ 10kg/cm2. Pressure gauge- IP-66 , SS316 bourdon,zero adjustment facility, micrometer screw type pointer, ±1% accuracy with all accessories. | pressure gauge |  | range: 0~10 kg/cm2 | type: bourdon, protection: IP-66, bourdon material: ss316 (stainless steel 316), feature: zero adjustment facility, pointer: micrometer screw type, accuracy: ±1%, accessories: all accessories | 21 | Nos. | Table 2
FIELD INSTRUMENTS | 8.1.4 ¦ supply of bourdon type pressure gauge with range 0~ 6kg/cm2. Pressure gauge- IP-66 , SS316 bourdon,zero adjustment facility, micrometer screw type pointer, ±1% accuracy with all accessories. | pressure gauge |  | range: 0~6 kg/cm2 | type: bourdon, protection: IP-66, bourdon material: ss316 (stainless steel 316), feature: zero adjustment facility, pointer: micrometer screw type, accuracy: ±1%, accessories: all accessories | 4 | Nos. | Table 2
FIELD INSTRUMENTS | 8.2.1 ¦ Supply of presssure transmitter with calibration range 0~ 25 kg/cm2. Pressure & Differential pressure transmitter | pressure transmitter |  | calibration range: 0~25 kg/cm2 |  | 6 | Nos. | Table 2
FIELD INSTRUMENTS | 8.3.1 ¦ Supply of tempreture transmitter with calibration range 0~ 100°C alonge with tempreture elements & cable from element to transmitter. Tempreture Transmitter | temperature transmitter |  | calibration range: 0~100°C | accessories: temperature elements & cable from element to transmitter | 3 | Nos. | Table 2
FIELD INSTRUMENTS | 8.4.1 ¦ Supply of level gauge. level gauge- Description:-Transperent Type,IP-66, C To C distance: HOLD, SS float, Vent & Drain Plug: 3/4 " NPT , Flange:1 1/2" 300# RF, Zone-1 IIA/IIB | level gauge |  | vent & drain plug: 3/4" NPT, flange: 1 1/2" 300# RF, c to c distance: HOLD | type: transparent, protection: IP-66, float material: ss (stainless steel), zone: 1 IIA/IIB | 2 | Nos. | Table 2
FIELD INSTRUMENTS | 8.5.1 ¦ Supply of tempreture gauge with range 0 ~ 100°C. Temprature gauge: all angle type, 1.5" 300# RF well connection, 1/2" NPT gauge,150mm dial size, SS316 material, shatterproof glass | temperature gauge |  | range: 0~100°C, well connection: 1.5" 300# RF, gauge connection: 1/2" NPT, dial size: 150mm | type: all angle, material: ss316 (stainless steel 316), glass: shatterproof | 5 | Nos. | Table 2
FIELD INSTRUMENTS | 8.6.1. ¦ Supply of Electromagnetic Flow meter with range 0 ~ 50 m3/hr. Electromagnetic Flow meter: For water line of 100mm. | electromagnetic flow meter |  | range: 0~50 m3/hr, water line: 100mm |  | 1 | Nos. | Table 2
FIELD INSTRUMENTS | 8.8.1 ¦ Supply of Magnetic Flow Switch with range 0 ~ 15m3/hr. Flow Switch: For Water application and line size is 25mm. | magnetic flow switch |  | range: 0~15 m3/hr, line size: 25mm | application: water | 4 | Nos. | Table 2
FIELD INSTRUMENTS | 8.8.1 ¦ Supply of Float type level switch with range of 0 ~ 3 mtr. Level Switch: Level Switch for waste water in plant Sumps. | float type level switch |  | range: 0~3 mtr | application: waste water in plant sumps | 3 | Nos. | Table 2
JUNCTION BOXES WITH SPARES ACCESSORIES, ALL REQUIRED COMPONENTS AS PER ITB SPECIFICATIONS AND DOCUMENTS/ DRAWINGS INCLUDING DOCUMENTATION, TECHNICAL DISCUSSIONS, CORRESPONDENCES, TESTING, INSPECTION, PACKING, TRANSPORTATION TO SITE, GUARANTEE ETC. | 9.1.1 ¦ Supply of Signal Junction Box (BLUE) : Flame proof /ex-proof, Die cast AL LM6 body, 12 inlet+2 outlet as per specification suitable for hazardous area of zone 1, group IIA/IIB, T3 ,having PESO/CMIFR approval. It shall be complete in all respect. Accessories like certified flameproof /exproof SS316 double compression cable glands with PVC shrouds & SS plugs for excess entries, SS 316 engraved tag plate, mounting clamp & SS 316 fasteners. Complete as per specifications / documents. Junction for Field Instruments | signal junction box |  | inlet: 12, outlet: 2 | color: blue, flame proof: yes, ex-proof: yes, body material: die cast AL LM6 (aluminium LM6), area suitability: hazardous area of zone 1, group IIA/IIB, temperature class: T3, approval: PESO/CMIFR, accessories: certified flameproof/exproof SS316 (stainless steel 316) double compression cable glands with PVC shrouds & SS plugs for excess entries, SS 316 engraved tag plate, mounting clamp & SS 316 fasteners, specification: as per specifications/documents | 2 | Nos. | Table 2
JUNCTION BOXES WITH SPARES ACCESSORIES, ALL REQUIRED COMPONENTS AS PER ITB SPECIFICATIONS AND DOCUMENTS/ DRAWINGS INCLUDING DOCUMENTATION, TECHNICAL DISCUSSIONS, CORRESPONDENCES, TESTING, INSPECTION, PACKING, TRANSPORTATION TO SITE, GUARANTEE ETC. | 9.1.2 ¦ Supply of Signal Junction Box (BLUE) : Flame proof /ex-proof, Die cast AL LM6 body, 6 inlet+2 outlet as per specification suitable for hazardous area of zone 1, group IIA/IIB, T3 ,having PESO/CMIFR approval. It shall be complete in all respect. Accessories like certified flameproof /exproof SS316 double compression cable glands with PVC shrouds & SS plugs for excess entries, SS 316 engraved tag plate, mounting clamp & SS 316 fasteners. Complete as per specifications / documents. Junction for Field Instruments | signal junction box |  | inlet: 6, outlet: 2 | color: blue, flame proof: yes, ex-proof: yes, body material: die cast AL LM6 (aluminium LM6), area suitability: hazardous area of zone 1, group IIA/IIB, temperature class: T3, approval: PESO/CMIFR, accessories: certified flameproof/exproof SS316 (stainless steel 316) double compression cable glands with PVC shrouds & SS plugs for excess entries, SS 316 engraved tag plate, mounting clamp & SS 316 fasteners, specification: as per specifications/documents | 2 | Nos. | Table 2
JUNCTION BOXES WITH SPARES ACCESSORIES, ALL REQUIRED COMPONENTS AS PER ITB SPECIFICATIONS AND DOCUMENTS/ DRAWINGS INCLUDING DOCUMENTATION, TECHNICAL DISCUSSIONS, CORRESPONDENCES, TESTING, INSPECTION, PACKING, TRANSPORTATION TO SITE, GUARANTEE ETC. | 9.1.3 ¦ Control Junction Box(GREY):Flame proof /ex-proof, Die cast AL LM6 body, 12 inlet+2 outlet as per specification suitable for hazardous area of zone 1, group IIA/IIB, T3 or better having PESO/CMIFR approval. It shall be complete in all respect. Accessories like certified flameproof /exproof SS316 double compression cable glands with PVC shrouds & SS plugs for excess entries, SS 316 engraved tag plate, mounting clamp & SS 316 fasteners. Complete as per specifications / documents. Junction for Field Instruments | control junction box |  | inlet: 12, outlet: 2 | color: grey, flame proof: yes, ex-proof: yes, body material: die cast AL LM6 (aluminium LM6), area suitability: hazardous area of zone 1, group IIA/IIB, temperature class: T3 or better, approval: PESO/CMIFR, accessories: certified flameproof/exproof SS316 (stainless steel 316) double compression cable glands with PVC shrouds & SS plugs for excess entries, SS 316 engraved tag plate, mounting clamp & SS 316 fasteners, specification: as per specifications/documents | 6 | Nos. | Table 2
JUNCTION BOXES WITH SPARES ACCESSORIES, ALL REQUIRED COMPONENTS AS PER ITB SPECIFICATIONS AND DOCUMENTS/ DRAWINGS INCLUDING DOCUMENTATION, TECHNICAL DISCUSSIONS, CORRESPONDENCES, TESTING, INSPECTION, PACKING, TRANSPORTATION TO SITE, GUARANTEE ETC. | 9.1.4 ¦ Supply of Power Junction Box (GREY): Flame proof /ex-proof, Die cast AL LM6 body, 12 inlet+2 outlet as per specification suitable for hazardous area of zone 1, group IIA/IIB, T3 or better having PESO/CMIFR approval. It shall be complete in all respect. Accessories like certified double compression cable glands with PVC shrouds & plugs for excess entries, SS 316 engraved tag plate, mounting clamp & SS 316 fasteners. Complete as per specifications / documents. Junction for Field Instruments | power junction box |  | inlet: 12, outlet: 2 | color: grey, flame proof: yes, ex-proof: yes, body material: die cast AL LM6 (aluminium LM6), area suitability: hazardous area of zone 1, group IIA/IIB, temperature class: T3 or better, approval: PESO/CMIFR, accessories: certified double compression cable glands with PVC shrouds & plugs for excess entries, SS 316 engraved tag plate, mounting clamp & SS 316 fasteners, specification: as per specifications/documents | 7 | Nos. | Table 2
JUNCTION BOXES WITH SPARES ACCESSORIES, ALL REQUIRED COMPONENTS AS PER ITB SPECIFICATIONS AND DOCUMENTS/ DRAWINGS INCLUDING DOCUMENTATION, TECHNICAL DISCUSSIONS, CORRESPONDENCES, TESTING, INSPECTION, PACKING, TRANSPORTATION TO SITE, GUARANTEE ETC. | 9.1.5 ¦ Junction Boxes Ex proof-EExd (JBP ) Terminals for LINE, NEUTRAL, shall be isolation breakers : All terminals suitable for 240 V AC , Exd type 12 nos. ½” NPTF cable entries at sides + 2 Nos. cable entries at bottom ; complete with suitable size double compressor SS316 Flame proof Glands with Check Nuts & gaskets. Junction for Field Instruments | junction box |  | cable entries at sides: 12 nos. ½” NPTF, cable entries at bottom: 2 nos. | ex proof: EExd, type: JBP, terminals: for line, neutral, feature: isolation breakers, voltage: 240 V AC, type: Exd, accessories: suitable size double compressor SS316 (stainless steel 316) flame proof glands with check nuts & gaskets | 1 | Nos. | Table 2
JUNCTION BOXES WITH SPARES ACCESSORIES, ALL REQUIRED COMPONENTS AS PER ITB SPECIFICATIONS AND DOCUMENTS/ DRAWINGS INCLUDING DOCUMENTATION, TECHNICAL DISCUSSIONS, CORRESPONDENCES, TESTING, INSPECTION, PACKING, TRANSPORTATION TO SITE, GUARANTEE ETC.; Junction box for DELUGE VALVE instruments & GAS DETECTORS | 9.2.1 ¦ Supply of Signal Junction Box (BLUE) : Flame proof /ex-proof, Die cast AL LM6 body, 12 inlet+2 outlet as per specification suitable for hazardous area of zone 1, group IIA/IIB, T3 ,having PESO/CMIFR approval. It shall be complete in all respect. Accessories like certified flameproof /exproof SS316 double compression cable glands with PVC shrouds & SS plugs for excess entries, SS 316 engraved tag plate, mounting clamp & SS 316 fasteners. Complete as per specifications / documents. | signal junction box |  | inlet: 12, outlet: 2 | color: blue, flame proof: yes, ex-proof: yes, body material: die cast AL LM6 (aluminium LM6), area suitability: hazardous area of zone 1, group IIA/IIB, temperature class: T3, approval: PESO/CMIFR (Petroleum and Explosives Safety Organisation/Central Mining Research Institute Fire Research), accessories: certified flameproof/exproof SS316 (stainless steel 316) double compression cable glands with PVC shrouds & SS plugs for excess entries, SS 316 engraved tag plate, mounting clamp & SS 316 fasteners, specification: as per specifications/documents | 3 | Nos. | Table 2
JUNCTION BOXES WITH SPARES ACCESSORIES, ALL REQUIRED COMPONENTS AS PER ITB SPECIFICATIONS AND DOCUMENTS/ DRAWINGS INCLUDING DOCUMENTATION, TECHNICAL DISCUSSIONS, CORRESPONDENCES, TESTING, INSPECTION, PACKING, TRANSPORTATION TO SITE, GUARANTEE ETC.; Junction box for DELUGE VALVE instruments & GAS DETECTORS | 9.2.2 ¦ Control Junction Box(GREY):Flame proof /ex-proof, Die cast AL LM6 body, 12 inlet+2 outlet as per specification suitable for hazardous area of zone 1, group IIA/IIB, T3 or better having PESO/CMIFR approval. It shall be complete in all respect. Accessories like certified flameproof /exproof SS316 double compression cable glands with PVC shrouds & SS plugs for excess entries, SS 316 engraved tag plate, mounting clamp & SS 316 fasteners. Complete as per specifications / documents. | control junction box |  | inlet: 12, outlet: 2 | color: grey, flame proof: yes, ex-proof: yes, body material: die cast AL LM6 (aluminium LM6), area suitability: hazardous area of zone 1, group IIA/IIB, temperature class: T3 or better, approval: PESO/CMIFR (Petroleum and Explosives Safety Organisation/Central Mining Research Institute Fire Research), accessories: certified flameproof/exproof SS316 (stainless steel 316) double compression cable glands with PVC shrouds & SS plugs for excess entries, SS 316 engraved tag plate, mounting clamp & SS 316 fasteners, specification: as per specifications/documents | 2 | Nos. | Table 2
JUNCTION BOXES WITH SPARES ACCESSORIES, ALL REQUIRED COMPONENTS AS PER ITB SPECIFICATIONS AND DOCUMENTS/ DRAWINGS INCLUDING DOCUMENTATION, TECHNICAL DISCUSSIONS, CORRESPONDENCES, TESTING, INSPECTION, PACKING, TRANSPORTATION TO SITE, GUARANTEE ETC.; Junction box for DELUGE VALVE instruments & GAS DETECTORS | 9.2.3 ¦ Supply of Junction Box(blue) for spot type IR gas detectors:Flame proof /ex-proof, Die cast AL LM6 body, 12 inlet+2 outlet as per specification suitable for hazardous area of zone 1, group IIA/IIB, T3 or better having PESO/CMIFR approval. It shall be complete in all respect. Accessories like certified flameproof /exproof SS316 double compression cable glands with PVC shrouds & SS plugs for excess entries, SS 316 engraved tag plate, mounting clamp & SS 316 fasteners. Complete as per specifications / documents. | junction box |  | inlet: 12, outlet: 2 | color: blue, application: for spot type IR (infrared) gas detectors, flame proof: yes, ex-proof: yes, body material: die cast AL LM6 (aluminium LM6), area suitability: hazardous area of zone 1, group IIA/IIB, temperature class: T3 or better, approval: PESO/CMIFR (Petroleum and Explosives Safety Organisation/Central Mining Research Institute Fire Research), accessories: certified flameproof/exproof SS316 (stainless steel 316) double compression cable glands with PVC shrouds & SS plugs for excess entries, SS 316 engraved tag plate, mounting clamp & SS 316 fasteners, specification: as per specifications/documents | 4 | Nos. | Table 2
ESD PUSH BUTTON STATION FOR ESD-ROV | 10.1 ¦ Supply of EX-proof/flameproof ESD Push button station with all accessories mounted at local nearby of ROV (as per IOCL instruction) for Emergecy shut down of ROV . 1 PB station shall be used for 1 no. ESD ROV closed only. | esd push button station |  |  | flame proof: yes, ex-proof: yes, mounting: at local nearby of ROV (remotely operated valve) as per IOCL (Indian Oil Corporation Limited) instruction, application: for emergency shut down of ROV, accessories: all accessories included, usage: 1 push button station for 1 ESD ROV closed only | 10 | Nos. | Table 2
INSTRUMENT CABLES | 11.01 ¦ 01P X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , OVERALL SHIELDED , SIGNAL CABLE | signal cable |  | core: 1 pair, cross section: 1.5 mm2 | insulation: PVC (polyvinyl chloride), armoured: yes, sheath: FRLS (flame retardant low smoke) PVC, shielding: overall shielded | 1101.9 | Mtrs | Table 2
INSTRUMENT CABLES | 11.02 ¦ 01T X 2.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , OVERALL SHIELDED , SIGNAL CABLE | signal cable |  | core: 1 triad, cross section: 2.5 mm2 | insulation: PVC (polyvinyl chloride), armoured: yes, sheath: FRLS (flame retardant low smoke) PVC, shielding: overall shielded | 571.2 | Mtrs | Table 2
INSTRUMENT CABLES | 11.03 ¦ 02C X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , CONTROL CABLE | control cable |  | core: 2 core, cross section: 1.5 mm2 | insulation: PVC (polyvinyl chloride), armoured: yes, sheath: FRLS (flame retardant low smoke) PVC | 7286.6 | Mtrs | Table 2
INSTRUMENT CABLES | 11.04 ¦ 02P X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , OVERALL SHIELDED , SIGNAL CABLE | signal cable |  | core: 2 pair, cross section: 1.5 mm2 | insulation: PVC (polyvinyl chloride), armoured: yes, sheath: FRLS (flame retardant low smoke) PVC, shielding: overall shielded | 538.02 | Mtrs | Table 2
INSTRUMENT CABLES | 11.05 ¦ 03C X 2.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , CONTROL CABLE | control cable |  | core: 3 core, cross section: 2.5 mm2 | insulation: PVC (polyvinyl chloride), armoured: yes, sheath: FRLS (flame retardant low smoke) PVC | 3625 | Mtrs | Table 2
INSTRUMENT CABLES | 11.06 ¦ 03C X 4.0 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , CONTROL CABLE | control cable |  | core: 3 core, cross section: 4.0 mm2 | insulation: PVC (polyvinyl chloride), armoured: yes, sheath: FRLS (flame retardant low smoke) PVC | 250 | Mtrs | Table 2
INSTRUMENT CABLES | 11.07 ¦ 03C X 6.0 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , CONTROL CABLE | control cable |  | core: 3 core, cross section: 6.0 mm2 | insulation: PVC (polyvinyl chloride), armoured: yes, sheath: FRLS (flame retardant low smoke) PVC | 200 | Mtrs | Table 2
INSTRUMENT CABLES | 11.08 ¦ 04C X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , CONTROL CABLE | control cable |  | core: 4 core, cross section: 1.5 mm2 | insulation: PVC (polyvinyl chloride), armoured: yes, sheath: FRLS (flame retardant low smoke) PVC | 1669.44 | Mtrs | Table 2
INSTRUMENT CABLES | 11.09 ¦ 04C X 2.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , CONTROL CABLE | control cable |  | core: 4 core, cross section: 2.5 mm2 | insulation: PVC (polyvinyl chloride), armoured: yes, sheath: FRLS (flame retardant low smoke) PVC | 1094.46 | Mtrs | Table 2
INSTRUMENT CABLES | 11.1 ¦ 04P X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , OVERALL SHIELDED , SIGNAL CABLE | signal cable |  | core: 4 pair, cross section: 1.5 mm2 | insulation: PVC (polyvinyl chloride), armoured: yes, sheath: FRLS (flame retardant low smoke) PVC, shielding: overall shielded | 350 | Mtrs | Table 2
INSTRUMENT CABLES | 11.11 ¦ 05C X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , CONTROL CABLE | control cable |  | core: 5 core, cross section: 1.5 mm2 | insulation: PVC (polyvinyl chloride), armoured: yes, sheath: FRLS (flame retardant low smoke) PVC | 1496.34 | Mtrs | Table 2
INSTRUMENT CABLES | 11.12 ¦ 06P X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , OVERALL SHIELDED , SIGNAL CABLE | signal cable |  | core: 6 pair, cross section: 1.5 mm2 | insulation: PVC (polyvinyl chloride), armoured: yes, sheath: FRLS (flame retardant low smoke) PVC, shielding: overall shielded | 539.58 | Mtrs | Table 2
INSTRUMENT CABLES | 11.13 ¦ 06T X 2.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , OVERALL SHIELDED , SIGNAL CABLE | signal cable |  | core: 6 triad, cross section: 2.5 mm2 | insulation: PVC (polyvinyl chloride), armoured: yes, sheath: FRLS (flame retardant low smoke) PVC, shielding: overall shielded | 211.14 | Mtrs | Table 2
INSTRUMENT CABLES | 11.14 ¦ 12C X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , CONTROL CABLE | control cable |  | core: 12 core, cross section: 1.5 mm2 | insulation: PVC (polyvinyl chloride), armoured: yes, sheath: FRLS (flame retardant low smoke) PVC | 1644.62 | Mtrs | Table 2
INSTRUMENT CABLES | 11.15 ¦ 12C X 2.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , CONTROL CABLE | control cable |  | core: 12 core, cross section: 2.5 mm2 | insulation: PVC (polyvinyl chloride), armoured: yes, sheath: FRLS (flame retardant low smoke) PVC | 211.14 | Mtrs | Table 2
INSTRUMENT CABLES | 11.16 ¦ 12P X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , OVERALL SHIELDED , SIGNAL CABLE | signal cable |  | core: 12 pair, cross section: 1.5 mm2 | insulation: PVC (polyvinyl chloride), armoured: yes, sheath: FRLS (flame retardant low smoke) PVC, shielding: overall shielded | 234.6 | Mtrs | Table 2
INSTRUMENT CABLES | 11.17 ¦ 10T X 2.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , OVERALL SHIELDED , SIGNAL CABLE | signal cable |  | core: 10 triad, cross section: 2.5 mm2 | insulation: PVC (polyvinyl chloride), armoured: yes, sheath: FRLS (flame retardant low smoke) PVC, shielding: overall shielded | 758.88 | Mtrs | Table 2
INSTRUMENT CABLES | 11.18 ¦ 24C X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , CONTROL CABLE | control cable |  | core: 24 core, cross section: 1.5 mm2 | insulation: PVC (polyvinyl chloride), armoured: yes, sheath: FRLS (flame retardant low smoke) PVC | 1149.54 | Mtrs | Table 2
INSTRUMENT CABLES | 11.19 ¦ 24C X 2.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , CONTROL CABLE | control cable |  | core: 24 core, cross section: 2.5 mm2 | insulation: PVC (polyvinyl chloride), armoured: yes, sheath: FRLS (flame retardant low smoke) PVC | 744.6 | Mtrs | Table 2
INSTRUMENT CABLES | 11.2 ¦ 36C X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , CONTROL CABLE | control cable |  | core: 36 core, cross section: 1.5 mm2 | insulation: PVC (polyvinyl chloride), armoured: yes, sheath: FRLS (flame retardant low smoke) PVC | 298.86 | Mtrs | Table 2
INSTRUMENT CABLES | 11.21 ¦ RS485 CABLE | rs485 cable | rs485 cable |  |  | 4279.92 | Mtrs | Table 2
INSTRUMENT CABLES | 11.22 ¦ Supply of Cat 6 cable.accessories like lugs, adapter, blank plate & patch cord etc as required is included | cat 6 cable |  |  | accessories: lugs, adapter, blank plate & patch cord etc as required is included | 590 | Mtrs | Table 2
INSTRUMENT CABLES | 11.23 ¦ Supply of 24 core OF armod cable in HDPE duct .OFC accessories like 12/24 port LIU, splice tray, loaded adapter, blank plate & patch cord etc as required is included | ofc cable | ofc cable | core: 24 core | armoured: yes, duct: HDPE (high density polyethylene), accessories: 12/24 port LIU (line interface unit), splice tray, loaded adapter, blank plate & patch cord etc as required is included | 2205 | Mtrs | Table 2
INSTRUMENT CABLES | 11.24 ¦ 04P X 0.8 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , OVERALL SHIELDED , SIGNAL CABLE | signal cable |  | core: 4 pair, cross section: 0.8 mm2 | insulation: PVC (polyvinyl chloride), armoured: yes, sheath: FRLS (flame retardant low smoke) PVC, shielding: overall shielded | 2010 | Mtrs | Table 2
FIELD INSTRUMENTS | 2030-01-12 00:00:00 ¦ GASKET -1/2" -150# -SS316 GRAPHITE WITH SPIRAL WOUND | gasket |  | diameter: 1/2" | pressure rating: 150#, material: SS316 (stainless steel 316), filler: graphite, type: spiral wound | 21 | Nos | Table 2
FIELD INSTRUMENTS | 2031-01-12 00:00:00 ¦ GASKET -1/2" -150# -SS316 GRAPHITE WITH SPIRAL WOUND | gasket |  | diameter: 1/2" | pressure rating: 150#, material: SS316 (stainless steel 316), filler: graphite, type: spiral wound | 21 | Nos | Table 2
FIELD INSTRUMENTS | 2032-01-12 00:00:00 ¦ GASKET -4"D -300# -SS316 GRAPHITE WITH SPIRAL WOUND | gasket |  | diameter: 4" | pressure rating: 300#, material: SS316 (stainless steel 316), filler: graphite, type: spiral wound | 3 | Nos | Table 2
FIELD INSTRUMENTS | 2033-01-12 00:00:00 ¦ GASKET -2"D -150# -SS316 GRAPHITE WITH SPIRAL WOUND | gasket |  | diameter: 2" | pressure rating: 150#, material: SS316 (stainless steel 316), filler: graphite, type: spiral wound | 3 | Nos | Table 2
FIELD INSTRUMENTS | 2034-01-12 00:00:00 ¦ GASKET -6"D -300# -SS316 GRAPHITE WITH SPIRAL WOUND | gasket |  | diameter: 6" | pressure rating: 300#, material: SS316 (stainless steel 316), filler: graphite, type: spiral wound | 9 | Nos | Table 2
FIELD INSTRUMENTS | 2035-01-12 00:00:00 ¦ GASKET -2"D -150# -SS316 GRAPHITE WITH SPIRAL WOUND | gasket |  | diameter: 2" | pressure rating: 150#, material: SS316 (stainless steel 316), filler: graphite, type: spiral wound | 3 | Nos | Table 2
FIELD INSTRUMENTS | 2036-01-12 00:00:00 ¦ STUDS AND NUTS -1/2" x 75MM -300# -SS316 GRAPHITE WITH SPIRAL WOUND | studs and nuts |  | diameter: 1/2", length: 75 mm | pressure rating: 300#, material: SS316 (stainless steel 316), filler: graphite, type: spiral wound | 84 | Nos | Table 2
FIELD INSTRUMENTS | 2037-01-12 00:00:00 ¦ STUDS AND NUTS -1/2" x 75MM -300# -SS316 GRAPHITE WITH SPIRAL WOUND | studs and nuts |  | diameter: 1/2", length: 75 mm | pressure rating: 300#, material: SS316 (stainless steel 316), filler: graphite, type: spiral wound | 84 | Nos | Table 2
FIELD INSTRUMENTS | 12.2.1 ¦ Supply FRP canopy as per drawing attached with SOR for pressure transmitters, pressure switch & level switch (suitable for vertical as well as horizontal mounting) | frp canopy |  |  | feature: as per drawing attached with SOR for pressure transmitters, pressure switch & level switch (suitable for vertical as well as horizontal mounting) | 6 | Nos | Table 2
FIELD INSTRUMENTS | 12.2.2 ¦ Supply of Maintenance Free CPRI approved Earth Pit (Ashlok /Equivalent make) of minimum 3.8 mtr length T45 model/equivalent safe earthing electrode with Pipe-in-pipe technology consisting of two mild steel pipes one inside the other, hot dip galvanized (80-100 microns), filled with high conductive & corrosion resistance crystalline mixture and backfilling compound around electrode, 25 mm dia G.I. watering pipe with funnel, test link, brick masonry earth pit including plastering in CM 1:4, 600x600 mm C.I. Manhole chamber etc. Equivalent make shall be approved by client / consultants. Procedure recommended by chemical earth supplier and IS code to be finally adopted. Item also includes provision of earth station flags with pit nos and date of inspection and the next due date of inspection. Job also includes provision of test certificate of earthing station from a licensed electrician as per the format of the Corporation | earth pit |  | length: minimum 3.8 mtr, watering pipe diameter: 25 mm, manhole chamber: 600x600 mm | type: maintenance free, approval: CPRI (central power research institute), make: Ashlok or equivalent, model: T45 or equivalent, technology: pipe-in-pipe, material: mild steel (two pipes, one inside the other), coating: hot dip galvanized (80-100 microns), filling: high conductive & corrosion resistance crystalline mixture and backfilling compound, accessories: G.I. watering pipe with funnel, test link, brick masonry earth pit including plastering in CM 1:4, C.I. manhole chamber, earth station flags with pit nos and date of inspection and next due date, certificate: test certificate of earthing station from licensed electrician, standard: IS code (indian standard), approval: client/consultants | 1 | Nos | Table 2
FIELD INSTRUMENTS | 12.3 ¦ SUPPLY & ERECTION OF STRUCTURALS STEEL: Structural steel work riveted,bolted or welded in built up sections, trusses & framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete: | structural steel work |  |  | feature: riveted, bolted or welded in built up sections, trusses & framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete | 2 | MT | Table 2
FIELD INSTRUMENTS | 13.01 ¦ TONG TESTER | tong tester |  |  |  | 1 | Nos | Table 2
FIELD INSTRUMENTS | 13.02 ¦ MEGGER TESTER | megger tester |  |  |  | 1 | Nos | Table 2
FIELD INSTRUMENTS | 13.03 ¦ EARTH TESTER | earth tester |  |  |  | 1 | Nos | Table 2
FIELD INSTRUMENTS | 13.04 ¦ PRESSURE GAUGE & TRANSMITTER TEST BENCH SET WITH OIL + 2 LITER OIL AS SPARE | pressure gauge and transmitter test bench set |  |  | accessories: oil + 2 liter oil as spare | 1 | Nos | Table 2
FIELD INSTRUMENTS | 13.05 ¦ HAND HELD CALIBRATOR /HART CALIBRATOR (UNIVERSAL TYPE ) | hand held calibrator or hart calibrator | hart calibrator |  | type: universal | 1 | Nos | Table 2
FIELD INSTRUMENTS | 13.06 ¦ TEMPRETURE BATH SET FOR RANGE 0~ 200°C | temperature bath set |  | range: 0~200°C |  | 1 | Nos | Table 2
FIELD INSTRUMENTS | 13.07 ¦ VIBRATION METER | vibration meter |  |  |  | 1 | Nos | Table 2
FIELD INSTRUMENTS | 13.08 ¦ GAS SENSOR CALIBRATOR CYLINDER | gas sensor calibrator cylinder |  |  |  | 1 | Set | Table 2
FIELD INSTRUMENTS | 13.09 ¦ LEL METER , IR TYPE , 0~100 VOL% , RESPONSE TIME - BELOW 20 SEC. | lel meter |  | range: 0~100 VOL% | type: IR, response time: below 20 sec. | 1 | Nos | Table 2
FIELD INSTRUMENTS | 13.1 ¦ OXYGEN METER | oxygen meter |  |  |  | 1 | Nos | Table 2
FIELD INSTRUMENTS | 13.11 ¦ ELCOMETER | elcometer |  |  |  | 1 | Nos | Table 2
FIELD INSTRUMENTS | 13.12 ¦ DIGITAL LUX METER | digital lux meter |  |  |  | 1 | Nos | Table 2
CCTV SYSTEM | 14.1.1 ¦ Supply of UL listed HD IP Fixed Dome Camera with IR and MFZ (Motorized Focus & Zoom) Lens 2MP, 1/3'' or better Prograsive scan Cmos sensor , 32GB SD card, multi streaming , H.264, PoE, DC12V/AC24V, IP 66 & IK 10 rated ,ONVIF with with features like Camera tampering, Network loss detectionand all accessories etc. complete as required. for weather proof application including all the wall Mount accessories & pole mounting or accesories as per site requirement. -Wall Mounting Quantity - 12 Nos -Pole Mounting Camera Quantity - 01 Nos Camera shall be installed under driver rest roo, cylinder counting, central monitoring hub room, security path, bulk truck safety, PMCC Panel Room, Fire water pump house, Entrance of admin office, canteen, store, incharge room, training hall/conference room. Below mentioned items to be provide along with cameras: -Surge Protectors -Mounting Bracket same make as Camera | hd ip fixed dome camera |  | lens: 2MP, sensor: 1/3'' or better, sd card: 32GB | listing: UL (underwriters laboratories), type: IR and MFZ (motorized focus & zoom), sensor: progressive scan CMOS, streaming: multi streaming, compression: H.264, power: PoE, DC12V/AC24V, rating: IP66, IK10, protocol: ONVIF, features: camera tampering, network loss detection, weather proof, accessories: wall mount accessories, pole mounting accessories, surge protectors, mounting bracket (same make as camera) | 13 | Nos | Table 2
CCTV SYSTEM | 14.1.2 ¦ Supply of UL listed IP Fixed Bullet Camera with MFZ (Motorized Focus Zoom) lens of 8MP, 4k resolution , better Progresive scan CMOS sensor, 32GB SD card, WDR, multi streaming , H.264, PoE, DC12V/AC24V, IP 67 ,ONVIF with Pole Mount accessories or accesory as per site requirement Cameras shall be installed under licensed entry & exit gate both for bulk and packed trucks, Main entry/Exit gate both for bul and packed trucs, external road at plant entry and exit. Below mentioned items to be provide along with cameras: -Surge Protectors -Mounting Bracket same make as Camera | ip fixed bullet camera |  | lens: 8MP, resolution: 4k, sd card: 32GB | listing: UL (underwriters laboratories), type: MFZ (motorized focus zoom), sensor: progressive scan CMOS, WDR, streaming: multi streaming, compression: H.264, power: PoE, DC12V/AC24V, rating: IP67, protocol: ONVIF, accessories: pole mount accessories, surge protectors, mounting bracket (same make as camera) | 6 | Nos | Table 2
CCTV SYSTEM | 14.1.3 ¦ Supply of UL listed IP Fixed Box Camera , 8MP lens, with 1/2.5'' or better Progresive scan CMOS sensor ,Varifocal lens (8MP) of 2.8 to 8.5mm, #4k Resolution, 32GB SD card, WDR,multi streaming , H.264, PoE, DC12V/AC24V, IP 67 ,ONVIF with Pole Mount accessories or accesory as per site requirement. Cameras shall be installed over perimeter at 65 M gap (max). | ip fixed box camera |  | lens: 8MP, sensor: 1/2.5'' or better, varifocal lens: 2.8 to 8.5mm, resolution: 4k, sd card: 32GB | listing: UL (underwriters laboratories), sensor: progressive scan CMOS, WDR, streaming: multi streaming, compression: H.264, power: PoE, DC12V/AC24V, rating: IP67, protocol: ONVIF, accessories: pole mount accessories | 15 | Nos | Table 2
CCTV SYSTEM | 14.1.4 ¦ Supply of Full HD , 2MP, IP PTZ Camera (for peripheral survilience in auto mode) with 30X HD optical zoom, IP 66 Day/Night CCD/CMOS, 4.8 to 120 mm Lens, motorised varifocal , progressive scan, Wide Dynamic Range, Dual H.264 and M-JPEG simultaneously, digital signal processing, both PoE and 12 VDC/24 VAC, ONVIF conformant, UL Listed, POE enabled, complete with IP 66 Connectors, Lens, Camera Mounts, Power Supply & all accessories complete as per specifiocation. Cameras shall be installed over perimeter in pair with Manual mode PTZ camera. Below mentioned items to be provide along with cameras: -Surge Protectors -Mounting Bracket same make as Camera | ip ptz camera | ptz camera | resolution: 2MP, optical zoom: 30X HD, lens: 4.8 to 120 mm | type: full HD, rating: IP66, day/night: CCD/CMOS, lens: motorised varifocal, sensor: progressive scan, feature: wide dynamic range, streaming: dual H.264 and M-JPEG, processing: digital signal processing, power: PoE and 12 VDC/24 VAC, protocol: ONVIF conformant, listing: UL (underwriters laboratories), POE enabled, accessories: IP66 connectors, lens, camera mounts, power supply, surge protectors, mounting bracket (same make as camera) | 6 | Nos | Table 2
CCTV SYSTEM | 14.1.5 ¦ Supply of Full HD , 2MP, IP PTZ Camera (for peripheral survilience in manual mode) with 30X HD optical zoom, IP 66 Day/Night CCD/CMOS, 4.8 to 120 mm Lens, motorised varifocal , progressive scan, Wide Dynamic Range, Dual H.264 and M-JPEG simultaneously, digital signal processing, both PoE and 12 VDC/24 VAC, ONVIF conformant, UL Listed, POE enabled, complete with IP 66 Connectors, Lens, Camera Mounts, Power Supply & all accessories complete as per specifiocation. Cameras shall be installed over perimeter in pair with Auto mode PTZ camera. Below mentioned items to be provide along with cameras: -Surge Protectors -Mounting Bracket same make as Camera | ip ptz camera | ptz camera | resolution: 2MP, optical zoom: 30X HD, lens: 4.8 to 120 mm | type: full HD, rating: IP66, day/night: CCD/CMOS, lens: motorised varifocal, sensor: progressive scan, feature: wide dynamic range, streaming: dual H.264 and M-JPEG, processing: digital signal processing, power: PoE and 12 VDC/24 VAC, protocol: ONVIF conformant, listing: UL (underwriters laboratories), POE enabled, accessories: IP66 connectors, lens, camera mounts, power supply, surge protectors, mounting bracket (same make as camera) | 6 | Nos | Table 2
CCTV SYSTEM | 14.1.6 ¦ Supply of Full HD , 2MP, IP PTZ Camera with 30X HD optical zoom, IP 66 Day/Night CCD/CMOS, 4.8 to 120 mm Lens, motorised varifocal , progressive scan, Wide Dynamic Range, Dual H.264 and M-JPEG simultaneously, digital signal processing, both PoE and 12 VDC/24 VAC, ONVIF conformant, UL Listed, POE enabled, complete with IP 66 Connectors, Lens, Camera Mounts, Power Supply & all accessories complete as per specifiocation. Cameras shall be installed in bulk storage area including manifold area, complete location of plant. Below mentioned items to be provide along with cameras: -Surge Protectors -Mounting Bracket same make as Camera | ip ptz camera | ptz camera | resolution: 2MP, optical zoom: 30X HD, lens: 4.8 to 120 mm | type: full HD, rating: IP66, day/night: CCD/CMOS, lens: motorised varifocal, sensor: progressive scan, feature: wide dynamic range, streaming: dual H.264 and M-JPEG, processing: digital signal processing, power: PoE and 12 VDC/24 VAC, protocol: ONVIF conformant, listing: UL (underwriters laboratories), POE enabled, accessories: IP66 connectors, lens, camera mounts, power supply, surge protectors, mounting bracket (same make as camera) | 2 | Nos | Table 2
CCTV SYSTEM | 14.1.7 ¦ Supply of Fixed Ultra High Definition Panoramic camera not less than 8 MP with H.264 with high profile H.264 compression, constant 360 degee recording along with simultaneous multiple angles of view using one sensor, ONVIF, 3D client side Dewarping with no blind spots, POE enabled, UL certified as per tender specification. Camera shall be installed in TT Parking area. Below mentioned items to be provide along with cameras: -Surge Protectors -Mounting Bracket same make as Camera | fixed panoramic camera |  | resolution: not less than 8 MP | type: ultra high definition, compression: high profile H.264, recording: constant 360 degree, feature: simultaneous multiple angles of view using one sensor, protocol: ONVIF, feature: 3D client side dewarping, feature: no blind spots, power: POE enabled, certification: UL (underwriters laboratories), accessories: surge protectors, mounting bracket (same make as camera) | 1 | Nos | Table 2
CCTV SYSTEM | 14.1.8 ¦ Supply of Explosion proof ATEX Certified Fixed camera , MFZ Lens of 2MP, resolution of 1920x1080 pixels camera with progresive scan, with H.264 with high profile H.264 compression, lens of 3 - 9 mm Lens,DC-Iris, Day-Night 32 GB MicroSD/SDHC card Slot, 30fps, Multi streams, POE enabled, UL certified. Camera shall be installed in hazardous areas such as LPG Pump House, LPG Compressor House, Empty Cum Filling SHed, Loading- unloading shed, TLD bays. Below mentioned items to be provide along with cameras: -Surge Protectors -Mounting Bracket same make as Camera | explosion proof fixed camera |  | lens: MFZ, resolution: 2MP, pixels: 1920x1080, lens: 3-9 mm, sd card: 32 GB | certification: ATEX, type: explosion proof, sensor: progressive scan, compression: high profile H.264, iris: DC-Iris, day-night, frame rate: 30fps, streaming: multi streams, power: POE enabled, certification: UL (underwriters laboratories), accessories: surge protectors, mounting bracket (same make as camera) | 5 | Nos | Table 2
CCTV SYSTEM > NEWTORK SERVER & VIDEO MANAGEMENT SOFTWARE | 14.2.1 ¦ Recording Server(s) with the following minimum configuration Intel Xeon Quad Core Server 32 GB RAM 2 Gigabit NICs Windows Server 2012 R2 x64 Standard/Data Center OS and Application Volume - Disk Configuration: 2 x 300 GB minimum RAID 5 (with server redundancy) Live Database Disk Configuration: Connectivity Internal or Direct Attached 10 x 15K RPM 600GB RAID 1 / RAID10 | recording server |  | ram: 32 GB, disk configuration: 2 x 300 GB minimum, live database disk: 10 x 15K RPM 600GB | processor: intel xeon quad core, network: 2 gigabit NICs, operating system: windows server 2012 R2 x64 standard/data center, disk configuration: RAID 5 (with server redundancy), live database disk configuration: RAID 1 or RAID10, connectivity: internal or direct attached | 1 | Nos | Table 2
CCTV SYSTEM > NEWTORK SERVER & VIDEO MANAGEMENT SOFTWARE | 14.2.2 ¦ Supply of NAS based CCTV storage array (Cumulative 220 TB minimum) for NETWORK SERVER with centralized, scalable video storage, ideal for small to medium setups. The storage shall delivers total available throughput of 350 Mbps / 120 Streams for recording of IP video streams as well as playback and export through the client machine .It should have following hardware fetaure as minimum Processor Intel® Xeon E3-1276 v3 or better, Operating System Microsoft® Windows®Server 2012 . It should have 1TB SSD storage for Operating system.It should gave Internal Memory 32 GB DDR3 ECC or better. It should support RAID 6 feature for HDD redundancy and NVR should be UL listed. It should have Internal, RedundantcPower Supply.build up hard disk for min. 90 days recording. Supply of Dual Redundant Network Video Recorder(NVR) Server with min 21" widescreen LED monitor(One no) with KVM switch complete as per specifications and Tender Document. | nas based cctv storage array | nas cctv storage array | storage: cumulative 220 TB minimum, ssd: 1TB, internal memory: 32 GB DDR3 ECC or better, hard disk: min. 90 days recording, monitor: min 21" widescreen LED | for: network server, throughput: 350 Mbps or 120 streams, processor: intel xeon E3-1276 v3 or better, operating system: microsoft windows server 2012, RAID: RAID 6 for HDD redundancy, NVR: UL (underwriters laboratories) listed, power supply: internal, redundant, accessories: dual redundant network video recorder (NVR) server, KVM switch | 3 | Nos | Table 2
CCTV SYSTEM > NEWTORK SERVER & VIDEO MANAGEMENT SOFTWARE | 14.2.3 ¦ Supply of Video Management software licesnes | video management software license |  |  |  | 54 | Nos | Table 2
CCTV SYSTEM > NEWTORK SERVER & VIDEO MANAGEMENT SOFTWARE | 14.2.4 ¦ Supply of Advanced Analytics Software for all fixed cameras (including varifocal, Panoramic, MFZ fixed cameras) alongwith compatible Analytics Server with OS, Antivirus etc including analytic license for each camera complete as per specifications and Tender Document. | advanced analytics software |  |  | for: all fixed cameras (including varifocal, panoramic, MFZ fixed cameras), includes: compatible analytics server with OS, antivirus, analytic license for each camera | 1 | Lot | Table 2
CCTV SYSTEM > WORKSTATION WITH CLIENT LINSENCE | 14.3.1 ¦ Supply of workstation. The workstation shall have the following specifications:- Processor – Intel Core i7-4790 @ 3.60GHz Intel® HD Graphics 4600,Memory – Minimum 16 GB,Hard disks – 2TB SATA at 7200 rpms,OS- Windows 8.1/10, 64bit,Network Card – 1Gbit/s network card, Graphic card of minimum 2 GB memory. Location as mentioned below: -Central Monitoring Hub Room -Security Room -Admin Building Plant Manager Room | workstation |  | memory: minimum 16 GB, hard disk: 2TB SATA at 7200 rpms, graphic card: minimum 2 GB memory | processor: intel core i7-4790 @ 3.60GHz, graphics: intel hd graphics 4600, operating system: windows 8.1 or 10, 64bit, network card: 1Gbit/s network card, location: central monitoring hub room, security room, admin building plant manager room | 3 | Nos | Table 2
CCTV SYSTEM > CCTV Central Monitoring Hub (CMH) /SECURITY ROOM | 14.4.1 ¦ Supply of 55" Flat LED 4K Colour Monitors installed -Security Room -Admin Building (PM cabin) | flat led 4k colour monitor |  | screen size: 55" | type: flat, resolution: 4k, color: colour, location: security room, admin building (PM cabin) | 2 | Nos | Table 2
CCTV SYSTEM > CCTV Central Monitoring Hub (CMH) /SECURITY ROOM | 14.4.2 ¦ Supply of 42 U Enclosure cabinet/panel along with all accessories/component for switches and server installation. | enclosure cabinet or panel |  | height: 42 U | accessories: all accessories/component for switches and server installation | 1 | Lot | Table 2
CCTV SYSTEM > CABLE, SWITCHES AND ERECTION MATERIAL | 14.5.1 ¦ 4 port Industrial grade layer 2 Managed POE/POE+ Ethernet Switch for connecting Cameras with 4 No. RJ copper port and 2 Nos. optical fiber ports and surge protector as per specifications and Tender Document. | industrial grade layer 2 managed poe ethernet switch | poe ethernet switch | ports: 4 RJ copper, 2 optical fiber | type: industrial grade, layer: 2, managed: yes, POE/POE+, accessories: surge protector | 28 | Nos | Table 2
CCTV SYSTEM > CABLE, SWITCHES AND ERECTION MATERIAL | 14.5.2 ¦ Supply of Layer 3 8 Port SFP , 2SFP+ Ports Managed Switch with Dual internal Power Supply. To be installed in CR | layer 3 managed switch |  | ports: 8 SFP, 2 SFP+ | layer: 3, managed: yes, power supply: dual internal, installation: CR | 2 | Nos | Table 2
CCTV SYSTEM > CABLE, SWITCHES AND ERECTION MATERIAL | 14.5.3 ¦ Supply of Explosion Proof junction box for field switches in licsence area | explosion proof junction box |  |  | for: field switches, area: license area, type: explosion proof | 6 | Nos | Table 2
CCTV SYSTEM > CABLE, SWITCHES AND ERECTION MATERIAL | 14.5.4 ¦ Supply of Layer 3 24 Port SFP , 2SFP+ Ports Managed Switch with Dual internal Power Supply. | layer 3 managed switch |  | ports: 24 SFP, 2 SFP+ | layer: 3, managed: yes, power supply: dual internal | 1 | Nos | Table 2
CCTV SYSTEM > CABLE, SWITCHES AND ERECTION MATERIAL | 14.5.5 ¦ Supply of IP 65 junction box Box for keeping the field switches in non licsence area | ip65 junction box |  |  | protection: IP65, for: field switches, area: non license area | 22 | Nos | Table 2
CCTV SYSTEM > CABLE, SWITCHES AND ERECTION MATERIAL | 14.5.6 ¦ Supply of 8 M with cantilever of 3 meter (Above ground) Hot Dip Galvanized Poles along with foundation & painting as per the tender specifications. This scope also includes supply, erection & fabrication of structural steel work for installation of JB & camera with industrial grade painting | hot dip galvanized pole |  | height: 8 M, cantilever: 3 meter (above ground) | foundation: included, painting: as per tender specifications, includes: supply, erection & fabrication of structural steel work for installation of JB & camera, painting: industrial grade | 7 | Nos | Table 2
CCTV SYSTEM > CABLE, SWITCHES AND ERECTION MATERIAL | 14.5.7 ¦ Supply of 8 M with cantilever of 1.5 meter (Above ground) Hot Dip Galvanized Poles along with foundation & painting as per the tender specifications. This scope also includes supply, erection & fabrication of structural steel work for installation of JB & camera with industrial grade painting | hot dip galvanized pole |  | height: 8 M, cantilever: 1.5 meter (above ground) | foundation: included, painting: as per tender specifications, includes: supply, erection & fabrication of structural steel work for installation of JB & camera, painting: industrial grade | 1 | Nos | Table 2
CCTV SYSTEM > CABLE, SWITCHES AND ERECTION MATERIAL | 14.5.8 ¦ Supply of 8 M with 2 cantilevers (one at 8 m & second at 1.5 M) of 1.5 meter (Above ground) Hot Dip Galvanized Poles along with foundation & painting as per the tender specifications. This scope also includes supply, erection & fabrication of structural steel work for installation of JB & camera with industrial grade painting | hot dip galvanized pole |  | height: 8 M, cantilevers: one at 8 m & second at 1.5 M of 1.5 meter (above ground) | foundation: included, painting: as per tender specifications, includes: supply, erection & fabrication of structural steel work for installation of JB & camera, painting: industrial grade | 1 | Nos | Table 2
CCTV SYSTEM > CABLE, SWITCHES AND ERECTION MATERIAL | 14.5.9 ¦ Supply of 6 M with cantilever of 3 meter (Above ground) Hot Dip Galvanized Poles along with foundation & painting as per the tender specifications. This scope also includes supply, erection & fabrication of structural steel work for installation of JB & camera with industrial grade painting | hot dip galvanized pole |  | height: 6 M, cantilever: 3 meter (above ground) | foundation: included, painting: as per tender specifications, includes: supply, erection & fabrication of structural steel work for installation of JB & camera, painting: industrial grade | 8 | Nos | Table 2
CCTV SYSTEM > CABLE, SWITCHES AND ERECTION MATERIAL | 2010-05-14 00:00:00 ¦ Supply of 6 M with cantilever of 1.5 meter (Above ground) Hot Dip Galvanized Poles along with foundation & painting as per the tender specifications. This scope also includes supply, erection & fabrication of structural steel work for installation of JB & camera with industrial grade painting | hot dip galvanized pole |  | height: 6 M, cantilever: 1.5 meter (above ground) | foundation: included, painting: as per tender specifications, includes: supply, erection & fabrication of structural steel work for installation of JB & camera, painting: industrial grade | 1 | Nos | Table 2
CCTV SYSTEM > CABLE, SWITCHES AND ERECTION MATERIAL | 2011-05-14 00:00:00 ¦ Supply of 6 M with 2 cantilevers (one at 8 m & second at 1.5 M) of 2.5 meter (Above ground) Hot Dip Galvanized Poles along with foundation & painting as per the tender specifications. This scope also includes supply, erection & fabrication of structural steel work for installation of JB & camera with industrial grade painting | hot dip galvanized pole |  | height: 6 M, cantilevers: one at 8 m & second at 1.5 M of 2.5 meter (above ground) | foundation: included, painting: as per tender specifications, includes: supply, erection & fabrication of structural steel work for installation of JB & camera, painting: industrial grade | 1 | Nos | Table 2
CCTV SYSTEM > CABLE, SWITCHES AND ERECTION MATERIAL | 2012-05-14 00:00:00 ¦ Supply of 10 M with cantilever of 1.5 meter (Above ground) Hot Dip Galvanized Poles along with foundation & painting as per the tender specifications. This scope also includes supply, erection & fabrication of structural steel work for installation of JB & camera with industrial grade painting | hot dip galvanized pole |  | height: 10 M, cantilever: 1.5 meter (above ground) | foundation: included, painting: as per tender specifications, includes: supply, erection & fabrication of structural steel work for installation of JB & camera, painting: industrial grade | 1 | Nos | Table 2
CCTV SYSTEM > CABLE, SWITCHES AND ERECTION MATERIAL | 2013-05-14 00:00:00 ¦ Supply of approx. 15 M (Above ground) Hot Dip Galvanized Poles along with foundation & painting as per the tender specifications. This scope also includes supply of structural steel work for installation of JB & camera with industrial grade painting | hot dip galvanized pole |  | height: approx. 15 M (above ground) | foundation: included, painting: as per tender specifications, includes: supply of structural steel work for installation of JB & camera, painting: industrial grade | 1 | Nos | Table 2
CCTV SYSTEM > CABLE, SWITCHES AND ERECTION MATERIAL | 2014-05-14 00:00:00 ¦ Supply of approx. 30 M (Above ground) Hot Dip Galvanized Poles as per the tender specifications. This scope also includes supply of structural steel work for installation of JB & camera with industrial grade painting (foundation design shall be provided by E & I vendor, foundation construction shall be in IOCL scope) | hot dip galvanized pole |  | height: approx. 30 M (above ground) | painting: as per tender specifications, includes: supply of structural steel work for installation of JB & camera, painting: industrial grade, foundation design: by E & I vendor, foundation construction: in IOCL scope | 1 | Nos | Table 2
CCTV SYSTEM > CABLE, SWITCHES AND ERECTION MATERIAL | 2015-05-14 00:00:00 ¦ suppy of 2'' GI Pipe | gi(galvanized iron) pipe | gi pipe | diameter: 2 inch |  | 1000 | Mtrs | Table 2
UPS SYSTEM | 15.01 ¦ 230V, 1-ph,2-wire- 2X25 kVA Parallel redundant, UPS system with static bypass supply along with suitable Ahrs. rating of Ni-Cd batteries for half hour backup, battery stands, Weatherproof double compression Ni plated brass cable glands and cable lugs for all incoming and outgoing cables etc and as per specification. The UPS shall have two numbers of 230 V output. One 230 V output shall feed to the 230/110 V, 2 kVA, control transformer, the secondary of which will feed to 110 V ACDB (as per SLD). | ups(uninterruptible power supply) system | ups system | capacity: 2x25 kVA, output: 2 x 230 V, backup: half hour | phase: 1-ph, wire: 2-wire, redundancy: parallel redundant, bypass: static, battery: Ni-Cd(nickel-cadmium), battery stands: included, cable glands: weatherproof double compression Ni plated brass, cable lugs: included, transformer: 230/110 V, 2 kVA control transformer, secondary output: 110 V ACDB(as per SLD), as per specification | 1 | No. | Table 2
UPS SYSTEM | 15.02 ¦ 230V, 1-ph,2-wire- 250A, Cu-Busbar,UPS distribution board (ACDB) as per attached specification and single line diagram PC00128- 1221 along with Weather proof double compression Ni plated brass cable glands and cable lugs for all incoming and outgoing cables. | ups(uninterruptible power supply) distribution board | ups distribution board | current: 250A | phase: 1-ph, wire: 2-wire, busbar: copper, specification: as per attached, single line diagram: PC00128-1221, cable glands: weatherproof double compression Ni plated brass, cable lugs: included | 1 | No. | Table 2
PLANT COMMUNICATION SYSTEM | 16.01 ¦ Supply of Plant Communication system along with Cable gland and lugs etc complete .The system shall comprise of following items as per latest IS/IEC. -Digital central exchange unit with power supply unit and battery back up - 1 set. -Desktop master call station- 1 No. -Weather proof field call station including amplifier with full keypad (12 keys) along with the functional keys- 05 Nos. -Explosion proof field call station including amplifier with full keypad (12 keys) along with the functional keys- 06 Nos -Explosion proof field call station including amplifier with full keypad (12 keys) along with the functional keys & Beacon- 01 Nos. -Weather proof loudspeaker 25W- 08 Nos. -Explosion proof loudspeaker 25W- 02 Nos. -Provision for interfacing with fire alarm and gas detection system. -Basic software and programming. Any other item not specifically mentioned but requireed for the completeness of the system shall be provided. Above shall be checked and read in conjuction with tender drawing. | plant communication system |  |  | cable glands: included, lugs: included, standard: IS(indian standard)/IEC(international electrotechnical commission), digital central exchange unit: 1 set, power supply unit: included, battery backup: included, desktop master call station: 1 No., weatherproof field call station: 5 Nos, amplifier: included, keypad: 12 keys, functional keys: included, explosion proof field call station: 6 Nos, explosion proof field call station with beacon: 1 No., weatherproof loudspeaker: 25W, 8 Nos, explosion proof loudspeaker: 25W, 2 Nos, interfacing: fire alarm and gas detection system, software: basic, programming: included, completeness: any other item required, reference: tender drawing | 1 | LOT | Table 2
EPABX & TELEPHONE | 17.01 ¦ Supply of EPABX System along with operator console, Battery, Battery Charger, junction boxes etc and required accessories including supply of suitbale size cable glands, cable lugs, as per scope of supply. EPABX shall be placed in CHM Room and telephone system cables shall be hooked between telephone system from CHM rooom to all telephone (hardwares to fulfill the system requirement) locations. | epabx(electronic private automatic branch exchange) system | epabx system |  | operator console: included, battery: included, battery charger: included, junction boxes: included, accessories: included, cable glands: suitable size, cable lugs: included, installation: CHM Room, cabling: between CHM room and all telephone locations, hardware: to fulfill system requirement | 1 | Lot. | Table 2
EPABX & TELEPHONE | 17.02 ¦ Analog telephone with LCD display, incoming call memory, outgoing call memory, Redial & pause function, 5 types of ringing tone for selection of intercom & parallel call transfer, volume control, caller ID Instrument and other standard features. | analog telephone |  |  | display: LCD, memory: incoming call, outgoing call, functions: redial, pause, ringing tone: 5 types, intercom: selection, call transfer: parallel, volume control: included, caller ID: included, features: standard | 1 | No. | Table 2
EPABX & TELEPHONE | 17.03 ¦ Analog telephone with Redial , recall & pause function, intercom parallel call transfer facility, volume control etc and other standard features. | analog telephone |  |  | functions: redial, recall, pause, intercom: parallel call transfer, volume control: included, features: standard | 1 | No. | Table 2
EPABX & TELEPHONE | 17.04 ¦ Roset box with voice tag & face plate | roset box |  |  | voice tag: included, face plate: included | 1 | No. | Table 2
EPABX & TELEPHONE | 17.05 ¦ Supply of armoured communication cable, junction boxes with suitable cable glands & lugs & associated PVC slotted channel with cover with structured cable laying - Lot. Quanteties shown hear are estimated only. Vendor shall provide actual quanties as per site requirement. This item is to be cosider as lumsum only. | armoured communication cable with junction boxes and accessories |  |  | cable: armoured, junction boxes: included, cable glands: suitable, lugs: included, PVC slotted channel: with cover, cable laying: structured, quantity: estimated, actual as per site, item: lump sum |  |  | Table 2
EPABX & TELEPHONE | 17.05.1 ¦ 1) 2Px 0.5 mm dia. | armoured communication cable |  | pairs: 2, diameter: 0.5 mm |  | 100 | Mtrs. | Table 2
EPABX & TELEPHONE | 17.05.2 ¦ 2) 4P x 0.5 mm dia. | armoured communication cable |  | pairs: 4, diameter: 0.5 mm |  | 300 | Mtrs. | Table 2
EPABX & TELEPHONE | 17.05.3 ¦ 3) 10Px 0.5 mm dia. | armoured communication cable |  | pairs: 10, diameter: 0.5 mm |  | 300 | Mtrs. | Table 2
CCTV SYSTEM > CABLE, SWITCHES AND ERECTION MATERIAL | 14.1.6 ¦ PVC conduit casing pipe | pvc(polyvinyl chloride) conduit casing pipe |  |  |  | 300 | Mtrs. | Table 2
INTRINSCIALLY SAFE (IP55)WALKIE-TALKIE SUITABLE FOR HAZARDOUS AREA DEFINED AS ZONE1, GAS GROUP IIA/IIB,TEMPERATURE CLASS T3 OF MOTOROLA MAKE INCLUDING LISONING AND OBTAINING LICENSE FROM DOT. (OFFICIAL FEE FOR LICENSE IF ANY SHALL BE PAID BY IOCL) | 18.1 ¦ Motorola GP 328 Intrinsically safe VHF handheld radio with 1800 mAh battery Tri Chemistry Charger with Adapter & Antenna-Genuine Motorola make | vhf(very high frequency) handheld radio |  | battery capacity: 1800 mAh | model: Motorola GP 328, safety: intrinsically safe, charger: tri chemistry, adapter: included, antenna: included, make: Motorola | 6 | Nos. | Table 2
INTRINSCIALLY SAFE (IP55)WALKIE-TALKIE SUITABLE FOR HAZARDOUS AREA DEFINED AS ZONE1, GAS GROUP IIA/IIB,TEMPERATURE CLASS T3 OF MOTOROLA MAKE INCLUDING LISONING AND OBTAINING LICENSE FROM DOT. (OFFICIAL FEE FOR LICENSE IF ANY SHALL BE PAID BY IOCL) | 18.2 ¦ Motorola GM 338 Fixed Station with Fist Mic,12V/10A Power supply unit cum battery charger with all accessories (maintenance free) (Base Station) | fixed radio station |  | power supply: 12V/10A | model: Motorola GM 338, microphone: fist mic, battery charger: included, accessories: all, maintenance: free, type: base station | 1 | No. | Table 2
INTRINSCIALLY SAFE (IP55)WALKIE-TALKIE SUITABLE FOR HAZARDOUS AREA DEFINED AS ZONE1, GAS GROUP IIA/IIB,TEMPERATURE CLASS T3 OF MOTOROLA MAKE INCLUDING LISONING AND OBTAINING LICENSE FROM DOT. (OFFICIAL FEE FOR LICENSE IF ANY SHALL BE PAID BY IOCL) | 18.3 ¦ Motorola GP 328 spare battery with 1800 mAh capacity of Genuine Motorola Make | spare battery |  | capacity: 1800 mAh | model: Motorola GP 328, make: Motorola | 3 | Nos. | Table 2
CABLE GLANDS | 19.1 ¦ Supply of weather proof double compression Ni plated brass cable gland of the following sizes of XLPE,Arm. FRLS cables. | weather proof double compression nickel plated brass cable gland |  |  | material: nickel plated brass, compression: double, weather proof: yes, suitable for: XLPE(cross-linked polyethylene), armoured, FRLS(fire retardant low smoke) cables |  |  | Table 2
CABLE GLANDS | 19.1.1 ¦ 01P X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , OVERALL SHIELDED , SIGNAL CABLE | weather proof double compression nickel plated brass cable gland |  | cable: 1 pair x 1.5 mm2, insulation: PVC(polyvinyl chloride), armoured, sheath: FRLS(fire retardant low smoke) PVC, shielded: overall, type: signal cable |  | 54 | Nos. | Table 2
CABLE GLANDS | 19.1.2 ¦ 02C X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , CONTROL CABLE | weather proof double compression nickel plated brass cable gland |  | cable: 2 core x 1.5 mm2, insulation: PVC(polyvinyl chloride), armoured, sheath: FRLS(fire retardant low smoke) PVC, type: control cable |  | 48 | Nos. | Table 2
CABLE GLANDS | 19.1.3 ¦ 02P X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , OVERALL SHIELDED , SIGNAL CABLE | weather proof double compression nickel plated brass cable gland |  | cable: 2 pair x 1.5 mm2, insulation: PVC(polyvinyl chloride), armoured, sheath: FRLS(fire retardant low smoke) PVC, shielded: overall, type: signal cable |  | 3 | Nos. | Table 2
CABLE GLANDS | 19.1.4 ¦ 04C X 2.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , CONTROL CABLE | weather proof double compression nickel plated brass cable gland |  | cable: 4 core x 2.5 mm2, insulation: PVC(polyvinyl chloride), armoured, sheath: FRLS(fire retardant low smoke) PVC, type: control cable |  | 31 | Nos. | Table 2
CABLE GLANDS | 19.1.5 ¦ 05C X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , CONTROL CABLE | weather proof double compression nickel plated brass cable gland |  | cable: 5 core x 1.5 mm2, insulation: PVC(polyvinyl chloride), armoured, sheath: FRLS(fire retardant low smoke) PVC, type: control cable |  | 19 | Nos. | Table 2
CABLE GLANDS | 19.1.6 ¦ 12C X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , CONTROL CABLE | weather proof double compression nickel plated brass cable gland |  | cable: 12 core x 1.5 mm2, insulation: PVC(polyvinyl chloride), armoured, sheath: FRLS(fire retardant low smoke) PVC, type: control cable |  | 11 | Nos. | Table 2
CABLE GLANDS | 19.2 ¦ Supply of Flameproof double compression nickel plated brass cable gland suitable for following XLPE , FRLS cable sizes & as per relevant IS for hazardous area Zone-1,IIA/IIB,T3. | flameproof double compression nickel plated brass cable gland |  |  | material: nickel plated brass, compression: double, flameproof: yes, suitable for: XLPE(cross-linked polyethylene), FRLS(fire retardant low smoke) cables, standard: IS(indian standard), hazardous area: Zone-1, IIA/IIB, T3 |  |  | Table 2
CABLE GLANDS | 19.2.1 ¦ 01P X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , OVERALL SHIELDED , SIGNAL CABLE | flameproof double compression nickel plated brass cable gland |  | cable: 1 pair x 1.5 mm2, insulation: PVC(polyvinyl chloride), armoured, sheath: FRLS(fire retardant low smoke) PVC, shielded: overall, type: signal cable |  | 54 | Nos. | Table 2
CABLE GLANDS | 19.2.2 ¦ 01T X 2.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , OVERALL SHIELDED , SIGNAL CABLE | flameproof double compression nickel plated brass cable gland |  | cable: 1 triad x 2.5 mm2, insulation: PVC(polyvinyl chloride), armoured, sheath: FRLS(fire retardant low smoke) PVC, shielded: overall, type: signal cable |  | 62 | Nos. | Table 2
CABLE GLANDS | 19.2.3 ¦ 02C X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , CONTROL CABLE | flameproof double compression nickel plated brass cable gland |  | cable: 2 core x 1.5 mm2, insulation: PVC(polyvinyl chloride), armoured, sheath: FRLS(fire retardant low smoke) PVC, type: control cable |  | 48 | Nos. | Table 2
CABLE GLANDS | 19.2.4 ¦ 04P X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , OVERALL SHIELDED , SIGNAL CABLE | flameproof double compression nickel plated brass cable gland |  | cable: 4 pair x 1.5 mm2, insulation: PVC(polyvinyl chloride), armoured, sheath: FRLS(fire retardant low smoke) PVC, shielded: overall, type: signal cable |  | 2 | Nos. | Table 2
CABLE GLANDS | 19.2.5 ¦ 06P X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , OVERALL SHIELDED , SIGNAL CABLE | flameproof double compression nickel plated brass cable gland |  | cable: 6 pair x 1.5 mm2, insulation: PVC(polyvinyl chloride), armoured, sheath: FRLS(fire retardant low smoke) PVC, shielded: overall, type: signal cable |  | 8 | Nos. | Table 2
CABLE GLANDS | 19.2.6 ¦ 06T X 2.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , OVERALL SHIELDED , SIGNAL CABLE | flameproof double compression nickel plated brass cable gland |  | cable: 6 triad x 2.5 mm2, insulation: PVC(polyvinyl chloride), armoured, sheath: FRLS(fire retardant low smoke) PVC, shielded: overall, type: signal cable |  | 8 | Nos. | Table 2
CABLE GLANDS | 19.2.7 ¦ 12P X 1.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , OVERALL SHIELDED , SIGNAL CABLE | flameproof double compression nickel plated brass cable gland |  | cable: 12 pair x 1.5 mm2, insulation: PVC(polyvinyl chloride), armoured, sheath: FRLS(fire retardant low smoke) PVC, shielded: overall, type: signal cable |  | 10 | Nos. | Table 2
CABLE GLANDS | 19.2.8 ¦ 12T X 2.5 MM2 PVC INSULATED ARMOURED, FRLS PVC SHEATHED , OVERALL SHIELDED , SIGNAL CABLE | flameproof double compression nickel plated brass cable gland |  | cable: 12 triad x 2.5 mm2, insulation: PVC(polyvinyl chloride), armoured, sheath: FRLS(fire retardant low smoke) PVC, shielded: overall, type: signal cable |  | 2 | Nos. | Table 2
SPARES | 20.1 ¦ Plant Communication System, Similar as supplied. | plant communication system | [5 empty] | Table 2
SPARES | 20.2 ¦ Flameproof Field Call Station. | flameproof field call station |  |  | flameproof: yes | 1 | Nos. | Table 2
SPARES | 20.3 ¦ Weatherproof Field Call Station. | weatherproof field call station |  |  | weatherproof: yes | 1 | Nos. | Table 2
SPARES | 20.4 ¦ Flameproof Loudspeaker. | flameproof loudspeaker |  |  | flameproof: yes | 1 | Nos. | Table 2
SPARES | 20.5 ¦ Weatherproof Loudspeaker. | weatherproof loudspeaker |  |  | weatherproof: yes | 1 | No. | Table 2
SPARES | 20.6 ¦ Local Control Station (LCS) Similar as Supplied. | local control station | lcs |  |  |  |  | Table 2
SPARES | 20.7 ¦ Flameproof Local control station with Start/Stop Push Button, FRP Canopy with Ammeter. | flameproof local control station |  |  | flameproof: yes, feature: start/stop push button, canopy: FRP(fiber reinforced plastic), ammeter: with | 1 | Nos. | Table 2
SPARES | 20.8 ¦ Flameproof Local control station,Start/Stop Push Button, FRP Canopy without ammeter. | flameproof local control station |  |  | flameproof: yes, feature: start/stop push button, canopy: FRP(fiber reinforced plastic), ammeter: without | 1 | Nos. | Table 2
SPARES | 20.9 ¦ Weatherproof Local control station with Start/Stop Push Button, FRP Canopy with Ammeter. | weatherproof local control station |  |  | weatherproof: yes, feature: start/stop push button, canopy: FRP(fiber reinforced plastic), ammeter: with | 1 | Nos. | Table 2
SPARES | 20.1 ¦ Weatherproof Local control station,Start/Stop Push Button, FRP Canopy without ammeter. | weatherproof local control station |  |  | weatherproof: yes, feature: start/stop push button, canopy: FRP(fiber reinforced plastic), ammeter: without | 1 | Nos. | Table 2
SPARES | 20.11 ¦ Junction Box Similar as Supplied. | junction box | [5 empty] | Table 2
SPARES | 20.12 ¦ Digital Meggar (make FLUKE / YAKOGAWA) | digital meggar |  |  | make: FLUKE or YAKOGAWA | 1 | Set. | Table 2
SPARES | 20.13 ¦ Tongue Tester (make FLUKE / YAKOGAWA) | tongue tester |  |  | make: FLUKE or YAKOGAWA | 1 | No. | Table 2
SPARES | 20.14 ¦ Digital Multimeter (make FLUKE / YAKOGAWA) | digital multimeter |  |  | make: FLUKE or YAKOGAWA | 1 | No. | Table 2
CABLE TRAYS | 21.1 ¦ G.I. Perforated Cable Trays , 100 mm deep, 3 mm thick G.I. perforated cable trays (Min. coating 100 microns of zinc) with bend, reducer, coupler plate and other hardware. | gi perforated cable trays |  | depth: 100 mm, thickness: 3 mm | material: GI(galvanized iron), coating: zinc, coating thickness: 100 microns (minimum), accessories: bend, reducer, coupler plate, other hardware |  |  | Table 2
CABLE TRAYS | b. ¦ 600mm Wide | gi perforated cable trays |  | width: 600 mm |  | 140 | m | Table 2
CABLE TRAYS | c. ¦ 300mm Wide | gi perforated cable trays |  | width: 300 mm |  | 60 | m | Table 2
CABLE TRAYS | d. ¦ 150mm Wide | gi perforated cable trays |  | width: 150 mm |  | 200 | m | Table 2
CABLE TRAYS | e. ¦ 50mm Wide | gi perforated cable trays |  | width: 50 mm |  | 75 | m | Table 2
CABLE TRAYS | 21.2 ¦ 90 deg Horizontal Bend Perforated | 90 degree horizontal bend perforated | [5 empty] | Table 2
CABLE TRAYS | b. ¦ 600mm Wide | 90 degree horizontal bend perforated |  | width: 600 mm |  | 4 | Nos. | Table 2
CABLE TRAYS | c. ¦ 300mm Wide | 90 degree horizontal bend perforated |  | width: 300 mm |  | 6 | Nos. | Table 2
CABLE TRAYS | 21.3 ¦ 90 deg Vertical Bend (Inside) Perforated | 90 degree vertical bend (inside) perforated | [5 empty] | Table 2
CABLE TRAYS | a. ¦ 600mm Wide | 90 degree vertical bend (inside) perforated |  | width: 600 mm |  | 4 | Nos. | Table 2
CABLE TRAYS | b. ¦ 300mm Wide | 90 degree vertical bend (inside) perforated |  | width: 300 mm |  | 4 | Nos. | Table 2
CABLE TRAYS | c. ¦ 150mm Wide | 90 degree vertical bend (inside) perforated |  | width: 150 mm |  | 12 | Nos. | Table 2
CABLE TRAYS | 21.4 ¦ 90 deg Vertical Bend (outside) Perforated | 90 degree vertical bend (outside) perforated | [5 empty] | Table 2
CABLE TRAYS | a. ¦ 600mm Wide | 90 degree vertical bend (outside) perforated |  | width: 600 mm |  | 4 | Nos. | Table 2
CABLE TRAYS | b. ¦ 300mm Wide | 90 degree vertical bend (outside) perforated |  | width: 300 mm |  | 4 | Nos. | Table 2
CABLE TRAYS | c. ¦ 150mm Wide | 90 degree vertical bend (outside) perforated |  | width: 150 mm |  | 20 | Nos. | Table 2
CABLE TRAYS | 21.5 ¦ TEE Connection Perforated type | tee connection perforated type | [5 empty] | Table 2
CABLE TRAYS | a. ¦ 600mm Wide | tee connection perforated type |  | width: 600 mm |  | 4 | Nos. | Table 2
EARTHING ITEMS FOR INSTRUMENTATION | 22.1 ¦ Supply of Hot dip Galvanized 10 Holes ∅13mm ground plate 550mmx50mmx6mm earth connection bar with fixing materials/ accessories , SS hardware etc. (min. coating 120 microns of zinc). | earth connection bar |  | holes: 10, hole diameter: 13 mm, plate size: 550 mm x 50 mm x 6 mm | material: hot dip galvanized, hardware: stainless steel (ss), coating: 120 microns of zinc | 12 | Nos. | Table 2
EARTHING ITEMS FOR INSTRUMENTATION | 22.2 ¦ Supply of following Hot dip Galvanized earthing and lightning protection materials along with the accessories conforming to IS & drg. Attachment no.-29 (LPG.ENG.117.06.03.2001) of contract specification Specifications and .(Galvanisation is 910gms/sq. mtr) - 1C x 6 mm2 PVC (Al) cable Green colour | earthing and lightning protection materials |  | cable: 1 core x 6 mm2 | material: hot dip galvanized, standard: indian standard (is), drawing: attachment no.-29 (lpg.eng.117.06.03.2001), galvanisation: 910 gms/sq. mtr, cable: pvc (polyvinyl chloride) (al) (aluminium), colour: green | 2400 | Mtr | Table 2
EARTHING ITEMS FOR INSTRUMENTATION | 22.3 ¦ Supply of Earthing Lug 1C x 6 mm2 PVC (Al) cable Green colour | earthing lug |  | cable: 1 core x 6 mm2 | cable: pvc (polyvinyl chloride) (al) (aluminium), colour: green | 250 | Nos. | Table 2