## Sheet1
section_context_for_this_product_block | full_product_description | core_product_name | acronymed_core_product_name | size | feature_or_specifications | quantity | unit | sheet_name
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 1.1 ¦ Design and supply of H-pole Structure for 11 KV Incoming Power Supply with Gang operated isolator, D.O. fuse with base, lightning arrestors, Insulator, earthing, construction of earth Pits, fencing, gate, gravel laying, padlocking, signages including all civil works for 11 KV Supply. The design shall be in line with Electricity board guidelines. | h-pole structure |  |  | voltage: 11 kv, feature: gang operated isolator, feature: d.o. (drop out) fuse with base, feature: lightning arrestors, feature: insulator, feature: earthing, feature: construction of earth pits, feature: fencing, feature: gate, feature: gravel laying, feature: padlocking, feature: signages, feature: all civil works for 11 kv supply, standard: electricity board guidelines | 1 | Set | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 2.1 ¦ 11 KV, 630 A, VCB panel indoor type comprising of metering and protection system including numerical relay, auxiliary relay, CTs, PTs , indication lamp, switches along with Weather proof double compression Ni plated brass cable gland and crimping type cable lugs for all incoming and outgoing cables and as per specfication.. | vcb panel | vcb panel | voltage: 11 kv, current: 630 a | type: indoor, feature: metering and protection system, feature: numerical relay, feature: auxiliary relay, feature: cts (current transformers), feature: pts (potential transformers), feature: indication lamp, feature: switches, feature: weather proof double compression ni (nickel) plated brass cable gland, feature: crimping type cable lugs for all incoming and outgoing cables, feature: as per specification | 1 | No. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 3.1 ¦ 500 KVA, 11KV/433V, Dyn11, AN type with off load tap changer power transformer complete with all accessories as per attached specifications & DS. | power transformer |  | capacity: 500 kva, voltage: 11kv/433v | vector group: dyn11, cooling type: an (air natural), feature: off load tap changer, feature: complete with all accessories, feature: as per attached specifications & ds (data sheet) | 1 | No. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 3.2 ¦ 200KVA, 415V/433V, Dyn1, natural air cooled Dry type Lighting transformer as per attached specifications & DS. | lighting transformer |  | capacity: 200kva, voltage: 415v/433v | vector group: dyn1, cooling type: natural air cooled dry type, feature: as per attached specifications & ds (data sheet) | 1 | No. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 4.1 ¦ PMCC: 415V, 3phase, 4 wire, 50 Hz, 800A, 50 KA for 1second, double front fully draw out type PMCC comprising of ACBs, CTs/PTs, relays, indicating lamps etc. as per attached SLDs, specifications & DS. | pmcc | pmcc | voltage: 415v, phase: 3phase, wire: 4 wire, frequency: 50 hz, current: 800a, short circuit rating: 50 ka for 1 second | type: double front fully draw out, feature: comprising of acbs (air circuit breakers), cts (current transformers)/pts (potential transformers), relays, indicating lamps, feature: as per attached slds (single line diagrams), specifications & ds (data sheet) | 1 | No. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 4.2 ¦ MLDB: 415V, 3phase, 4 wire, 50 Hz, 400A, 25KA for 1second MLDB including as per attached SLD, specifications & DS. | mldb | mldb | voltage: 415v, phase: 3phase, wire: 4 wire, frequency: 50 hz, current: 400a, short circuit rating: 25ka for 1 second | feature: as per attached sld (single line diagram), specifications & ds (data sheet) | 1 | No. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 4.3 ¦ Fire water MCC: 415V, 3phase, 4 wire, 50 Hz, 400A, 50KA for 1second MCC including as per attached SLD, specifications & DS. | fire water mcc | mcc | voltage: 415v, phase: 3phase, wire: 4 wire, frequency: 50 hz, current: 400a, short circuit rating: 50ka for 1 second | feature: as per attached sld (single line diagram), specifications & ds (data sheet) | 1 | No. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 4.4 ¦ CAPACITOR PANEL : 415V, 3Ph-N, 50Hz, 50KA for 1second, 250KVAR capacitor panel with capacitors 2X75, 1X50, 2X25 KVAR) and APFC relay, protections, filters etc. as per attached SLD, specifications & DS including weather proof double compression Ni plated brass cable glands and lugs for all incoming and outgoing feeders. | capacitor panel |  | voltage: 415v, phase: 3ph-n, frequency: 50hz, short circuit rating: 50ka for 1 second, capacity: 250kvar | capacitors: 2x75, 1x50, 2x25 kvar, feature: apfc (automatic power factor correction) relay, feature: protections, feature: filters, feature: as per attached sld (single line diagram), specifications & ds (data sheet), feature: weather proof double compression ni (nickel) plated brass cable glands and lugs for all incoming and outgoing feeders | 1 | No. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 5.1 ¦ LDB / LP, W eatherproof, IP 65, incomer 63A, 3 Phase, 4 wire, 3 Way LDB, 10kA for 1 sec with RCBO | ldb | ldb | incomer: 63a, phase: 3 phase, wire: 4 wire, way: 3 way, short circuit rating: 10ka for 1 sec | type: weatherproof, protection: ip 65, feature: with rcbo (residual current circuit breaker with overcurrent protection) | 1 | No. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 5.2 ¦ LDB / LP, W eatherproof, IP 65, incomer 63A, 3 Phase, 4 wire, 6 Way LDB, 10kA for 1 sec with RCBO | ldb | ldb | incomer: 63a, phase: 3 phase, wire: 4 wire, way: 6 way, short circuit rating: 10ka for 1 sec | type: weatherproof, protection: ip 65, feature: with rcbo (residual current circuit breaker with overcurrent protection) | 1 | No. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 5.3 ¦ LDB / LP, Outdoor type, Flame proof (FLP) Type, IP class suitable for FLP and minimum protection shall be IP-65, incomer 63A, 3 Phase, 4 wire, 3 Way LDB, 10kA for 1 sec with RCBO | ldb | ldb | incomer: 63a, phase: 3 phase, wire: 4 wire, way: 3 way, short circuit rating: 10ka for 1 sec | type: outdoor, type: flame proof (flp), protection: ip class suitable for flp, minimum protection: ip-65, feature: with rcbo (residual current circuit breaker with overcurrent protection) | 5 | No. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 5.4 ¦ LDB / LP, Outdoor type, Flame proof (FLP) Type, IP class suitable for FLP and minimum protection shall be IP-65 , incomer 63A, 3 Phase, 4 wire, 6 Way LDB, 10kA for 1 sec with RCBO | ldb | ldb | incomer: 63a, phase: 3 phase, wire: 4 wire, way: 6 way, short circuit rating: 10ka for 1 sec | type: outdoor, type: flame proof (flp), protection: ip class suitable for flp, minimum protection: ip-65, feature: with rcbo (residual current circuit breaker with overcurrent protection) | 1 | No. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 5.5 ¦ UPS DB - 230V, 50Hz,Outdoor type, Flame proof (FLP) Type, IP class suitable for FLP and minimum protection shall be IP-65, incomer 63A, 3 Phase, 4 wire, 3 Way LDB, 10kA for 1 sec with RCBO | ups db | db | voltage: 230v, frequency: 50hz, incomer: 63a, phase: 3 phase, wire: 4 wire, way: 3 way, short circuit rating: 10ka for 1 sec | type: outdoor, type: flame proof (flp), protection: ip class suitable for flp, minimum protection: ip-65, feature: with rcbo (residual current circuit breaker with overcurrent protection) | 1 | No. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 5.6 ¦ Feeder Pillar for street Lighting . 415V, 3Ph, 50Hz, Flame proof (IP class suitable for FLP and minimum protection shall be IP-65) sheet steel enclosure column/structural mounted, with photovoltic cell based control with A/M selector switch, start/stop PB, indicating lamps etc. with 3mm thick FRP canopy and side cover of the following incoming and outgoing feeders: i) 1no.-Incomer 63A, 3 phase RCBO 30 mA ii) 3nos.-O/G 16A TPN MCB | feeder pillar |  | voltage: 415v, phase: 3ph, frequency: 50hz, enclosure thickness: 3mm frp (fiber reinforced plastic) canopy and side cover, incomer: 63a, outgoing: 16a tpn mcb | type: flame proof, protection: ip class suitable for flp (flame proof), minimum protection: ip-65, enclosure: sheet steel, mounting: column/structural, control: photovoltic cell based, selector switch: a/m (auto/manual), feature: start/stop pb (push button), feature: indicating lamps, feature: with 1no.-incomer 63a, 3 phase rcbo 30 ma, feature: 3nos.-o/g (outgoing) 16a tpn (triple pole neutral) mcb (miniature circuit breaker) | 1 | No. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 5.7 ¦ PDB at outdoor location . 415V, 3Ph, 50Hz, W eatherproof and Flame proof (IP class suitable for FLP and minimum protection shall be IP-65) sheet steel enclosure column/structural mounted, start/stop PB, indicating lamps etc. with 3mm thick FRP canopy and side cover of the following incoming and outgoing feeders: i) 1no.-Incomer 100A TPN MCCB ii) 5nos.-O/G 32A TPN MCCB One outgoing shall be provided with photovoltic cell based control with A/M selector switch, start/stop PB, indicating lamps etc to feed the street light. | pdb | pdb | voltage: 415v, phase: 3ph, frequency: 50hz, enclosure thickness: 3mm frp (fiber reinforced plastic) canopy and side cover, incomer: 100a tpn mccb, outgoing: 32a tpn mccb | type: weatherproof, type: flame proof, protection: ip class suitable for flp (flame proof), minimum protection: ip-65, enclosure: sheet steel, mounting: column/structural, feature: start/stop pb (push button), feature: indicating lamps, feature: with 1no.-incomer 100a tpn (triple pole neutral) mccb (moulded case circuit breaker), feature: 5nos.-o/g (outgoing) 32a tpn mccb, feature: one outgoing with photovoltic cell based control with a/m (auto/manual) selector switch, start/stop pb, indicating lamps to feed the street light | 1 | No. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 6.1 ¦ 110V, 10A BATTERY CHARGER consisting of dual float cum boost charger and Ni-Cd type battery (43AH) with two hour back up capacity as per attached specifications & DS. | battery charger |  | voltage: 110v, current: 10a, battery capacity: 43ah, backup time: two hour | feature: dual float cum boost charger, battery type: ni-cd (nickel-cadmium), feature: as per attached specifications & ds (data sheet) | 1 | No. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 6.2 ¦ DC DISTRIBUTION BOARD: 110V DC, 2 wire 63A DC Distribution Board fed by duel float cum boost charger as per attached SLD, specifications & DS. Incomer: 63A DP MCB Outgoing: 15nos. 16A DP MCB | dc distribution board |  | voltage: 110v dc, wire: 2 wire, incomer: 63a dp mcb, outgoing: 15nos. 16a dp mcb | fed by: duel float cum boost charger, feature: as per attached sld (single line diagram), specifications & ds (data sheet) | 1 | No. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 7.1 ¦ Supply of Flameproof lighting fixtures, Lamps & Accessories as per attached specification. (All Lighting fixtures shall be provided with required no. of FLP double compression stainless steel cable glands and FLP stopping plug and control gear boxes etc. All fixtures shall have inbuilt JBs for loop in loop out facility of 3Cx2.5 sqmm Cu lighting cables) 230 Volt AC, 40W Well glass Flameproof Ex'd',LED lighting fixtures and all other accessories | flameproof lighting fixtures |  | voltage: 230 volt ac, power: 40w | type: well glass, type: flameproof ex'd', type: led, feature: with lamps & accessories, feature: as per attached specification, feature: provided with required no. of flp (flame proof) double compression stainless steel cable glands and flp stopping plug and control gear boxes, feature: inbuilt jbs (junction boxes) for loop in loop out facility of 3cx2.5 sqmm cu (copper) lighting cables | 135 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 7.2 ¦ Supply of weatherproof lighting fixtures, Lamps & Accessories as per attached specification. (All Lighting fixtures shall be provided with required no. of double compression stainless steel cable glands and stopping plug. All control gear boxes shall be provided with 3mm thick FRP canopy with side cover. .All fixtures shall have inbuilt JBs for loop in loop out facility of 3Cx2.5 sqmm Cu lighting cables) 230 Volt AC, 40W Well glass weatherproof ,LED lighting fixtures and all other accessories | weatherproof lighting fixtures |  | voltage: 230 volt ac, power: 40w | type: well glass, type: weatherproof, type: led, feature: with lamps & accessories, feature: as per attached specification, feature: provided with required no. of double compression stainless steel cable glands and stopping plug, feature: control gear boxes with 3mm thick frp (fiber reinforced plastic) canopy with side cover, feature: inbuilt jbs (junction boxes) for loop in loop out facility of 3cx2.5 sqmm cu (copper) lighting cables | 22 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 8.1 ¦ 240 Volt AC, 16 A, Cast Aluminium Flameproof Ex'd' (Zone-1, IIA / IIB) 4-way, 125 mm (minimum) internal dimensions junction box with terminals block suitable for 2.5 sq.mm along with flameproof double compression Ni plated brass cables glands for all incoming and outgoing cables,PVC shroud and other accessories. | junction box |  | voltage: 240 volt ac, current: 16 a, internal dimensions: 125 mm (minimum) | material: cast aluminium, type: flameproof ex'd' (flame proof ex'd'), zone: 1, gas group: iia or iib, configuration: 4-way, terminal block suitability: 2.5 sq.mm, cable glands: flameproof double compression ni (nickel) plated brass, accessories: pvc shroud and other accessories | 45 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 8.2 ¦ 240 Volt AC, 16 A, Cast Aluminium weatherproof 4-way, 125 mm (minimum) internal dimensions junction box with terminals block suitable for 2.5 sq.mm along with weatherproof double compression Ni plated brass cables glands for all incoming and outgoing cables,PVC shroud and other accessories. | junction box |  | voltage: 240 volt ac, current: 16 a, internal dimensions: 125 mm (minimum) | material: cast aluminium, type: weatherproof, configuration: 4-way, terminal block suitability: 2.5 sq.mm, cable glands: weatherproof double compression ni (nickel) plated brass, accessories: pvc shroud and other accessories | 18 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 8.3 ¦ JUNCTION BOXES FOR PUMP MOTOR (WEATHER PROOF, FLAME PROOF): Design, Supply, Installation, Testing and Commissionong of following 415V, 3P, Industrial type, W eatherproof, Flame proof “Ex-d” (suitable for hazardous area of gas group IIA/IIB, temperature class T3 and Zone-1), IP 65 suitable for Wall / Column / Structure mounting Including cabling from JB to terminal box for Star-Delta pump motor having different terminal for star and delta connection. All JBs shall be made up of cast Aluminium alloy (LM6 grade) with Canopy of 14 gauge CRCA sheet with side cover. JBs shall confirm to specification/data sheet of tender document. Junction Boxes shall be complete with busbar of suitable rating, support insulator, suitable for 2 nos. of 1RX 3.5 C X 150 Sqmm of Incoming cable size and 2 nos. of 1RX 3.5 C X 95 Sqmm of outgoing cable size XLPE insulated, extruded PVC inner & outer sheathed, FRLS, Armoured cables & shall be supplied along with FLP type double compression, Ni plated brass cable glands, lugs & plugs. However, exact cable sizes shall be indicated during drawing approval only. | junction boxes for pump motor |  | voltage: 415v, phase: 3p, incoming cable size: 2 nos. of 1rx 3.5 c x 150 sqmm, outgoing cable size: 2 nos. of 1rx 3.5 c x 95 sqmm | type: weatherproof, type: flame proof ex-d (explosion proof), hazardous area suitability: gas group iia/iib, temperature class: t3, zone: 1, ip rating: ip 65, mounting: wall or column or structure, material: cast aluminium alloy (lm6 grade), canopy: 14 gauge crca (cold rolled close annealed) sheet with side cover, busbar: suitable rating, support insulator: included, cable insulation: xlpe (cross-linked polyethylene), cable sheathing: extruded pvc inner & outer, cable type: frls (flame retardant low smoke), armoured, cable glands: flp (flame proof) type double compression ni (nickel) plated brass, lugs & plugs: included, specification: as per tender document | 1 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 9.1 ¦ Supply of flameproof Interlocking type switch sockets and plugs of following ratings as per attached specifications. All switch sockets shall be provided with 3mm thick FRP canopy with side cover and required no. of FLP double compression stainless steel cable glands and FLP stopping plug. i) 415V, 5-pin, 63A flame proof switch socket and plug | flameproof interlocking type switch sockets and plugs |  | voltage: 415v, pins: 5-pin, current: 63a | type: flame proof, feature: interlocking, specification: as per attached specifications, canopy: 3mm thick frp (fiber reinforced plastic) with side cover, cable glands: flp (flame proof) double compression stainless steel, flp stopping plug: included | 4 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 9.1 ¦ Supply of flameproof Interlocking type switch sockets and plugs of following ratings as per attached specifications. All switch sockets shall be provided with 3mm thick FRP canopy with side cover and required no. of FLP double compression stainless steel cable glands and FLP stopping plug. ii) 240V, 3-pin, 16A/5A flame proof switch socket and plug | flameproof interlocking type switch sockets and plugs |  | voltage: 240v, pins: 3-pin, current: 16a or 5a | type: flame proof, feature: interlocking, specification: as per attached specifications, canopy: 3mm thick frp (fiber reinforced plastic) with side cover, cable glands: flp (flame proof) double compression stainless steel, flp stopping plug: included | 6 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 9.2 ¦ Supply of weatherproof Interlocking type switch sockets and plugs of following ratings as per attached specifications. All switch sockets shall be provided with 3mm thick FRP canopy with side cover and required no. of double compression stainless steel cable glands and stopping plug. i) 415V, 5-pin, 63A weatherproof switch socket and plug | weatherproof interlocking type switch sockets and plugs |  | voltage: 415v, pins: 5-pin, current: 63a | type: weatherproof, feature: interlocking, specification: as per attached specifications, canopy: 3mm thick frp (fiber reinforced plastic) with side cover, cable glands: double compression stainless steel, stopping plug: included | 2 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 9.2 ¦ Supply of weatherproof Interlocking type switch sockets and plugs of following ratings as per attached specifications. All switch sockets shall be provided with 3mm thick FRP canopy with side cover and required no. of double compression stainless steel cable glands and stopping plug. ii) 240V, 3-pin, 16A/5A weatherproof switch socket and plug | weatherproof interlocking type switch sockets and plugs |  | voltage: 240v, pins: 3-pin, current: 16a or 5a | type: weatherproof, feature: interlocking, specification: as per attached specifications, canopy: 3mm thick frp (fiber reinforced plastic) with side cover, cable glands: double compression stainless steel, stopping plug: included | 2 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 10.1 ¦ Supply of PVC rigid conduit of min. 2mm thick wall, heavy duty type as per IS (with bends, reducers, couplers etc.) of following sizes:- 25 mm Dia. PVC Rigid Conduit | pvc rigid conduit |  | wall thickness: min. 2mm, diameter: 25 mm | type: heavy duty, standard: is (indian standard), accessories: bends, reducers, couplers etc. | 50 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 10.2 ¦ Supply of PVC rigid conduit of min. 2mm thick wall, heavy duty type as per IS (with bends, reducers, couplers etc.) of following sizes:- 50 mm Dia. PVC Rigid Conduit | pvc rigid conduit |  | wall thickness: min. 2mm, diameter: 50 mm | type: heavy duty, standard: is (indian standard), accessories: bends, reducers, couplers etc. | 150 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 10.3 ¦ Supply of PVC rigid conduit of min. 2mm thick wall, heavy duty type as per IS (with bends, reducers, couplers etc.) of following sizes:- 75 mm Dia. PVC Rigid Conduit | pvc rigid conduit |  | wall thickness: min. 2mm, diameter: 75 mm | type: heavy duty, standard: is (indian standard), accessories: bends, reducers, couplers etc. | 50 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 10.4 ¦ Supply of following PVC flexible conduit of min. 2mm thick wall, heavy duty type & as per IS: 2509. 25 mm Dia PVC Flexible Conduit | pvc flexible conduit |  | wall thickness: min. 2mm, diameter: 25 mm | type: heavy duty, standard: is 2509 (indian standard 2509) | 425 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | Lighting Cable ¦ 0.6/1 kV grade 3C X 2.5 Sqmm Cu XLPE insulated FRLS PVC sheathed Lighting Cable | lighting cable |  | voltage grade: 0.6/1 kv, cores: 3c, conductor size: 2.5 sqmm | conductor material: cu (copper), insulation: xlpe (cross-linked polyethylene), sheathing: frls (flame retardant low smoke) pvc (polyvinyl chloride) | 1800 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | LIGHTING POLES ¦ Supply of 9.5 Mtr lighting pole (polygonal type) for base mounting complete with all accessories like MCB & terminal block, JB (as applicable), Zinc passivated hardware for fixtures support & pole support, cable protection pipe with earthing rod/ wire as applicable, clamps, nuts, bolts, etc. | lighting pole |  | height: 9.5 mtr | type: polygonal, mounting: base, accessories: mcb (miniature circuit breaker) & terminal block, jb (junction box) as applicable, zinc passivated hardware for fixtures support & pole support, cable protection pipe with earthing rod or wire as applicable, clamps, nuts, bolts, etc. | 6 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | HIGH MAST LIGHTING TOWER ¦ Civil & Structural design, engineering & supply of hot dip galvanised High Mast lighting tower (30 m height) including all accessories for High Mast like 24 nos. of High mast lantern Carraige, 16 nos. of 350 watt LED fixture with lamp, head frame, stainless steel rope, double drum winch, Flameproof junction boxes, Flameproof plugs and sockets, Flameproof feeder pillar, galvanised lantern carrier arrangement, cables and cable accessories control panel for feeder pillar etc. as per specification, data sheet and direction of Engineer- in-charge ingincluding supply of commissioning and 2 years O&M spares. | high mast lighting tower |  | height: 30 m | finish: hot dip galvanised, accessories: 24 nos. high mast lantern carriage, 16 nos. 350 watt led fixture with lamp, head frame, stainless steel rope, double drum winch, flameproof junction boxes, flameproof plugs and sockets, flameproof feeder pillar, galvanised lantern carrier arrangement, cables and cable accessories, control panel for feeder pillar, commissioning and 2 years o&m (operation & maintenance) spares, specification: as per specification, data sheet and direction of engineer-in-charge | 4 | Nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14.1 ¦ SUPPLY OF HT/ LT CABLES AS PER ENCLOSED SPECIFICATION ¦ 11 KV(UE) Grade Cables as per typical specifications ; XLPE insulated; PVC Sheathed; Armoured Aluminium Conductor Cables of Following Sizes As Per Is:1554 (Part-I), IS 7098 Part I & IS 1225-Latest Version and Sealed properly with Pvc Caps of following size:- 3C x 240 sqmm (AL) | ht or lt cable |  | voltage grade: 11 kv(ue), cores: 3c, conductor size: 240 sqmm | insulation: xlpe (cross-linked polyethylene), sheathing: pvc (polyvinyl chloride), type: armoured, conductor material: aluminium, standard: is 1554 (part-i), is 7098 part i, is 1225-latest version, end sealing: pvc caps | 250 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14.2 ¦ SUPPLY OF HT/ LT CABLES AS PER ENCLOSED SPECIFICATION ¦ 1.1KV(E) XLPE insulated, FRLS, PVC sheathed aluminium/copper conductor, 1.1 kV grade armoured cable conforming to IS:7098, as per approved make AS PER ENCLOSED SPECIFICATIONS 1C x 400, Sqmm XLPE AL | ht or lt cable |  | voltage grade: 1.1kv(e), cores: 1c, conductor size: 400 sqmm | insulation: xlpe (cross-linked polyethylene), sheathing: frls (flame retardant low smoke) pvc (polyvinyl chloride), conductor material: aluminium or copper, type: armoured, standard: is 7098 (indian standard 7098), specification: as per approved make, as per enclosed specifications | 1010 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14.3 ¦ SUPPLY OF HT/ LT CABLES AS PER ENCLOSED SPECIFICATION ¦ 1.1KV(E) XLPE insulated, FRLS, PVC sheathed aluminium/copper conductor, 1.1 kV grade armoured cable conforming to IS:7098, as per approved make AS PER ENCLOSED SPECIFICATIONS 3.5C x 150, Sqmm XLPE AL | ht or lt cable |  | voltage grade: 1.1kv(e), cores: 3.5c, conductor size: 150 sqmm | insulation: xlpe (cross-linked polyethylene), sheathing: frls (flame retardant low smoke) pvc (polyvinyl chloride), conductor material: aluminium or copper, type: armoured, standard: is 7098 (indian standard 7098), specification: as per approved make, as per enclosed specifications | 100 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14.4 ¦ SUPPLY OF HT/ LT CABLES AS PER ENCLOSED SPECIFICATION ¦ 1.1KV(E) XLPE insulated, FRLS, PVC sheathed aluminium/copper conductor, 1.1 kV grade armoured cable conforming to IS:7098, as per approved make AS PER ENCLOSED SPECIFICATIONS 3.5C x 95, Sqmm XLPE AL | ht or lt cable |  | voltage grade: 1.1kv(e), cores: 3.5c, conductor size: 95 sqmm | insulation: xlpe (cross-linked polyethylene), sheathing: frls (flame retardant low smoke) pvc (polyvinyl chloride), conductor material: aluminium or copper, type: armoured, standard: is 7098 (indian standard 7098), specification: as per approved make, as per enclosed specifications | 500 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14.5 ¦ SUPPLY OF HT/ LT CABLES AS PER ENCLOSED SPECIFICATION ¦ 3.5C X 50, Sqmm XLPE AL | ht or lt cable |  | cores: 3.5c, conductor size: 50 sqmm | insulation: xlpe (cross-linked polyethylene), conductor material: aluminium | 3000 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14.6 ¦ SUPPLY OF HT/ LT CABLES AS PER ENCLOSED SPECIFICATION ¦ 4C X 25, Sqmm XLPE AL | ht or lt cable |  | cores: 4c, conductor size: 25 sqmm | insulation: xlpe (cross-linked polyethylene), conductor material: aluminium | 6800 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14.7 ¦ SUPPLY OF HT/ LT CABLES AS PER ENCLOSED SPECIFICATION ¦ 4C X 16, Sqmm XLPE AL | ht or lt cable |  | cores: 4c, conductor size: 16 sqmm | insulation: xlpe (cross-linked polyethylene), conductor material: aluminium | 600 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14.8 ¦ SUPPLY OF HT/ LT CABLES AS PER ENCLOSED SPECIFICATION ¦ 4C X 10, Sqmm XLPE AL | ht or lt cable |  | cores: 4c, conductor size: 10 sqmm | insulation: xlpe (cross-linked polyethylene), conductor material: aluminium | 100 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14.9 ¦ SUPPLY OF HT/ LT CABLES AS PER ENCLOSED SPECIFICATION ¦ 4C X 6, Sqmm XLPE AL | ht or lt cable |  | cores: 4c, conductor size: 6 sqmm | insulation: xlpe (cross-linked polyethylene), conductor material: aluminium | 8000 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14.1 ¦ SUPPLY OF HT/ LT CABLES AS PER ENCLOSED SPECIFICATION ¦ 4C X 4, Sqmm XLPE AL | ht or lt cable |  | cores: 4c, conductor size: 4 sqmm | insulation: xlpe (cross-linked polyethylene), conductor material: aluminium | 3100 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14.11 ¦ SUPPLY OF HT/ LT CABLES AS PER ENCLOSED SPECIFICATION ¦ 4C X 2.5, Sqmm XLPE AL | ht or lt cable |  | cores: 4c, conductor size: 2.5 sqmm | insulation: xlpe (cross-linked polyethylene), conductor material: aluminium | 2200 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14.12 ¦ SUPPLY OF HT/ LT CABLES AS PER ENCLOSED SPECIFICATION ¦ 3C X 6, Sqmm XLPE AL | ht or lt cable |  | cores: 3c, conductor size: 6 sqmm | insulation: xlpe (cross-linked polyethylene), conductor material: aluminium | 400 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14.13 ¦ SUPPLY OF HT/ LT CABLES AS PER ENCLOSED SPECIFICATION ¦ 3C X 2.5, Sqmm XLPE AL | ht or lt cable |  | cores: 3c, conductor size: 2.5 sqmm | insulation: xlpe (cross-linked polyethylene), conductor material: aluminium | 100 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14.14 ¦ SUPPLY OF HT/ LT CABLES AS PER ENCLOSED SPECIFICATION ¦ 2C X 4, Sqmm XLPE AL | ht or lt cable |  | cores: 2c, conductor size: 4 sqmm | insulation: xlpe (cross-linked polyethylene), conductor material: aluminium | 200 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14.15 ¦ SUPPLY OF HT/ LT CABLES AS PER ENCLOSED SPECIFICATION ¦ 2C X 16, Sqmm XLPE AL | ht or lt cable |  | cores: 2c, conductor size: 16 sqmm | insulation: xlpe (cross-linked polyethylene), conductor material: aluminium | 900 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14.16 ¦ 1.1KV(E) armoured XLPE, FRLS Control Cable of following size:- 7C x 2.5 SQMM CU | control cable |  | voltage grade: 1.1kv(e), cores: 7c, conductor size: 2.5 sqmm | type: armoured, insulation: xlpe (cross-linked polyethylene), sheathing: frls (flame retardant low smoke), conductor material: copper | 27000 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 14.17 ¦ 1.1KV(E) armoured XLPE, FRLS Control Cable of following size:- 3C x 2.5 SQMM CU | control cable |  | voltage grade: 1.1kv(e), cores: 3c, conductor size: 2.5 sqmm | type: armoured, insulation: xlpe (cross-linked polyethylene), sheathing: frls (flame retardant low smoke), conductor material: copper | 800 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 15.1 ¦ Supply of Flameproof double compression stainless steel cable gland suitable for following XLPE , FRLS cable sizes & as per relevant IS for hazardous area. 3.5C x 150, Sqmm XLPE AL | cable gland |  | cores: 3.5c, conductor size: 150 sqmm | feature: flameproof, type: double compression, material: stainless steel, suitability: xlpe (cross-linked polyethylene) and frls (flame retardant low smoke) cable sizes, standard: relevant indian standard, application: hazardous area | 5 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 15.2 ¦ Supply of Flameproof double compression stainless steel cable gland suitable for following XLPE , FRLS cable sizes & as per relevant IS for hazardous area. 3.5C x 95, Sqmm XLPE AL | cable gland |  | cores: 3.5c, conductor size: 95 sqmm | feature: flameproof, type: double compression, material: stainless steel, suitability: xlpe (cross-linked polyethylene) and frls (flame retardant low smoke) cable sizes, standard: relevant indian standard, application: hazardous area | 5 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 15.3 ¦ Supply of Flameproof double compression stainless steel cable gland suitable for following XLPE , FRLS cable sizes & as per relevant IS for hazardous area. 3.5C X 50, Sqmm XLPE AL | cable gland |  | cores: 3.5c, conductor size: 50 sqmm | feature: flameproof, type: double compression, material: stainless steel, suitability: xlpe (cross-linked polyethylene) and frls (flame retardant low smoke) cable sizes, standard: relevant indian standard, application: hazardous area | 20 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 15.4 ¦ Supply of Flameproof double compression stainless steel cable gland suitable for following XLPE , FRLS cable sizes & as per relevant IS for hazardous area. 4C X 25, Sqmm XLPE AL | cable gland |  | cores: 4c, conductor size: 25 sqmm | feature: flameproof, type: double compression, material: stainless steel, suitability: xlpe (cross-linked polyethylene) and frls (flame retardant low smoke) cable sizes, standard: relevant indian standard, application: hazardous area | 50 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 15.5 ¦ Supply of Flameproof double compression stainless steel cable gland suitable for following XLPE , FRLS cable sizes & as per relevant IS for hazardous area. 4C X 16, Sqmm XLPE AL | cable gland |  | cores: 4c, conductor size: 16 sqmm | feature: flameproof, type: double compression, material: stainless steel, suitability: xlpe (cross-linked polyethylene) and frls (flame retardant low smoke) cable sizes, standard: relevant indian standard, application: hazardous area | 50 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 15.6 ¦ Supply of Flameproof double compression stainless steel cable gland suitable for following XLPE , FRLS cable sizes & as per relevant IS for hazardous area. 4C X 10, Sqmm XLPE AL | cable gland |  | cores: 4c, conductor size: 10 sqmm | feature: flameproof, type: double compression, material: stainless steel, suitability: xlpe (cross-linked polyethylene) and frls (flame retardant low smoke) cable sizes, standard: relevant indian standard, application: hazardous area | 4 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 15.7 ¦ Supply of Flameproof double compression stainless steel cable gland suitable for following XLPE , FRLS cable sizes & as per relevant IS for hazardous area. 4C X 6, Sqmm XLPE AL | cable gland |  | cores: 4c, conductor size: 6 sqmm | feature: flameproof, type: double compression, material: stainless steel, suitability: xlpe (cross-linked polyethylene) and frls (flame retardant low smoke) cable sizes, standard: relevant indian standard, application: hazardous area | 60 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 15.8 ¦ Supply of Flameproof double compression stainless steel cable gland suitable for following XLPE , FRLS cable sizes & as per relevant IS for hazardous area. 4C X 4, Sqmm XLPE AL | cable gland |  | cores: 4c, conductor size: 4 sqmm | feature: flameproof, type: double compression, material: stainless steel, suitability: xlpe (cross-linked polyethylene) and frls (flame retardant low smoke) cable sizes, standard: relevant indian standard, application: hazardous area | 15 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 15.9 ¦ Supply of Flameproof double compression stainless steel cable gland suitable for following XLPE , FRLS cable sizes & as per relevant IS for hazardous area. 4C X 2.5, Sqmm XLPE AL | cable gland |  | cores: 4c, conductor size: 2.5 sqmm | feature: flameproof, type: double compression, material: stainless steel, suitability: xlpe (cross-linked polyethylene) and frls (flame retardant low smoke) cable sizes, standard: relevant indian standard, application: hazardous area | 16 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 15.1 ¦ Supply of Flameproof double compression stainless steel cable gland suitable for following XLPE , FRLS cable sizes & as per relevant IS for hazardous area. 3C X 2.5, Sqmm XLPE AL | cable gland |  | cores: 3c, conductor size: 2.5 sqmm | feature: flameproof, type: double compression, material: stainless steel, suitability: xlpe (cross-linked polyethylene) and frls (flame retardant low smoke) cable sizes, standard: relevant indian standard, application: hazardous area | 5 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 15.11 ¦ Supply of Flameproof double compression stainless steel cable gland suitable for following XLPE , FRLS cable sizes & as per relevant IS for hazardous area. 3C X 6, Sqmm XLPE AL | cable gland |  | cores: 3c, conductor size: 6 sqmm | feature: flameproof, type: double compression, material: stainless steel, suitability: xlpe (cross-linked polyethylene) and frls (flame retardant low smoke) cable sizes, standard: relevant indian standard, application: hazardous area | 10 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 15.12 ¦ Supply of Flameproof double compression stainless steel cable gland suitable for following XLPE , FRLS cable sizes & as per relevant IS for hazardous area. 2C X 4, Sqmm XLPE AL | cable gland |  | cores: 2c, conductor size: 4 sqmm | feature: flameproof, type: double compression, material: stainless steel, suitability: xlpe (cross-linked polyethylene) and frls (flame retardant low smoke) cable sizes, standard: relevant indian standard, application: hazardous area | 4 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 15.13 ¦ Supply of Flameproof double compression stainless steel cable gland suitable for following XLPE , FRLS cable sizes & as per relevant IS for hazardous area. 2C X 16, Sqmm XLPE AL | cable gland |  | cores: 2c, conductor size: 16 sqmm | feature: flameproof, type: double compression, material: stainless steel, suitability: xlpe (cross-linked polyethylene) and frls (flame retardant low smoke) cable sizes, standard: relevant indian standard, application: hazardous area | 4 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 15.14 ¦ Supply of Flameproof double compression stainless steel cable gland suitable for following XLPE , FRLS cable sizes & as per relevant IS for hazardous area. 7C x 2.5 SQMM CU | cable gland |  | cores: 7c, conductor size: 2.5 sqmm | feature: flameproof, type: double compression, material: stainless steel, suitability: xlpe (cross-linked polyethylene) and frls (flame retardant low smoke) cable sizes, standard: relevant indian standard, application: hazardous area | 70 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 15.15 ¦ Supply of Flameproof double compression stainless steel cable gland suitable for following XLPE , FRLS cable sizes & as per relevant IS for hazardous area. 3C x 2.5 SQMM CU | cable gland |  | cores: 3c, conductor size: 2.5 sqmm | feature: flameproof, type: double compression, material: stainless steel, suitability: xlpe (cross-linked polyethylene) and frls (flame retardant low smoke) cable sizes, standard: relevant indian standard, application: hazardous area | 10 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 15.16 ¦ Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 1C x 400, Sqmm XLPE AL | cable gland |  | cores: 1c, conductor size: 400 sqmm | type: double compression, material: stainless steel, suitability: xlpe (cross-linked polyethylene) and frls (flame retardant low smoke) cable sizes, standard: relevant indian standard, application: indoor use | 60 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 15.17 ¦ Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 3.5C x 150, Sqmm XLPE AL | cable gland |  | cores: 3.5c, conductor size: 150 sqmm | type: double compression, material: stainless steel, suitability: xlpe (cross-linked polyethylene) and frls (flame retardant low smoke) cable sizes, standard: relevant indian standard, application: indoor use | 6 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 15.18 ¦ Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 3.5C x 95, Sqmm XLPE AL | cable gland |  | cores: 3.5c, conductor size: 95 sqmm | type: double compression, material: stainless steel, suitability: xlpe (cross-linked polyethylene) and frls (flame retardant low smoke) cable sizes, standard: relevant indian standard, application: indoor use | 5 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 15.19 ¦ Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 3.5C X 50, Sqmm XLPE AL | cable gland |  | cores: 3.5c, conductor size: 50 sqmm | type: double compression, material: stainless steel, suitability: xlpe (cross-linked polyethylene) and frls (flame retardant low smoke) cable sizes, standard: relevant indian standard, application: indoor use | 22 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 15.2 ¦ Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 4C X 25, Sqmm XLPE AL | cable gland |  | cores: 4c, conductor size: 25 sqmm | type: double compression, material: stainless steel, suitability: xlpe (cross-linked polyethylene) and frls (flame retardant low smoke) cable sizes, standard: relevant indian standard, application: indoor use | 50 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 15.21 ¦ Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 4C X 16, Sqmm XLPE AL | cable gland |  | cores: 4c, conductor size: 16 sqmm | type: double compression, material: stainless steel, suitability: xlpe (cross-linked polyethylene) and frls (flame retardant low smoke) cable sizes, standard: relevant indian standard, application: indoor use | 50 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 15.22 ¦ Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 4C X 10, Sqmm XLPE AL | cable gland |  | cores: 4c, conductor size: 10 sqmm | type: double compression, material: stainless steel, suitability: xlpe (cross-linked polyethylene) and frls (flame retardant low smoke) cable sizes, standard: relevant indian standard, application: indoor use | 4 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 15.23 ¦ Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 4C X 6, Sqmm XLPE AL | cable gland |  | cores: 4c, conductor size: 6 sqmm | type: double compression, material: stainless steel, suitability: xlpe (cross-linked polyethylene) and frls (flame retardant low smoke) cable sizes, standard: relevant indian standard, application: indoor use | 60 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 15.24 ¦ Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 4C X 4, Sqmm XLPE AL | cable gland |  | cores: 4c, conductor size: 4 sqmm | type: double compression, material: stainless steel, suitability: xlpe (cross-linked polyethylene) and frls (flame retardant low smoke) cable sizes, standard: relevant indian standard, application: indoor use | 15 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 15.25 ¦ Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 4C X 2.5, Sqmm XLPE AL | cable gland |  | cores: 4c, conductor size: 2.5 sqmm | type: double compression, material: stainless steel, suitability: xlpe (cross-linked polyethylene) and frls (flame retardant low smoke) cable sizes, standard: relevant indian standard, application: indoor use | 16 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 15.26 ¦ Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 3C X 2.5, Sqmm XLPE AL | cable gland |  | cores: 3c, conductor size: 2.5 sqmm | type: double compression, material: stainless steel, suitability: xlpe (cross-linked polyethylene) and frls (flame retardant low smoke) cable sizes, standard: relevant indian standard, application: indoor use | 5 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 15.27 ¦ Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 3C X 6, Sqmm XLPE AL | cable gland |  | cores: 3c, conductor size: 6 sqmm | type: double compression, material: stainless steel, suitability: xlpe (cross-linked polyethylene) and frls (flame retardant low smoke) cable sizes, standard: relevant indian standard, application: indoor use | 10 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 15.28 ¦ Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 2C X 4, Sqmm XLPE AL | cable gland |  | cores: 2c, conductor size: 4 sqmm | type: double compression, material: stainless steel, suitability: xlpe (cross-linked polyethylene) and frls (flame retardant low smoke) cable sizes, standard: relevant indian standard, application: indoor use | 4 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 15.29 ¦ Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 2C X 16, Sqmm XLPE AL | cable gland |  | cores: 2c, conductor size: 16 sqmm | type: double compression, material: stainless steel, suitability: xlpe (cross-linked polyethylene) and frls (flame retardant low smoke) cable sizes, standard: relevant indian standard, application: indoor use | 4 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 15.3 ¦ Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 7C x 2.5 SQMM CU | cable gland |  | cores: 7c, conductor size: 2.5 sqmm | type: double compression, material: stainless steel, suitability: xlpe (cross-linked polyethylene) and frls (flame retardant low smoke) cable sizes, standard: relevant indian standard, application: indoor use | 70 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 15.31 ¦ Supply of double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use. 3C x 2.5 SQMM CU | cable gland |  | cores: 3c, conductor size: 2.5 sqmm | type: double compression, material: stainless steel, suitability: xlpe (cross-linked polyethylene) and frls (flame retardant low smoke) cable sizes, standard: relevant indian standard, application: indoor use | 10 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 15.32 ¦ Supply of Raychem make heat shrinkable end termination kit suitable for 11 KV (UE) XLPE, FRLS cables of following sizes. 3C x 240 sqmm (AL) ( suitable for outdoor purpose) | end termination kit |  | cores: 3c, conductor size: 240 sqmm | manufacturer: raychem, type: heat shrinkable, suitability: 11 kv (ue) xlpe (cross-linked polyethylene) and frls (flame retardant low smoke) cables, application: outdoor purpose | 1 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 15.34 ¦ Supply of Raychem make heat shrinkable end termination kit suitable for 11 KV (UE) XLPE, FRLS cables of following sizes. 3C x 240 sqmm (AL) ( suitable for indoor purpose) | end termination kit |  | cores: 3c, conductor size: 240 sqmm | manufacturer: raychem, type: heat shrinkable, suitability: 11 kv (ue) xlpe (cross-linked polyethylene) and frls (flame retardant low smoke) cables, application: indoor purpose | 3 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 16.1 ¦ Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 3.5C x 150, Sqmm XLPE AL | cable lugs |  | cores: 3.5c, conductor size: 150 sqmm | type: crimping, feature: heavy duty, barrel: long, finish: tinned, feature: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cables | 25 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 16.2 ¦ Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 3.5C x 95, Sqmm XLPE AL | cable lugs |  | cores: 3.5c, conductor size: 95 sqmm | type: crimping, feature: heavy duty, barrel: long, finish: tinned, feature: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cables | 20 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 16.3 ¦ Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 3.5C X 50, Sqmm XLPE AL | cable lugs |  | cores: 3.5c, conductor size: 50 sqmm | type: crimping, feature: heavy duty, barrel: long, finish: tinned, feature: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cables | 80 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 16.4 ¦ Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 4C X 25, Sqmm XLPE AL | cable lugs |  | cores: 4c, conductor size: 25 sqmm | type: crimping, feature: heavy duty, barrel: long, finish: tinned, feature: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cables | 200 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 16.5 ¦ Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 4C X 16, Sqmm XLPE AL | cable lugs |  | cores: 4c, conductor size: 16 sqmm | type: crimping, feature: heavy duty, barrel: long, finish: tinned, feature: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cables | 200 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 16.6 ¦ Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 4C X 10, Sqmm XLPE AL | cable lugs |  | cores: 4c, conductor size: 10 sqmm | type: crimping, feature: heavy duty, barrel: long, finish: tinned, feature: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cables | 8 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 16.7 ¦ Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 4C X 6, Sqmm XLPE AL | cable lugs |  | cores: 4c, conductor size: 6 sqmm | type: crimping, feature: heavy duty, barrel: long, finish: tinned, feature: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cables | 240 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 16.8 ¦ Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 4C X 4, Sqmm XLPE AL | cable lugs |  | cores: 4c, conductor size: 4 sqmm | type: crimping, feature: heavy duty, barrel: long, finish: tinned, feature: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cables | 60 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 16.8 ¦ Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 4C X 2.5, Sqmm XLPE AL | cable lugs |  | cores: 4c, conductor size: 2.5 sqmm | type: crimping, feature: heavy duty, barrel: long, finish: tinned, feature: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cables | 64 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 16.9 ¦ Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 3C X 2.5, Sqmm XLPE AL | cable lugs |  | cores: 3c, conductor size: 2.5 sqmm | type: crimping, feature: heavy duty, barrel: long, finish: tinned, feature: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cables | 12 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 16.1 ¦ Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 3C X 6, Sqmm XLPE AL | cable lugs |  | cores: 3c, conductor size: 6 sqmm | type: crimping, feature: heavy duty, barrel: long, finish: tinned, feature: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cables | 15 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 16.11 ¦ Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 2C X 4, Sqmm XLPE AL | cable lugs |  | cores: 2c, conductor size: 4 sqmm | type: crimping, feature: heavy duty, barrel: long, finish: tinned, feature: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cables | 8 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 16.12 ¦ Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 2C X 16, Sqmm XLPE AL | cable lugs |  | cores: 2c, conductor size: 16 sqmm | type: crimping, feature: heavy duty, barrel: long, finish: tinned, feature: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cables | 16 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 16.13 ¦ Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 7C x 2.5 SQMM CU | cable lugs |  | cores: 7c, conductor size: 2.5 sqmm | type: crimping, feature: heavy duty, barrel: long, finish: tinned, feature: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cables | 500 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 16.14 ¦ Supply of crimping type heavy duty, long barrel Tinned, Flameproof type Cu /Al lugs for all Al and Cu cables as the case may be for the following size:- 3C x 2.5 SQMM CU | cable lugs |  | cores: 3c, conductor size: 2.5 sqmm | type: crimping, feature: heavy duty, barrel: long, finish: tinned, feature: flameproof, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: xlpe (cross-linked polyethylene) cables | 100 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | nan ¦ Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- | cable lugs |  |  | type: crimping, feature: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: indoor use |  |  | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 16.15 ¦ Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 1C x 400, Sqmm XLPE AL | cable lugs |  | cores: 1c, conductor size: 400 sqmm | type: crimping, feature: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: indoor use, suitability: xlpe (cross-linked polyethylene) cables | 60 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 16.16 ¦ Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 3.5C x 150, Sqmm XLPE AL | cable lugs |  | cores: 3.5c, conductor size: 150 sqmm | type: crimping, feature: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: indoor use, suitability: xlpe (cross-linked polyethylene) cables | 25 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 16.17 ¦ Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 3.5C x 95, Sqmm XLPE AL | cable lugs |  | cores: 3.5c, conductor size: 95 sqmm | type: crimping, feature: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: indoor use, suitability: xlpe (cross-linked polyethylene) cables | 20 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 16.18 ¦ Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 3.5C X 50, Sqmm XLPE AL | cable lugs |  | cores: 3.5c, conductor size: 50 sqmm | type: crimping, feature: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: indoor use, suitability: xlpe (cross-linked polyethylene) cables | 80 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 16.19 ¦ Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 4C X 25, Sqmm XLPE AL | cable lugs |  | cores: 4c, conductor size: 25 sqmm | type: crimping, feature: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: indoor use, suitability: xlpe (cross-linked polyethylene) cables | 200 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 16.2 ¦ Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 4C X 16, Sqmm XLPE AL | cable lugs |  | cores: 4c, conductor size: 16 sqmm | type: crimping, feature: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: indoor use, suitability: xlpe (cross-linked polyethylene) cables | 200 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 16.21 ¦ Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 4C X 10, Sqmm XLPE AL | cable lugs |  | cores: 4c, conductor size: 10 sqmm | type: crimping, feature: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: indoor use, suitability: xlpe (cross-linked polyethylene) cables | 8 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 16.22 ¦ Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 4C X 6, Sqmm XLPE AL | cable lugs |  | cores: 4c, conductor size: 6 sqmm | type: crimping, feature: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: indoor use, suitability: xlpe (cross-linked polyethylene) cables | 240 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 16.23 ¦ Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 4C X 4, Sqmm XLPE AL | cable lugs |  | cores: 4c, conductor size: 4 sqmm | type: crimping, feature: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: indoor use, suitability: xlpe (cross-linked polyethylene) cables | 60 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 16.24 ¦ Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 4C X 2.5, Sqmm XLPE AL | cable lugs |  | cores: 4c, conductor size: 2.5 sqmm | type: crimping, feature: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: indoor use, suitability: xlpe (cross-linked polyethylene) cables | 64 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 16.25 ¦ Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 3C X 2.5, Sqmm XLPE AL | cable lugs |  | cores: 3c, conductor size: 2.5 sqmm | type: crimping, feature: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: indoor use, suitability: xlpe (cross-linked polyethylene) cables | 12 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 16.26 ¦ Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 3C X 6, Sqmm XLPE AL | cable lugs |  | cores: 3c, conductor size: 6 sqmm | type: crimping, feature: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: indoor use, suitability: xlpe (cross-linked polyethylene) cables | 15 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 16.27 ¦ Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 2C X 4, Sqmm XLPE AL | cable lugs |  | cores: 2c, conductor size: 4 sqmm | type: crimping, feature: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: indoor use, suitability: xlpe (cross-linked polyethylene) cables | 8 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 16.28 ¦ Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 2C X 16, Sqmm XLPE AL | cable lugs |  | cores: 2c, conductor size: 16 sqmm | type: crimping, feature: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: indoor use, suitability: xlpe (cross-linked polyethylene) cables | 16 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 16.29 ¦ Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 7C x 2.5 SQMM CU | cable lugs |  | cores: 7c, conductor size: 2.5 sqmm | type: crimping, feature: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: indoor use | 500 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 16.3 ¦ Supply of crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:- 3C x 2.5 SQMM CU | cable lugs |  | cores: 3c, conductor size: 2.5 sqmm | type: crimping, feature: heavy duty, barrel: long, finish: tinned, material: copper or aluminium, suitability: all aluminium and copper cables, suitability: indoor use | 100 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.1 ¦ Ladder type GI cable tray (100mmx2mm, 3 Meter length) with minimum hot dip zinc coating 75 micron with accessories like coupler plates,bends, Stainless steels hardwares like nuts & bolts , bends, washers etc and as per IS & ES:8161. a. ¦ 750mm Wide | ladder type galvanized iron cable tray | gi cable tray | width: 750 mm, thickness: 2 mm, length: 3 meter | coating: hot dip zinc, coating thickness: 75 micron, accessories: coupler plates, accessories: bends, accessories: stainless steel hardwares (nuts & bolts, washers), standard: indian standard & engineering standard 8161 | 40 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.1 ¦ Ladder type GI cable tray (100mmx2mm, 3 Meter length) with minimum hot dip zinc coating 75 micron with accessories like coupler plates,bends, Stainless steels hardwares like nuts & bolts , bends, washers etc and as per IS & ES:8161. b. ¦ 600mm Wide | ladder type galvanized iron cable tray | gi cable tray | width: 600 mm, thickness: 2 mm, length: 3 meter | coating: hot dip zinc, coating thickness: 75 micron, accessories: coupler plates, accessories: bends, accessories: stainless steel hardwares (nuts & bolts, washers), standard: indian standard & engineering standard 8161 | 300 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.1 ¦ Ladder type GI cable tray (100mmx2mm, 3 Meter length) with minimum hot dip zinc coating 75 micron with accessories like coupler plates,bends, Stainless steels hardwares like nuts & bolts , bends, washers etc and as per IS & ES:8161. c. ¦ 300mm Wide | ladder type galvanized iron cable tray | gi cable tray | width: 300 mm, thickness: 2 mm, length: 3 meter | coating: hot dip zinc, coating thickness: 75 micron, accessories: coupler plates, accessories: bends, accessories: stainless steel hardwares (nuts & bolts, washers), standard: indian standard & engineering standard 8161 | 200 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.1 ¦ Ladder type GI cable tray (100mmx2mm, 3 Meter length) with minimum hot dip zinc coating 75 micron with accessories like coupler plates,bends, Stainless steels hardwares like nuts & bolts , bends, washers etc and as per IS & ES:8161. d. ¦ 150mm Wide | ladder type galvanized iron cable tray | gi cable tray | width: 150 mm, thickness: 2 mm, length: 3 meter | coating: hot dip zinc, coating thickness: 75 micron, accessories: coupler plates, accessories: bends, accessories: stainless steel hardwares (nuts & bolts, washers), standard: indian standard & engineering standard 8161 | 228 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.1 ¦ Ladder type GI cable tray (100mmx2mm, 3 Meter length) with minimum hot dip zinc coating 75 micron with accessories like coupler plates,bends, Stainless steels hardwares like nuts & bolts , bends, washers etc and as per IS & ES:8161. e. ¦ 50mm Wide | ladder type galvanized iron cable tray | gi cable tray | width: 50 mm, thickness: 2 mm, length: 3 meter | coating: hot dip zinc, coating thickness: 75 micron, accessories: coupler plates, accessories: bends, accessories: stainless steel hardwares (nuts & bolts, washers), standard: indian standard & engineering standard 8161 | 100 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.2 ¦ 90 deg Horizontal Bend Ladder type (shall be decided as per detail engineering) a. ¦ 750mm Wide | ladder type cable tray horizontal bend |  | width: 750 mm | bend angle: 90 degree, type: ladder, feature: shall be decided as per detail engineering | 4 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.2 ¦ 90 deg Horizontal Bend Ladder type (shall be decided as per detail engineering) b. ¦ 600mm Wide | ladder type cable tray horizontal bend |  | width: 600 mm | bend angle: 90 degree, type: ladder, feature: shall be decided as per detail engineering | 16 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.2 ¦ 90 deg Horizontal Bend Ladder type (shall be decided as per detail engineering) c. ¦ 300mm Wide | ladder type cable tray horizontal bend |  | width: 300 mm | bend angle: 90 degree, type: ladder, feature: shall be decided as per detail engineering | 8 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.2 ¦ 90 deg Horizontal Bend Ladder type (shall be decided as per detail engineering) d. ¦ 150mm Wide | ladder type cable tray horizontal bend |  | width: 150 mm | bend angle: 90 degree, type: ladder, feature: shall be decided as per detail engineering | 5 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.3 ¦ TEE Connection Ladder type (shall be decided as per detail engineering) a. ¦ 600mm Wide | ladder type cable tray tee connection |  | width: 600 mm | feature: shall be decided as per detail engineering | 16 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.3 ¦ TEE Connection Ladder type (shall be decided as per detail engineering) b. ¦ 300mm Wide | ladder type cable tray tee connection |  | width: 300 mm | feature: shall be decided as per detail engineering | 5 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.4 ¦ 90 deg Vertical Bend (inside) Ladder (shall be decided as per detail engineering) a. ¦ 600mm Wide | ladder type cable tray vertical bend (inside) |  | width: 600 mm | bend angle: 90 degree, type: ladder, position: inside, feature: shall be decided as per detail engineering | 10 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.4 ¦ 90 deg Vertical Bend (inside) Ladder (shall be decided as per detail engineering) b. ¦ 300mm Wide | ladder type cable tray vertical bend (inside) |  | width: 300 mm | bend angle: 90 degree, type: ladder, position: inside, feature: shall be decided as per detail engineering | 2 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.5 ¦ 90 deg Vertical Bend (outside) Perforated (shall be decided as per detail engineering) a. ¦ 600mm Wide | perforated cable tray vertical bend (outside) |  | width: 600 mm | bend angle: 90 degree, type: perforated, position: outside, feature: shall be decided as per detail engineering | 10 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.5 ¦ 90 deg Vertical Bend (outside) Perforated (shall be decided as per detail engineering) b. ¦ 300mm Wide | perforated cable tray vertical bend (outside) |  | width: 300 mm | bend angle: 90 degree, type: perforated, position: outside, feature: shall be decided as per detail engineering | 2 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.6 ¦ G.I. Perforated Cable Trays , 100 mm deep, 3 mm thick G.I. perforated cable trays (Min. coating 100 microns of zinc) with bend, reducer, coupler plate and other hardware. a. ¦ 750mm Wide | galvanized iron perforated cable tray | gi perforated cable tray | depth: 100 mm, thickness: 3 mm, width: 750 mm | coating: zinc, coating thickness: 100 micron, accessories: bend, accessories: reducer, accessories: coupler plate, accessories: other hardware | 10 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.6 ¦ G.I. Perforated Cable Trays , 100 mm deep, 3 mm thick G.I. perforated cable trays (Min. coating 100 microns of zinc) with bend, reducer, coupler plate and other hardware. b. ¦ 600mm Wide | galvanized iron perforated cable tray | gi perforated cable tray | depth: 100 mm, thickness: 3 mm, width: 600 mm | coating: zinc, coating thickness: 100 micron, accessories: bend, accessories: reducer, accessories: coupler plate, accessories: other hardware | 550 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.6 ¦ G.I. Perforated Cable Trays , 100 mm deep, 3 mm thick G.I. perforated cable trays (Min. coating 100 microns of zinc) with bend, reducer, coupler plate and other hardware. c. ¦ 300mm Wide | galvanized iron perforated cable tray | gi perforated cable tray | depth: 100 mm, thickness: 3 mm, width: 300 mm | coating: zinc, coating thickness: 100 micron, accessories: bend, accessories: reducer, accessories: coupler plate, accessories: other hardware | 175 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.6 ¦ G.I. Perforated Cable Trays , 100 mm deep, 3 mm thick G.I. perforated cable trays (Min. coating 100 microns of zinc) with bend, reducer, coupler plate and other hardware. d. ¦ 150mm Wide | galvanized iron perforated cable tray | gi perforated cable tray | depth: 100 mm, thickness: 3 mm, width: 150 mm | coating: zinc, coating thickness: 100 micron, accessories: bend, accessories: reducer, accessories: coupler plate, accessories: other hardware | 350 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.6 ¦ G.I. Perforated Cable Trays , 100 mm deep, 3 mm thick G.I. perforated cable trays (Min. coating 100 microns of zinc) with bend, reducer, coupler plate and other hardware. e. ¦ 50mm Wide | galvanized iron perforated cable tray | gi perforated cable tray | depth: 100 mm, thickness: 3 mm, width: 50 mm | coating: zinc, coating thickness: 100 micron, accessories: bend, accessories: reducer, accessories: coupler plate, accessories: other hardware | 100 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.7 ¦ 90 deg Horizontal Bend Perforated (shall be decided as per detail engineering) a. ¦ 750mm Wide | perforated cable tray horizontal bend |  | width: 750 mm | bend angle: 90 degree, type: perforated, feature: shall be decided as per detail engineering | 3 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.7 ¦ 90 deg Horizontal Bend Perforated (shall be decided as per detail engineering) b. ¦ 600mm Wide | perforated cable tray horizontal bend |  | width: 600 mm | bend angle: 90 degree, type: perforated, feature: shall be decided as per detail engineering | 20 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.7 ¦ 90 deg Horizontal Bend Perforated (shall be decided as per detail engineering) c. ¦ 300mm Wide | perforated cable tray horizontal bend |  | width: 300 mm | bend angle: 90 degree, type: perforated, feature: shall be decided as per detail engineering | 20 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.8 ¦ 90 deg Vertical Bend (Inside) Perforated (shall be decided as per detail engineering) a. ¦ 600mm Wide | perforated cable tray vertical bend (inside) |  | width: 600 mm | bend angle: 90 degree, type: perforated, position: inside, feature: shall be decided as per detail engineering | 10 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.8 ¦ 90 deg Vertical Bend (Inside) Perforated (shall be decided as per detail engineering) b. ¦ 300mm Wide | perforated cable tray vertical bend (inside) |  | width: 300 mm | bend angle: 90 degree, type: perforated, position: inside, feature: shall be decided as per detail engineering | 4 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.8 ¦ 90 deg Vertical Bend (Inside) Perforated (shall be decided as per detail engineering) c. ¦ 150mm Wide | perforated cable tray vertical bend (inside) |  | width: 150 mm | bend angle: 90 degree, type: perforated, position: inside, feature: shall be decided as per detail engineering | 20 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.9 ¦ 90 deg Vertical Bend (outside) Perforated (shall be decided as per detail engineering) a. ¦ 600mm Wide | perforated cable tray vertical bend (outside) |  | width: 600 mm | bend angle: 90 degree, type: perforated, position: outside, feature: shall be decided as per detail engineering | 10 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.9 ¦ 90 deg Vertical Bend (outside) Perforated (shall be decided as per detail engineering) b. ¦ 300mm Wide | perforated cable tray vertical bend (outside) |  | width: 300 mm | bend angle: 90 degree, type: perforated, position: outside, feature: shall be decided as per detail engineering | 4 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.9 ¦ 90 deg Vertical Bend (outside) Perforated (shall be decided as per detail engineering) c. ¦ 150mm Wide | perforated cable tray vertical bend (outside) |  | width: 150 mm | bend angle: 90 degree, type: perforated, position: outside, feature: shall be decided as per detail engineering | 20 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 17.1 ¦ TEE Connection Perforated type (shall be decided as per detail engineering) a. ¦ 600mm Wide | perforated cable tray tee connection |  | width: 600 mm | type: perforated, feature: shall be decided as per detail engineering | 8 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 18.1 ¦ Supply and Erection of MS Structural Steel: MS structural steel like ISMC , angles, flats etc conforming to IS-2062. : Structural steel work riveted,bolted or welded in built up sections, trusses & framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete: | ms structural steel supply and erection |  |  | material: ms(mild steel), type: structural steel, includes: ISMC, angles, flats, standard: indian standard 2062, work: riveted, bolted or welded in built up sections, trusses & framed work, includes: cutting, hoisting, fixing in position, priming coat of approved steel primer | 7 | ton | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 18.2 ¦ Supplying and fixing of 6 mm thick chequered plate on cable trench inside swtich room, DG room, earthing pit including cutting, painting, lifting hooks, etc conforming to IS-3502. | chequered plate supply and fixing |  | thickness: 6 mm | application: cable trench inside switch room, DG(diesel generator) room, earthing pit, includes: cutting, painting, lifting hooks, standard: indian standard 3502 | 100 | sqm | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 18.3 ¦ 3mm to 10mm thick MS plate conforming to IS-2062 | ms plate |  | thickness: 3 mm to 10 mm | material: ms(mild steel), standard: indian standard 2062 | 1.5 | ton | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS', 'EARTHING & LIGHTNING'] | 19.1 ¦ 50 x 6 mm GI Strip | gi(galvanized iron) strip |  | dimension: 50 x 6 mm | material: gi(galvanized iron) | 4400 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS', 'EARTHING & LIGHTNING'] | 19.2 ¦ 35 x 6 mm GI Strip | gi(galvanized iron) strip |  | dimension: 35 x 6 mm | material: gi(galvanized iron) | 2400 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS', 'EARTHING & LIGHTNING'] | 19.3 ¦ 25 x 6 mm GI Strip | gi(galvanized iron) strip |  | dimension: 25 x 6 mm | material: gi(galvanized iron) | 1100 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS', 'EARTHING & LIGHTNING'] | 19.4 ¦ 1C x 150 mm2 PVC (Al) cable Green colour | pvc(aluminium) cable |  | core: 1, area: 150 mm2 | material: aluminium, insulation: pvc(polyvinyl chloride), colour: green | 560 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS', 'EARTHING & LIGHTNING'] | 19.5 ¦ 1C x 95 mm2 PVC (Al) cable Green colour | pvc(aluminium) cable |  | core: 1, area: 95 mm2 | material: aluminium, insulation: pvc(polyvinyl chloride), colour: green | 670 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS', 'EARTHING & LIGHTNING'] | 19.6 ¦ 1C x 35 mm2 PVC (Al) cable Green colour | pvc(aluminium) cable |  | core: 1, area: 35 mm2 | material: aluminium, insulation: pvc(polyvinyl chloride), colour: green | 330 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS', 'EARTHING & LIGHTNING'] | 19.7 ¦ 1C x 16 mm2 PVC (Al) cable Green colour | pvc(aluminium) cable |  | core: 1, area: 16 mm2 | material: aluminium, insulation: pvc(polyvinyl chloride), colour: green | 850 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS', 'EARTHING & LIGHTNING'] | 19.8 ¦ 1C x 2.5 mm2 PVC (Cul) cable Green colour | pvc(copper) cable |  | core: 1, area: 2.5 mm2 | material: copper, insulation: pvc(polyvinyl chloride), colour: green | 150 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS', 'EARTHING & LIGHTNING'] | 19.8 ¦ Hot dip Galvanized 10 Holes ∅13mm ground plate 550mmx50mmx6mm earth connection bar with fixing materials/ accessories , SS hardware etc. (min. coating 120 microns of zinc). | hot dip galvanized earth connection bar |  | holes: 10, hole diameter: 13 mm, plate size: 550 mm x 50 mm x 6 mm | coating: hot dip galvanized, coating thickness: 120 microns of zinc, includes: fixing materials/accessories, hardware: ss(stainless steel) | 70 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS', 'EARTHING & LIGHTNING'] | 19.9 ¦ Flexible earth provision inclusive of flexible cable, hanger, grounding clip etc for LPG unloading tanker | flexible earth provision |  |  | includes: flexible cable, hanger, grounding clip, application: lpg(liquefied petroleum gas) unloading tanker | 3 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS', 'EARTHING & LIGHTNING'] | 19.1 ¦ 1000mm long,20 dia. Hot dipped GI air termination rod(lightning rod-120 Micron coating) with all fixing material,accessories as per IS:2309 | gi(galvanized iron) air termination rod |  | length: 1000 mm, diameter: 20 mm | coating: hot dipped, coating thickness: 120 micron, includes: all fixing material, accessories, standard: indian standard 2309 | 3 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS', 'Earthing Lug'] | 20.1 ¦ 1C x 150 mm2 PVC (Al) cable Green colour | pvc(aluminium) cable |  | core: 1, area: 150 mm2 | material: aluminium, insulation: pvc(polyvinyl chloride), colour: green | 60 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS', 'Earthing Lug'] | 20.2 ¦ 1C x 95 mm2 PVC (Al) cable Green colour | pvc(aluminium) cable |  | core: 1, area: 95 mm2 | material: aluminium, insulation: pvc(polyvinyl chloride), colour: green | 80 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS', 'Earthing Lug'] | 20.3 ¦ 1C x 35 mm2 PVC (Al) cable Green colour | pvc(aluminium) cable |  | core: 1, area: 35 mm2 | material: aluminium, insulation: pvc(polyvinyl chloride), colour: green | 65 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS', 'Earthing Lug'] | 20.4 ¦ 1C x 16 mm2 PVC (Al) cable Green colour | pvc(aluminium) cable |  | core: 1, area: 16 mm2 | material: aluminium, insulation: pvc(polyvinyl chloride), colour: green | 300 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS', 'Earthing Lug'] | 20.5 ¦ 1C x 2.5 mm2 PVC (Cul) cable Green colour | pvc(copper) cable |  | core: 1, area: 2.5 mm2 | material: copper, insulation: pvc(polyvinyl chloride), colour: green | 850 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS', 'Earthing Lug'] | 20.5 ¦ SQUARE TAPE CLAMP | square tape clamp |  |  |  | 40 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS', 'Earthing Lug'] | 20.6 ¦ TEST LINK | test link |  |  |  | 10 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS', 'Earthing Lug'] | 20.7 ¦ TAPE CLIP | tape clip |  |  |  | 1000 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS', 'Earthing Lug'] | 20.8 ¦ TEE JOINT | tee joint |  |  |  | 700 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS', 'Earthing Lug'] | 20.9 ¦ Earth Pit: Supply of Maintanance Free (chemical) Earth electrode with all parts including required hardware for earth pit (equipment earthing, Neutral earthing and for lightning protection) and required test link for checking earth connectivity.as per specification,Attachment-29 LPG.ENG.117.06.03.2001, IS and direction of Engineer-in-charge icludingincluding supply of commissioning and 2 years O&M spares. | earth pit |  |  | type: maintenance free (chemical) earth electrode, included: all parts, hardware, test link, application: equipment earthing, neutral earthing, lightning protection, specification: as per specification, attachment-29 lpg.eng.117.06.03.2001, standard: indian standard, included: supply of commissioning and 2 years o&m(operation & maintenance) spares |  |  | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS', 'Earthing Lug'] | a. ¦ Earth pit for Body Earthing ( BEP) | earth pit |  |  | application: body earthing (bep) | 23 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS', 'Earthing Lug'] | b. ¦ Earth pit for Lightning Earthing ( LEP) | earth pit |  |  | application: lightning earthing (lep) | 31 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS', 'Earthing Lug'] | c. ¦ Earth pit for Neutral Earthing ( NEP) | earth pit |  |  | application: neutral earthing (nep) | 8 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS', 'Earthing Lug'] | d. ¦ Instrument earth pit (IEP) | earth pit |  |  | application: instrument earth pit (iep) | 27 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 21 ¦ Earth Pit: Supply of Maintanance Free (chemical) Earth electrode 4 mtr long, 100 mm dia suitable for rocky area with all parts including required hardware for earth pit as required as per IS 3043. The pipe shall be embedded as far as possible vertically into the ground, except when hard rock is encountered, where it may be burled inclined to the vertical, the inclination being limited to 30 degree from the vertical. The connection of MS flat to each electrode shall be made through MS links by bolted joints to enable isolation of the electrode for testing purposes. . This is included with excavation, restoration and removal extra earth/rock. and required test link for checking earth connectivity.as per specification,Attachment-29 LPG.ENG.117.06.03.2001, IS and direction of Engineer-in-charge icludingincluding supply of commissioning and 2 years O&M spares. | earth pit |  | length: 4 mtr, diameter: 100 mm | type: maintenance free (chemical) earth electrode, suitable for: rocky area, included: all parts, hardware, test link, application: earth pit, standard: indian standard 3043, installation: vertical or up to 30 degree inclined, connection: ms(mild steel) flat with ms links by bolted joints, included: excavation, restoration, removal of extra earth/rock, specification: as per specification, attachment-29 lpg.eng.117.06.03.2001, included: supply of commissioning and 2 years o&m(operation & maintenance) spares | 8 | nos | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 22.1 ¦ 11 kV, 900mm wide, electric grade floor rubber mat conforming to relevant IS. ISI mark shall be there on rubber mat. | electric grade floor rubber mat |  | voltage: 11 kv, width: 900 mm | standard: indian standard, certification: isi mark | 5 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 22.2 ¦ 1.1 kV, 900mm wide, electric grade floor rubber mat (in pieces of length not less than 2 mtrs.) conforming to relevant IS. ISI mark shall be there on rubber mat. | electric grade floor rubber mat |  | voltage: 1.1 kv, width: 900 mm, length: not less than 2 mtrs. | standard: indian standard, certification: isi mark | 60 | m | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 22.3 ¦ Rubber Hand Gloves of 11 KV grade. | rubber hand gloves |  | voltage: 11 kv |  | 4 | pair | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 22.4 ¦ Rubber Hand Gloves of 415V grade. | rubber hand gloves |  | voltage: 415 v |  | 6 | pair | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 22.5 ¦ First aid box of GI, 18 SWG sheet with necessary items. | first aid box |  | sheet: 18 swg(standard wire gauge) | material: gi(galvanized iron), included: necessary items | 8 | no. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 22.6 ¦ DANGER PLATE (As per IS 2551) | danger plate |  |  | standard: indian standard 2551 | 30 | nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 22.7 ¦ CABLE ROUTE MARKER | cable route marker |  |  |  | 200 | nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 22.8 ¦ CO2 fire extinguishers 5kg with fixing bracket | co2(carbon dioxide) fire extinguisher |  | capacity: 5 kg | included: fixing bracket | 18 | nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 22.9 ¦ ABC Dry chemical powder (DCP) fire extinguishers 5kg with fixing bracket | abc dry chemical powder fire extinguisher | dcp fire extinguisher | capacity: 5 kg | included: fixing bracket | 18 | nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 21.1 ¦ Shock treatment chart | shock treatment chart |  |  |  | 40 | nos. | Table 1
['ELE', 'PART A - SUPPLY OF ELECTRICAL ITEMS'] | 21.11 ¦ Fire buckets (4nos.) with sand & M.S. Hooks / stand | fire bucket |  | quantity: 4 nos. | included: sand, ms(mild steel) hooks, stand | 10 | set | Table 1
['INST', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 1.1.1 ¦ Supply of pressure transmitter (24 V DC) Exd type, 2 nos. with each DV (1 nos. for air line & 1 no. for water line) Description:IP-66, EExia IIA IIB, T3 (ATEX /CENELEC),CCOE 4 ~ 20 mA +HART, Range: 0~7kg/cm2 (11 nos.) & 0~15kg/cm2 (11 Nos ), Acuracy:0.075% of span. Rangeability – 1:100 , service: water & Air, SS316 cable gland. refer tender specification for detail. | pressure transmitter |  | voltage: 24 v dc, range: 0~7 kg/cm2 (11 nos.), range: 0~15 kg/cm2 (11 nos.) | type: exd, included: 2 nos. with each dv(deluge valve) (1 nos. for air line & 1 no. for water line), protection: ip-66, certification: eexia iia iib, t3 (atex /cenelec), ccoe, output: 4~20 ma +hart, accuracy: 0.075% of span, rangeability: 1:100, service: water & air, cable gland: ss316(stainless steel 316) | 22 | nos. | Table 1
['INST', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 1.1.2 ¦ Supply flameproof solenoid valve (24V DC) suitable for Hazardous area zone-1, IIA/IIB T3, 1/2" NPT connection as per specification (9 nos for DV+2 Nos spares) | flameproof solenoid valve |  | voltage: 24v dc, connection: 1/2" npt | suitable for: hazardous area zone-1, certification: iia/iib t3, included: 9 nos for dv(deluge valve) + 2 nos spares | 9 | nos. | Table 1
['INST', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 1.2.1 ¦ Supply of ESD Push button station with all accessories like cables , glanding & termination etc. mounted on Exd JBs located at different areas - a)Filling Shed, b)Pump house, c)LPG Bullets, d)TLD , e)Central Monitoring Hub f) plant manager room g) Filled Cylinder Area | esd push button station | esd push button station |  | included: all accessories like cables, glanding & termination etc., mounting: exd(explosion proof) junction boxes, locations: filling shed, pump house, lpg bullets, tld, central monitoring hub, plant manager room, filled cylinder area | 7 | nos. | Table 1
['INST', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 1.3.1 ¦ Supply of electric siren at pump house/PMCC/Security room. Scope also includes: a) supply of necessory equipments/component/ accessories including siren controller required to complete system as per tender document. b) supply of any support required for siren & it's panel | electric siren |  |  | location: pump house, pmcc(power & motor control center), security room, included: siren controller, necessary equipment/component/accessories, support for siren & panel, as per tender document | 1 | nos. | Table 1
['INST', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 1.3.2 ¦ Supply of Hand operated siren for the location of LPG pump house, security room, TLD bay & Empty cum filling shed. | hand operated siren |  |  | location: lpg pump house, security room, tld bay, empty cum filling shed | 4 | nos. | Table 1
['INST', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 1.4.1 ¦ Supply of Fire Alarm System panel along with electronic card and other electrical accessories. All hardware and software to integrate all devices for successful functioning of the system included in the scope. All Fire Alarm Panel Panels shall be integrated through MODBUS / PROFIBUS / OEM RECOMMENDED SERIAL LINK COMMUNICATION. Common Fault Alarm shall be generated in Fire Alarm Panel to hook up through hardware cable to PLC / ESD located at CR. Associated electrical or electronics circuit connecting with the field devices of detection system requires high availability and reliability in confirmation to tender drawings and specification. Fire alarm system shall be UL listed. Fire Detection System Panel shall include below mentioned items: 1. Intelligent Analogue Addressable type non-ex-proof type Manual Call point (06 Nos), to be hooked up with Fire Alarm Panel at CMH, 2. Intelligent Analogue Addressable type Flame proof type Manual Call point (07 Nos), to be hooked up with Fire Alarm Panel at CMH, 3. Isolator Modules (03 Nos), to be hooked up with Fire Alarm Panel at CMH. 4. Control Modules (05 Nos), to be hooked up with Fire Alarm Panel at CMH. 5. Intelligent Analogue Addressable type Multi Criteria Detector (05 Nos) to be hooked up in Fire Alarm Panel of CMH). 6. Response Indicators (05 Nos), 7 Audio Visual Fire Alarm Siren (05 Nos). Above items shall be read in conjuction with Fire Detection drawing & ILSD drawing. | fire alarm system panel |  |  | included: electronic card, electrical accessories, hardware and software for integration, communication: modbus, profibus, oem recommended serial link, common fault alarm, integration: plc(programmable logic controller)/esd(emergency shutdown device) at cr(control room), high availability and reliability, standard: ul(underwriters laboratories) listed, includes: manual call points (non-ex-proof and flame proof), isolator modules, control modules, multi criteria detector, response indicators, audio visual fire alarm siren, reference: fire detection drawing & ilsd(integrated leak detection system) drawing | 1 | lot | Table 1
['INST', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 1.4.2 ¦ SUPPLY of DV Operation Panel integrating with PLC and with PB (with operation indicating lamp for "DV on Fire" and "DV Operated") for opening of Deluge Valve (09 nos+ 1 spare) . All hardware as required and software included. (1 No. DV panel shall be installed at fire water pump house, 1 No. at main gate security room.) | dv operation panel |  |  | integration: plc(programmable logic controller), pb(push button), indication: operation lamp for 'dv on fire' and 'dv operated', for: deluge valve (9 nos + 1 spare), included: all hardware and software, installation: fire water pump house, main gate security room | 2 | lot | Table 1
['INST', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 2.1.1 ¦ Supply of flameproof/EX -proof , IP-66 IR gas detector suitable to hazardous area Zone-1, IIA/B T3 . Canopy & any otther acessories required is included in scope | ir gas detector |  |  | protection: flameproof/ex-proof(explosion proof), ingress protection: ip-66, suitable for: hazardous area zone-1, certification: iia/b t3, included: canopy and accessories | 28 | nos. | Table 1
['INST', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 2.2.1 ¦ Gas monitoring system: Supply of Dual redundant (Parallel/ Hot Standby) wall mounted Programmable Logic Controller (Process PLC) along with PLC Panels, Input Output modules, Power supply units, Relays with base, barriers, TBs, Dual Ethernet ports per processors, Serial Interface Modules, wirings, glands, plugs, other modules/ hardwares required for interfacing all the required field and Central Monitoring Hub (CMH) equipments including spare requirements, licenses, tags, softwares etc complete as per specification and tender document. AI -28 Nos DI -12 Nos DO -04 Nos Serial Interface Ports: 04 Additional 20% spare (min 1) qty to be supplied over the above mentioned I/O quantity.Size of the PLC panel shall be optimized mode to accomodate all the signals in wall mounted panel only. Gas monitoring system at Central Monitoring Hub (CMH) as per tender documents. the scope also includes supply of all componennt, accessories required for complete the system and customization of reports as detailed in specifications and tender documents. | gas monitoring system |  |  | controller: dual redundant (parallel/hot standby) wall mounted programmable logic controller (process plc), included: plc panels, input output modules, power supply units, relays with base, barriers, tbs(terminal blocks), dual ethernet ports per processor, serial interface modules, wirings, glands, plugs, other modules/hardware, spare requirements, licenses, tags, software, ai(analog input): 28 nos, di(digital input): 12 nos, do(digital output): 4 nos, serial interface ports: 4, additional 20% spare (min 1), panel: wall mounted, location: central monitoring hub (cmh), includes: all components, accessories, customization of reports | 1 | lot | Table 1
['INST', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 2.2.2 ¦ Supply of weather proof Repeater panel at security room alongwith hooter & indication of Fault & LEL Alarm as per tender secifications. Panel to be hooked up with GMS at CMH. | weather proof repeater panel |  |  | location: security room, included: hooter, indication of fault & lel(lower explosive limit) alarm, connection: gms(gas monitoring system) at cmh(central monitoring hub), standard: as per tender specifications | 1 | nos. | Table 1
['INST', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 2.2.3 ¦ Supply of Flameproof/Ex-Proof cum weatherproof Repeater Panel alongwith Flameproof/Ex-proof Hooter & indication of Fault & LEL Alarm as per tender secifications. same to be hooked up with GMS at CR , All cabling & hardware included (Common repeater panel 1 no. in LPG Pump House room for TLD, LPG P/H & MSV's area gas detectors; 1 no for Filling shed & filled cylinder shed. ) | flameproof cum weatherproof repeater panel |  |  | protection: flameproof/ex-proof(explosion proof), weatherproof, included: flameproof/ex-proof hooter, indication of fault & lel(lower explosive limit) alarm, connection: gms(gas monitoring system) at cr(control room), included: all cabling & hardware, locations: lpg pump house room for tld, lpg p/h & msv's area gas detectors, filling shed & filled cylinder shed, standard: as per tender specifications | 2 | nos. | Table 1
['INST', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 2.2.4 ¦ Supply of sample gas cylinder for gas detectors sufficient to calibrate min. 21 nos. Gas detectors at a time. All asscessories needed for calibration are included in scope | sample gas cylinder for gas detectors |  |  | sufficient for: calibration of minimum 21 gas detectors at a time, included: all accessories for calibration | 4 | lot | Table 1
['INST', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 3.1.1 ¦ The followings shall be considered for above - i) Servo Gauge with Display , Accuracy +-1mm LAB conditions,Density Measurement - 1 no. for each MSV | servo gauge with display |  |  | accuracy: ±1mm lab conditions, density measurement, quantity per msv(mounded storage vessel): 1 | 3 | nos | Table 1
['INST', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 3.1.2 ¦ ii) Pressure Tx with 2 valve manifold for vapour pressure measurement Range 0 -15 Kg/CM2 - 2 nos. for each MSV | pressure transmitter with 2 valve manifold |  | range: 0 -15 kg/cm2 | application: vapour pressure measurement, quantity per msv(mounded storage vessel): 2 | 3 | nos | Table 1
['INST', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 3.1.3 ¦ iii) Radar Gauge with Display and - +/-1mm LAB condition with Display (Smart typeTank Side Indicator),Temperature sensor interface, Suitable for 6" Sch 10 Stilling pipe,1 Nos. SIL3 Relay Output & Analog Output - 1 no. for each MSV | radar gauge with display |  | suitable for: 6" sch(schedule) 10 stilling pipe | accuracy: ±1mm lab condition, display: smart type tank side indicator, temperature sensor interface, outputs: sil3 relay output & analog output, quantity per msv(mounded storage vessel): 1 | 3 | nos | Table 1
['INST', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 3.1.4 ¦ iv) Vibration Fork type level switch with HH/LL set points - 1no. For each MSV | vibration fork type level switch |  |  | set points: hh(high high)/ll(low low), quantity per msv(mounded storage vessel): 1 | 3 | nos | Table 1
['INST', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 3.1.5 ¦ v) Smart type tank side indicator for Radar gauge at LPG pump house & interfacing with Radar gauge & Process PLC /safety PLC - 1 no. for each MSV | smart type tank side indicator for radar gauge |  |  | location: lpg pump house, interfacing: radar gauge & process plc(programmable logic controller)/safety plc, quantity per msv(mounded storage vessel): 1 | 3 | nos | Table 1
['INST', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 3.1.6 ¦ vi) Smart type tank side indicator for servo Gauge at LPG pump house & interfacing with servo gauge & Process PLC /safety PLC 1 no. for each MSV | smart type tank side indicator for servo gauge |  |  | location: lpg pump house, interfacing: servo gauge & process plc(programmable logic controller)/safety plc, quantity per msv(mounded storage vessel): 1 | 3 | nos | Table 1
['INST', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 3.1.7 ¦ vii) local indicator for pressure transmitter at LPG pump house - 1 no. for each MSV | local indicator for pressure transmitter |  |  | location: lpg pump house, quantity per msv(mounded storage vessel): 1 | 6 | nos | Table 1
['INST', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 3.1.8 ¦ viii) Interface (Radar & Servo) | interface for radar and servo |  |  |  | 6 | nos | Table 1
['INST', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 3.1.9 ¦ ix) 9 Point temperature probe ( to be interface with Radar & Servo) | 9 point temperature probe |  |  | interface: radar & servo | 3 | nos | Table 1
['INST', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 2010-01-03 00:00:00 ¦ x) Redundant CIU/FCU with all interfacing , 2 nos of Modbus ports for Process PLC and 2 nos of Modbus ports for TFMS connectivity as required - 1 set | redundant ciu/fcu |  |  | interfacing: all, modbus ports: 2 for process plc(programmable logic controller), 2 for tfms(tank farm management system) connectivity, quantity: 1 set | 1 | set | Table 1
['INST', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 2011-01-03 00:00:00 ¦ xii) Verification pin set | verification pin set |  |  |  | 20 | nos | Table 1
['INST', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 2012-01-03 00:00:00 ¦ xiii)TFMS Software supplied by bidder shall be same make as radar manufacturer and compatible with servo gauges. Licence shall be 12 nos min. | tfms software |  |  | compatibility: same make as radar manufacturer, compatible with servo gauges, licence: minimum 12 nos | 1 | lot | Table 1
['INST', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 2013-01-03 00:00:00 ¦ xiv) Junction Boxes - | junction boxes |  |  |  | 4 | nos | Table 1
['INST', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 2014-01-03 00:00:00 ¦ xv) PDB Panel for TFMS. | pdb panel for tfms(tank farm management system) | pdb panel for tfms |  |  | 2 | nos | Table 1
['INST', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 2015-01-03 00:00:00 ¦ xvi) Communication cable, RTD cable, Power cable for TFMS | communication cable, rtd(resistance temperature detector) cable, power cable for tfms(tank farm management system) |  |  |  | 1 | lot | Table 1
['INST', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 2016-01-03 00:00:00 ¦ xvIi) Audio-Visual Annunciation Panel for annunciation at LPG Pump House, integrated with all Level Switches of MSVs (Single common Panel for all level switches) | audio-visual annunciation panel |  |  | location: lpg pump house, integration: all level switches of msvs(mounded storage vessels), feature: single common panel for all level switches | 1 | nos | Table 1
['INST', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 3.2 ¦ Tank Farm Management Servers - Commodity Grade, working on redundant (Primary and Secondary) hot standby mode with software, including backlit LED Monitor, key board and mouse. Supply , Installation, erection and commissioning of Operator Interface Console Computer (OIC) with 22" colour LED monitor, standard keyboard etc. complete as per specifications at Central Monitoring Hub (CMH). | tank farm management servers |  | monitor size: 22" | grade: commodity, redundancy: primary and secondary hot standby mode, includes: software, backlit led monitor, keyboard, mouse, supply, installation, erection, commissioning of operator interface console computer(oic), location: central monitoring hub(cmh) | 1 | lot | Table 1
['INST', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)'] | 3.3 ¦ Other items for above - FLP Double compression type SS cable glands - As required , Adaptor Plate for Radar Gauge 4"/6",300# (SS316) for Radar tags - 1 no , Adaptor Plate for Temperature Probes 2",300# (SS316) - 4 nos , Fabricated Adaptor Chamber for Servo Gauge 2"X 4" X 6"300# (MOC CS) with pressure gauge, needle valve & pressure relief valve for Servo Tags , Studs as per SA 320 Gr. L7 & Bolts Nuts as per SA 194 Gr. 7 , Gaskets ( 6",4", 2") Spiral wound Metallic AISI 304, asbestos filled as per API 601 , fabricated cable for CIU & PC - As required ,fabrication of manifold for ionstllation of local indicator (radar /servo)- as required, Cables for communication of Servo , Radar / Servo / field Instruments to CIU (FRLS Cable for data communicatin) - As required , All software and Hardware shall be included as required , Bidder shall consider Process PLC & Tank Gauging system interface on redundant Modbus Communication , Any other item to achieve complete system to successful functioning and integration with other system as required are included. | other items for above |  | adaptor plate for radar gauge: 4"/6", adaptor plate for temperature probes: 2", fabricated adaptor chamber for servo gauge: 2"x 4" x 6" | flp(flamproof) double compression type ss(stainless steel) cable glands, adaptor plate for radar gauge: 300# (ss316), adaptor plate for temperature probes: 300# (ss316), fabricated adaptor chamber for servo gauge: 300# (moc cs(carbon steel)), includes: pressure gauge, needle valve, pressure relief valve for servo tags, studs: sa 320 gr. l7, bolts nuts: sa 194 gr. 7, gaskets: spiral wound metallic aisi 304, asbestos filled as per api 601, fabricated cable for ciu(communication interface unit) & pc(personal computer), fabrication of manifold for installation of local indicator (radar or servo), cables for communication of servo, radar or servo or field instruments to ciu (frls(fire retardant low smoke) cable for data communication), all software and hardware included, process plc(programmable logic controller) & tank gauging system interface on redundant modbus communication, any other item for complete system functioning and integration | 1 | lot | Table 1
['INST', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)', 'AUTOMATION SYSTEM', 'TLF/TLD GANTRY'] | 4.1.1 ¦ Supply of Flameproof cum weather proof smart type Grounding unit with one green indicating lamp and dual output for safety earthing of tank trucks, suitable for giving safety interlocking signal to PLC all complete as per specifications | smart type grounding unit |  |  | protection: flameproof and weather proof, indicator: one green indicating lamp, output: dual, application: safety earthing of tank trucks, feature: suitable for giving safety interlocking signal to plc(programmable logic controller) | 2 | nos. | Table 1
['INST', 'PART A - SUPPLY OF CONTROL & INSTRUMENTATION (C & I) WORKS (INSTRUMENTATION, AUTOMATION, CCTV, ILSD, GMS, TFMS, ACS WORKS ETC)', 'AUTOMATION SYSTEM', 'Central Monitoring Hub (CMH) INSTRUMENTATION'] | 4.2.1 ¦ Supply of Dual redundant (Parallel/ Hot Standby) Programmable Logic Controller (Process PLC) along with PLC Panels, Marshalling Panels, Input Output modules, Power supply units, Relays with base, barriers, TBs, Dual Ethernet ports per processors, Serial Interface Modules, HMI console, wirings, glands, plugs, other modules/ hardwares required for interfacing all the required field and Central Monitoring Hub (CMH) equipments including spare requirements, licenses, tags, GUI, softwares etc complete as per specification and tender document. AI -25 Nos DI -96 Nos DO -80 Nos Serial Interface Ports: 28 Minimum 20% spare IO to be supplied as per tender specification. Count of PLC panel shall be optimized to accomodate all the signals in one panel only. | programmable logic controller | process plc | ai(analog input): 25 nos, di(digital input): 96 nos, do(digital output): 80 nos, serial interface ports: 28 | redundancy: dual redundant (parallel or hot standby), includes: plc panels, marshalling panels, input output modules, power supply units, relays with base, barriers, tbs(terminal blocks), dual ethernet ports per processor, serial interface modules, hmi(human machine interface) console, wirings, glands, plugs, other modules or hardware for interfacing all required field and cmh(central monitoring hub) equipment, spare requirements, licenses, tags, gui(graphical user interface), software, minimum 20% spare io(input/output), panel count optimized for all signals in one panel, as per specification and tender document | 1 | lot | Table 1