## Sheet1
section_context_for_this_product_block | full_product_description | core_product_name | size | feature_or_specifications | acronymed_core_product_name | quantity | unit
P ¦ BIOBIQUETE STORE > P1 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 80 mm NB | ms black steel pipe | size: 80 mm NB | material: ms(mild steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint: grooved with groove coupling, scope: all related civil work, supports etc shall be of vendor's scope |  | 12.0 | Mtr
P ¦ BIOBIQUETE STORE > P1 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 40 mm NB | ms black steel pipe | size: 40 mm NB | material: ms(mild steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint: grooved with groove coupling, scope: all related civil work, supports etc shall be of vendor's scope |  | 18.0 | Mtr
P ¦ BIOBIQUETE STORE > P1 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 25 mm NB | ms black steel pipe | size: 25 mm NB | material: ms(mild steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint: grooved with groove coupling, scope: all related civil work, supports etc shall be of vendor's scope |  | 12.0 | Mtr
P ¦ BIOBIQUETE STORE > P1 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. Size80 mm NB | butterfly valve | size: 80 mm NB | standard: british standard 5155, type: wafer, fittings: matching flanges, nuts & bolts, feature: necessary fittings shall be provided by erection vendor |  | 1.0 | Nos
P ¦ BIOBIQUETE STORE > P1 ¦ AUTOMATIC SPRINKLER SYSTEM | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts. Size80 mm NB | non return valve | size: 80 mm NB | type: wafer, fittings: matching flanges, nuts & bolts |  | 1.0 | Nos
P ¦ BIOBIQUETE STORE > P1 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & fixing of paddle type Flow Switch | flow switch |  | type: paddle |  | 1.0 | Nos
P ¦ BIOBIQUETE STORE > P1 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Fixing of Sprinkler Head Pendent type for K factor-80. Temp rating 68 deg C.UL/FM Approved. | sprinkler head pendent type | k factor: 80 | temperature rating: 68 deg c, certification: ul(underwriters laboratories), certification: fm(factory mutual) |  | 3.0 | Nos
P ¦ BIOBIQUETE STORE > P1 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, installation of automatic 25 NB Air Release Valve | air release valve | size: 25 NB | feature: automatic |  | 1.0 | Nos
P ¦ BIOBIQUETE STORE > P1 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends Size 40NB | globe valve | size: 40 NB | material: bronze, standard: indian standard 778, ends: screwed |  | 1.0 | Nos
P ¦ BIOBIQUETE STORE > P1 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends Size 25NB | globe valve | size: 25 NB | material: bronze, standard: indian standard 778, ends: screwed |  | 2.0 | Nos
P ¦ BIOBIQUETE STORE > P1 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Erection and testing of Installation Control Valve complete with trims & gong. Size 80 mm NB | installation control valve | size: 80 mm NB | feature: complete with trims & gong |  | 1.0 | Nos
P ¦ BIOBIQUETE STORE > P2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | multicriteria detector |  | type: analogue addressable |  | 3.0 | Nos
P ¦ BIOBIQUETE STORE > P2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Manual Call point | manual call point |  | type: analogue addressable |  | 1.0 | Nos
P ¦ BIOBIQUETE STORE > P2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of Hooter cum strobe | hooter cum strobe |  |  |  | 1.0 | Nos
P ¦ BIOBIQUETE STORE > P2 ¦ FDA SYSTEM | Supply, erction, testing & commissioning of analogue addressable Control Module | control module |  | type: analogue addressable |  | 1.0 | Nos
P ¦ BIOBIQUETE STORE > P2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Isolator Module | isolator module |  | type: analogue addressable |  | 2.0 | Nos
P ¦ BIOBIQUETE STORE > P2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Monitor module | monitor module |  | type: analogue addressable |  | 1.0 | Nos
P ¦ BIOBIQUETE STORE > P2 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cabling | configuration: 2C x 1.5 mm2 | feature: loop cable, feature: armoured, fittings: lugs, laying and termination of both ends |  | 36.0 | Mtr
P ¦ BIOBIQUETE STORE > P2 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Power cable) | armoured cabling | configuration: 2C x 1.5 mm2 | feature: power cable, feature: armoured, fittings: lugs, laying and termination of both ends |  | 24.0 | Mtr
P ¦ BIOBIQUETE STORE > P2 ¦ FDA SYSTEM | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable trays |  | material: gi(galvanized iron), feature: for laying all type of cables, fittings: necessary structural supports |  | 36.0 | Mtr
P ¦ BIOBIQUETE STORE > P3 ¦ PA SYSTEM | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | paging station |  | feature: IP based, feature: networkable, feature: touch screen, feature: selection of zones, feature: supervision of system status, feature: scheduled broadcasts, feature: central exchange with stand by CPU, feature: built-in monitoring loudspeaker, feature: goose-neck microphone, feature: LCD touchscreen display, feature: audio input |  | 1.0 | Nos
P ¦ BIOBIQUETE STORE > P3 ¦ PA SYSTEM | 9 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | horn type speaker | power: 9 W | feature: high efficiency, feature: weather protection IP 65, feature: weatherproof type, feature: suitable for outdoor area |  | 1.0 | Nos
P ¦ BIOBIQUETE STORE > P3 ¦ PA SYSTEM | Rack Mounted 125 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | power amplifier | power: 125 watt | mounting: rack mounted, feature: battery back up, feature: wattage shall be as per requirement |  | 1.0 | Nos
P ¦ BIOBIQUETE STORE > P3 ¦ PA SYSTEM | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | dvd player |  | feature: features to hook up to amplifiers of pa system for music in the common areas |  | 1.0 | Nos
P ¦ BIOBIQUETE STORE > P3 ¦ PA SYSTEM | Paging Loudspeaker | loudspeaker |  | feature: paging |  | 1.0 | Nos