## Sheet1
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
R | PRE TREATMENT CHEMICAL (PTC)
R1 | HYDRANT SYSTEM
1 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope.
a | 150 mm NB | Mtr | 18
b | 80 mm NB | Mtr | 12
c | 25 mm NB | Mtr | 12
2 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts.
a | Size 150 mm NB | Nos | 2
3 | Supply, installation, testing and commissioning of CS Non return valve with companion flanges,nuts & bolts and gaskets.
a | Size 150 mm NB | Nos | 1
4 | Supply & installation of SS oblique type single headed Landing valve with 80 mm inlet and 63 mm outlet SS instantaneous male coupling with rubber cap and chain conforming to IS : 5290 including matching flanges, gasket, nuts and bolts complete. | Nos | 3
5 | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor.
a | Size 80 mm NB | Nos | 3
6 | Supply & installation of SS branch pipe with 20 mm nozzle conforming to IS : 903 complete | Nos | 3
7 | Supply & installation of 63 mm dia rubberized reinforced rubber line hose pipe in 15 m length conforming to IS : 636 Type II ISI marked with gunmetal male and female instantaneous coupling conforming to IS 903 wounded with 18 SWG copper wire complete | Nos | 6
8 | Supply & installation of MS Hose Box of fabricated from 16 SWG CRCA sheet double door with lockable arrangements to accommodate 2 RRL hose of 15 m length and one branch pipe painted white inside and red outside with one key. (750X600X250 mm) | Nos | 3
8 | Supply & installation of swinging type hose reel drum fabricated from 14 SWG CRCA sheets painted with red colour stove paint 2 coats over 1 coat of primer with 30 m long 20 mm dia rubber hose pipe with with SS self closing shut – off nozzle of 5 mm outlet fixed on wall. | Nos | 3
9 | Supply and installation of pressure gauge, 1/2 inch bottom entry, of suitable range with ball valves and other accessories. | Nos | 1
10 | Supply, installation of automatic 25 NB Air Release Valve | Nos | 1
11 | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends
a | Size 25NB | Nos | 5
12 | Supply & installation of 250ltr foam tank filled with 3% AFFF foam concentrate with foam making branch and pick up tube. | Nos | 1
R2 | FOAM WATER SPRAY SYSTEM
1 | Supply, erection , testing & commissioning of Deluge valve with dry pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 3/2 way Solenoid Valve, air filter regulator etc. & manual release unit. The valve shall be electro-pneumatic double inter lock system as per scheme drawing.
a | 150 mm NB | Nos | 1
2 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts.
a | 150 mm NB | Nos | 3
3 | Supply, installation, testing of Y- Strainer.
a | Size 150 mm NB | Nos | 1
4 | Supply,installation,testing and commissioning of Foam Sprinkler nozzle with necessary threaded fittings as per drawing. The sprinkler shall be Open Aspiration, Pendent type, K-42 with standard spray angle.End connection 1/2" NPT/BSP.UL/FM Approved.
a | Spray nozzle K factor -42 | Nos | 59
5 | Supply,installation and commissioning of UL/FM approved Quartzoid Bulb Detector for K factor-80. Temp rating 68 deg C | Nos | 59
6 | Supply, installation, testing and commissioning of Ratio Controller. | Nos
a | 150NB | Nos | 1
7 | Supply, installation, testing and commissioning of Foam bladder tank vertical type ,manufacturing as per ASME, section-VIII part- I. The bladder material shall be BUNA-N. The Bladder Tank shall be supplied along with all necessary valves, Hydraulically Operated Foam Concentrae Control Valve ,fittingss & instruments as per Technical data sheet attached with Tender documents.
a | Capacity of 2100 ltr. | Nos | 1
8 | Supply of AR-AFFF(3%) foam concentrate(PFOS/PFAS free) having sp. Gravity 1.0±.02 g/mlat 20⁰C , PH 7.0-8.5 & viscosity 1200 ±300 cps. | Ltr | 2100
9 | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications
a | 150 NB | Mtr | 12
b | 100 NB | Mtr | 18
c | 80 NB | Mtr | 24
d | 65 NB | Mtr | 24
e | 50 NB | Mtr | 18
f | 40NB | Mtr | 66
g | 25NB | Mtr | 284
10 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope.
a | 80 mm NB | Mtr | 24
b | 65 mm NB | Mtr | 12
c | 50 mm NB | Mtr | 18
R3 | AUTOMATIC SPRINKLER SYSTEM
1 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved red oxide primer and two coats of approved red enamel paint and welded joints complete with cutting and making good the complete with cutting and making good the walls, floors or any other surface
a | 80 mm NB | Mtr | 24
b | 65 mm NB | Mtr | 12
c | 50 mm NB | Mtr | 18
d | 40 mm NB | Mtr | 12
e | 25 mm NB | Mtr | 24
2 | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor.
a | Size 80 mm NB | Nos | 1
3 | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts.
a | Size 80 mm NB | Nos | 1
4 | Supply & fixing of paddle type Flow Switch | Nos | 1
5 | Supply,Fixing of Sprinkler Head Pendent type for K factor-80. Temp rating 68 deg C. UL/FM Approved. | Nos | 18
6 | Supply, installation of automatic 25 NB Air Release Valve | Nos | 1
7 | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends
a | Size 25NB | Nos | 2
b | Size 40NB | Nos | 1
8 | Supply,Erection and testing of Installation Control Valve complete with trims & gong.
a | Size 80 mm NB | Nos | 1
R4 | FDA SYSTEM
1 | Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | Nos | 4
3 | Supply, erection, testing & commissioning of IR Detector | Nos | 7
4 | Supply, erection, testing & commissioning of analogue addressable Manual Call point | Nos | 4
5 | Supply, erection, testing & commissioning of Hooter cum strobe | Nos | 4
6 | Supply, erction, testing & commissioning of analogue addressable Control Module | Nos | 3
7 | Supply, erection, testing & commissioning of analogue addressable Isolator Module | Nos | 2
8 | Supply, erection, testing & commissioning of analogue addressable Monitor module | Nos | 9
9 | Supply, erection, testing & commissioning of 6 Watt Ceiling mounted Speakers | Nos | 9
10 | Providing & fixing 100Watt Amplifier with necessary accessories. | Nos | 1
11 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Loop cable) | Mtr | 256
12 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Power cable) | Mtr | 127
13 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Speaker cable) | Mtr | 140
14 | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | Mtr | 256
R5 | PA SYSTEM
1 | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | Nos | 1
2 | 15 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | Nos | 3
3 | Rack Mounted 125 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | Nos | 1
4 | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | Mtr | 90
5 | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | Nos | 1
6 | Paging Loudspeaker | Nos | 1
TOTAL