## Sheet1
section_context_for_this_product_block | full_product_description | core_product_name | size | feature_or_specifications | acronymed_core_product_name | quantity | unit
F ¦ R & D BUILDING > F1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be of groove with grooved coupling. All escavation, pedestal support, structural support shall be of vendor's scope. a. 100 mm NB | ms black steel pipe | size: 100 mm NB | grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: groove with grooved coupling, scope: all excavation, pedestal support, structural support by vendor |  | 36.0 | Mtr
F ¦ R & D BUILDING > F1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be of groove with grooved coupling. All escavation, pedestal support, structural support shall be of vendor's scope. b 80 mm NB | ms black steel pipe | size: 80 mm NB | grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: groove with grooved coupling, scope: all excavation, pedestal support, structural support by vendor |  | 36.0 | Mtr
F ¦ R & D BUILDING > F1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be of groove with grooved coupling. All escavation, pedestal support, structural support shall be of vendor's scope. c 25 mm NB | ms black steel pipe | size: 25 mm NB | grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: groove with grooved coupling, scope: all excavation, pedestal support, structural support by vendor |  | 18.0 | Mtr
F ¦ R & D BUILDING > F1 ¦ HYDRANT SYSTEM | Supply & installation of swinging type hose reel drum fabricated from 14 SWG CRCA sheets painted with red colour stove paint 2 coats over 1 coat of primer with 30 m long 20 mm dia rubber hose pipe with with SS self closing shut – off nozzle of 5 mm outlet fixed on wall. | hose reel drum | hose length: 30 m, hose diameter: 20 mm, nozzle outlet: 5 mm | type: swinging, fabrication: 14 SWG CRCA sheets, painting: red colour stove paint 2 coats over 1 coat of primer, nozzle material: stainless steel, nozzle type: self closing shut-off, mounting: fixed on wall |  | 3.0 | Nos
F ¦ R & D BUILDING > F1 ¦ HYDRANT SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends a Size 25NB | globe valve | size: 25NB | material: bronze, standard: indian standard 778, end connection: screwed |  | 3.0 | Nos
F ¦ R & D BUILDING > F1 ¦ HYDRANT SYSTEM | Supply & installation of SS oblique type single headed Landing valve with 80 mm inlet and 63 mm outlet SS instantaneous male coupling with rubber cap and chain conforming to IS : 5290 including matching flanges, gasket, nuts and bolts complete. | landing valve | inlet: 80 mm, outlet: 63 mm | material: stainless steel, type: oblique, head: single, coupling: stainless steel instantaneous male, accessories: rubber cap and chain, standard: indian standard 5290, accessories: matching flanges, gasket, nuts and bolts |  | 2.0 | Nos
F ¦ R & D BUILDING > F1 ¦ HYDRANT SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. a Size 80 mm NB | butterfly valve | size: 80 mm NB | standard: british standard 5155, type: wafer, accessories: matching flanges, nuts & bolts, fittings: provided by erection vendor |  | 2.0 | Nos
F ¦ R & D BUILDING > F1 ¦ HYDRANT SYSTEM | Supply & installation of SS branch pipe with 20 mm nozzle conforming to IS : 903 complete | branch pipe | nozzle: 20 mm | material: stainless steel, standard: indian standard 903 |  | 2.0 | Nos
F ¦ R & D BUILDING > F1 ¦ HYDRANT SYSTEM | Supply & installation of 63 mm dia rubberized reinforced rubber line hose pipe in 15 m length conforming to IS : 636 Type II ISI marked with gunmetal male and female instantaneous coupling conforming to IS 903 wounded with 18 SWG copper wire complete | rubber line hose pipe | diameter: 63 mm, length: 15 m | type: rubberized reinforced, standard: indian standard 636 type II, certification: ISI, coupling: gunmetal male and female instantaneous, coupling standard: indian standard 903, wire: 18 SWG copper |  | 4.0 | Nos
F ¦ R & D BUILDING > F1 ¦ HYDRANT SYSTEM | Supply & installation of MS Hose Box of fabricated from 16 SWG CRCA sheet double door with lockable arrangements to accommodate 2 RRL hose of 15 m length and one branch pipe painted white inside and red outside with one key. (750X600X250 mm) | hose box | dimensions: 750X600X250 mm | material: ms, fabrication: 16 SWG CRCA sheet, door: double, lockable: yes, capacity: 2 RRL hose of 15 m length and one branch pipe, painting: white inside and red outside, accessory: one key |  | 2.0 | Nos
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. e 50 mm NB | ms black steel pipe | size: 50 mm NB | grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, scope: all related civil work, supports by vendor |  | 12.0 | Mtr
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. f 40 mm NB | ms black steel pipe | size: 40 mm NB | grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, scope: all related civil work, supports by vendor |  | 12.0 | Mtr
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. g 25 mm NB | ms black steel pipe | size: 25 mm NB | grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, scope: all related civil work, supports by vendor |  | 66.0 | Mtr
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. a Size150 mm NB | butterfly valve | size: 150 mm NB | standard: british standard 5155, type: wafer, fittings: matching flanges, nuts & bolts, feature: necessary fittings by erection vendor |  | 2.0 | Nos
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. b Size50 mm NB | butterfly valve | size: 50 mm NB | standard: british standard 5155, type: wafer, fittings: matching flanges, nuts & bolts, feature: necessary fittings by erection vendor |  | 1.0 | Nos
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts confirming to API 594. a Size150 mm NB | non return valve | size: 150 mm NB | type: wafer, fittings: matching flanges, nuts & bolts, standard: API 594 |  | 2.0 | Nos
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts confirming to API 594. b Size50 mm NB | non return valve | size: 50 mm NB | type: wafer, fittings: matching flanges, nuts & bolts, standard: API 594 |  | 1.0 | Nos
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & fixing of Paddle type Flow Switch | paddle type flow switch |  |  |  | 2.0 | Nos
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Fixing of Sprinkler Head Pendent type for K factor-80. Temp rating 68 deg C. UL/FM Approved. | sprinkler head pendent type | k factor: 80 | temperature rating: 68 deg C, certification: UL(underwriters laboratories), certification: FM(factory mutual) |  | 108.0 | Nos
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, installation of automatic 25 NB Air Release Valve | air release valve | size: 25 NB | feature: automatic |  | 1.0 | Nos
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends a Size 40NB | globe valve | size: 40 NB | material: bronze, standard: indian standard 778, ends: screwed |  | 2.0 | Nos
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends b Size 25NB | globe valve | size: 25 NB | material: bronze, standard: indian standard 778, ends: screwed |  | 2.0 | Nos
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Erection and testing of Installation Control Valve complete with trims & gong. a Size 100 mm NB | installation control valve | size: 100 mm NB | feature: complete with trims & gong |  | 1.0 | Nos
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. a Size 100 mm NB | gate valve | size: 100 mm NB | material: cs(carbon steel), standard: API 600, class: 150, fittings: matching flanges, nuts & bolts |  | 1.0 | Nos
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | multicriteria detector |  | type: analogue addressable |  | 25.0 | Nos
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, testing & commissioning of analogue addressable Manual Call point | manual call point |  | type: analogue addressable |  | 4.0 | Nos
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, testing & commissioning of Hooter cum strobe | hooter cum strobe |  |  |  | 4.0 | Nos
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, testing & commissioning of Telephone jack. | telephone jack |  |  |  | 2.0 | Nos
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erction, testing & commissioning of analogue addressable Control Module | control module |  | type: analogue addressable |  | 2.0 | Nos
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, testing & commissioning of analogue addressable Isolator Module | isolator module |  | type: analogue addressable |  | 1.0 | Nos
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, testing & commissioning of analogue addressable Monitor module | monitor module |  | type: analogue addressable |  | 3.0 | Nos
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. a 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cabling | size: 2C x 1.5 mm2 | feature: loop cable, fittings: lugs, laying and termination of both ends |  | 170.0 | Mtr
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. a 2C x 1.5 mm2 Armoured ( Power cable) | armoured cabling | size: 2C x 1.5 mm2 | feature: power cable, fittings: lugs, laying and termination of both ends |  | 104.0 | Mtr
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Providing & fixing FRLS CABLING complete with lugs, laying and termination of both ends. a 2C x 0.5 mm2 Armoured ( Telephone cable) | frls cabling | size: 2C x 0.5 mm2 | feature: telephone cable, fittings: lugs, laying and termination of both ends |  | 28.0 | Mtr
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Providing & fixing 200Watt Amplifier with necessary accessories. | amplifier | power: 200Watt | accessories: necessary accessories |  | 1.0 | Nos
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, testing & commissioning of Repeater Panel | repeater panel |  |  |  | 1.0 | Nos
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | ip based networkable touch screen paging station |  | feature: selection of zones, feature: supervision of system status, feature: setting of scheduled broadcasts, feature: central exchange with stand by cpu, feature: built-in monitoring loudspeaker, feature: goose-neck microphone, feature: lcd touchscreen display, feature: audio input |  | 1.0 | Nos
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | 6 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | horn type of speaker | power: 6 W | feature: high efficiency, protection: weather protection ip 65 (weatherproof type), feature: suitable for outdoor area |  | 21.0 | Nos
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Rack Mounted 200 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | power amplifier | power: 200 watt | mounting: rack mounted, feature: battery back up, feature: wattage shall be as per requirement |  | 1.0 | Nos
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | xlpe cu cable | core: 2C, cross section: 1.5 mm2 | feature: multi stranded, feature: shielded, feature: armoured, application: for power & signal |  | 164.0 | Mtr
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | dvd player |  | feature: hook up to amplifiers of pa system for music in the common areas |  | 1.0 | Nos
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Paging Loudspeaker | paging loudspeaker |  |  |  | 1.0 | Nos