## Sheet1
section_context_for_this_product_block | full_product_description | core_product_name | size | feature_or_specifications | acronymed_core_product_name | quantity | unit
D ¦ SOLVENT PLANT > D1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall of grooved with groove couplings. All escavations, pedestal supports, structural supports shall be of vendors scope. 100 mm NB | ms black steel pipe | size: 100 mm NB | material: ms(mild steel), finish: black, grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove couplings, scope: all excavations, pedestal supports, structural supports by vendor |  | 166.0 | Mtr
D ¦ SOLVENT PLANT > D1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall of grooved with groove couplings. All escavations, pedestal supports, structural supports shall be of vendors scope. 80 mm NB | ms black steel pipe | size: 80 mm NB | material: ms(mild steel), finish: black, grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove couplings, scope: all excavations, pedestal supports, structural supports by vendor |  | 56.0 | Mtr
D ¦ SOLVENT PLANT > D1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall of grooved with groove couplings. All escavations, pedestal supports, structural supports shall be of vendors scope. 25 mm NB | ms black steel pipe | size: 25 mm NB | material: ms(mild steel), finish: black, grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove couplings, scope: all excavations, pedestal supports, structural supports by vendor |  | 12.0 | Mtr
D ¦ SOLVENT PLANT > D1 ¦ HYDRANT SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. Size 100 mm NB | gate valve | size: 100 mm NB | material: cs(carbon steel), standard: api 600, class: 150, flanges: matching, accessories: nuts & bolts |  | 3.0 | Nos
D ¦ SOLVENT PLANT > D1 ¦ HYDRANT SYSTEM | Supply, installation, testing and commissioning of CS Non return valve as per BS 1868, Class 150 with companion flanges,nuts & bolts and gaskets. Size 100 mm NB | non return valve | size: 100 mm NB | material: cs(carbon steel), standard: bs 1868, class: 150, flanges: companion, accessories: nuts & bolts, gaskets |  | 3.0 | Nos
D ¦ SOLVENT PLANT > D1 ¦ HYDRANT SYSTEM | Supply & installation of SS oblique type single headed Landing valve with 80 mm inlet and 63 mm outlet SS instantaneous male coupling with rubber cap and chain conforming to IS : 5290 including matching flanges, gasket, nuts and bolts complete. | landing valve | inlet: 80 mm, outlet: 63 mm | material: ss(stainless steel), type: oblique, head: single, coupling: ss(stainless steel) instantaneous male, accessories: rubber cap and chain, standard: indian standard 5290, flanges: matching, accessories: gasket, nuts and bolts |  | 10.0 | Nos
D ¦ SOLVENT PLANT > D1 ¦ HYDRANT SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. Size 80 mm NB | butterfly valve | size: 80 mm NB | standard: bs 5155, type: wafer, flanges: matching, accessories: nuts & bolts, fittings: provided by erection vendor |  | 10.0 | Nos
D ¦ SOLVENT PLANT > D1 ¦ HYDRANT SYSTEM | Supply & installation of SS branch pipe with 20 mm nozzle conforming to IS : 903 complete | branch pipe | nozzle: 20 mm | material: ss(stainless steel), standard: indian standard 903 |  | 10.0 | Nos
D ¦ SOLVENT PLANT > D1 ¦ HYDRANT SYSTEM | Supply & installation of 63 mm dia rubberized reinforced rubber line hose pipe in 15 m length conforming to IS : 636 Type II ISI marked with gunmetal male and female instantaneous coupling conforming to IS 903 wounded with 18 SWG copper wire complete | hose pipe | diameter: 63 mm, length: 15 m | type: rubberized reinforced rubber line, standard: indian standard 636 type ii, certification: isi, coupling: gunmetal male and female instantaneous, coupling standard: indian standard 903, wire: 18 swg copper |  | 20.0 | Nos
D ¦ SOLVENT PLANT > D1 ¦ HYDRANT SYSTEM | Supply & installation of MS Hose Box of fabricated from 16 SWG CRCA sheet double door with lockable arrangements to accommodate 2 RRL hose of 15 m length and one branch pipe painted white inside and red outside with one key. (750X600X250 mm) | hose box | dimensions: 750X600X250 mm | material: ms(mild steel), sheet: 16 swg crca, doors: double, lockable: yes, capacity: 2 rrl hose of 15 m length and one branch pipe, paint: white inside and red outside, accessories: one key |  | 10.0 | Nos
D ¦ SOLVENT PLANT > D1 ¦ HYDRANT SYSTEM | Supply & installation of swinging type hose reel drum fabricated from 14 SWG CRCA sheets painted with red colour stove paint 2 coats over 1 coat of primer with 30 m long 20 mm dia rubber hose pipe with with SS self closing shut – off nozzle of 5 mm outlet fixed on wall. | hose reel drum | hose length: 30 m, hose diameter: 20 mm, nozzle outlet: 5 mm | type: swinging, material: 14 swg crca sheets, paint: red colour stove paint 2 coats over 1 coat of primer, hose: rubber, nozzle: ss(stainless steel) self closing shut-off, mounting: fixed on wall |  | 10.0 | Nos
D ¦ SOLVENT PLANT > D1 ¦ HYDRANT SYSTEM | Supply and installation of pressure gauge, 1/2 inch bottom entry, of suitable range with ball valves and other accessories. | pressure gauge | bottom entry: 1/2 inch | range: suitable, accessories: ball valves and other accessories |  | 1.0 | Nos
D ¦ SOLVENT PLANT > D1 ¦ HYDRANT SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends Size 25NB | globe valve | size: 25NB | material: bronze, standard: indian standard 778, end-connection: screwed |  | 16.0 | Nos
D ¦ SOLVENT PLANT > D1 ¦ HYDRANT SYSTEM | Supply & installation of 250ltr foam tank filled with 3% ARFFF foam concentrate with foam making branch and pick up tube. | foam tank | tank capacity: 250ltr | foam concentrate: 3% ARFFF, included: foam making branch and pick up tube |  | 2.0 | Nos
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection , testing & commissioning of Deluge valve with dry pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 2 way Solenoid Valve, etc. & manual release unit. 150 mm NB | deluge valve | size: 150 mm NB | trim assembly: dry pilot, included: strainer, drain valve, pressure gauge, pressure switch, solenoid valve: flame proof 2 way, manual release unit: included |  | 5.0 | Nos
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection , testing & commissioning of Deluge valve with dry pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 2 way Solenoid Valve, etc. & manual release unit. 100 mm NB | deluge valve | size: 100 mm NB | trim assembly: dry pilot, included: strainer, drain valve, pressure gauge, pressure switch, solenoid valve: flame proof 2 way, manual release unit: included |  | 5.0 | Nos
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, Class 150 with matching flanges complete with nuts & bolts. 150 mm NB | gate valve | size: 150 mm NB | material: cs(carbon steel), standard: API 600, class: 150, included: matching flanges, nuts & bolts |  | 15.0 | Nos
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, Class 150 with matching flanges complete with nuts & bolts. 100 mm NB | gate valve | size: 100 mm NB | material: cs(carbon steel), standard: API 600, class: 150, included: matching flanges, nuts & bolts |  | 15.0 | Nos
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing and commissioning of Y-Strainer. 150 mm NB | y-strainer | size: 150 mm NB |  |  | 5.0 | Nos
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing and commissioning of Y-Strainer. 100 mm NB | y-strainer | size: 100 mm NB |  |  | 5.0 | Nos
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply,installation,testing and commissioning of Foam Sprinkler nozzle with necessary threaded fittings as per drawing. The sprinkler shall be Open Aspiration, Pendent type, K-42 with standard spray angle.End connection 1/2" NPT/BSP.UL/FM Approved. Spray nozzle K factor -42 | foam sprinkler nozzle | k factor: 42, end connection: 1/2" NPT/BSP | type: open aspiration, type: pendent, spray angle: standard, approval: UL(underwriters laboratories)/FM(factory mutual), fittings: necessary threaded fittings as per drawing |  | 517.0 | Nos
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply,installation and commissioning of UL/FM approved Quartzoid Bulb Detector for K factor-80. Temp rating 68 deg C. | quartzoid bulb detector | k factor: 80 | approval: UL(underwriters laboratories)/FM(factory mutual), temperature rating: 68 deg C |  | 517.0 | Nos
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Capacity of 1700 ltr. | capacity | capacity: 1700 ltr. |  |  | 7.0 | Nos
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply of AR-AFFF(3%) foam concentrate(PFOS/PFAS free) having sp. Gravity 1.0±.02 g/mlat 20⁰C , PH 7.0-8.5 & viscosity 1200 ±300 cps. | ar-afff foam concentrate |  | concentration: 3%, pfos/pfas: free, specific gravity: 1.0±.02 g/ml at 20⁰C, ph: 7.0-8.5, viscosity: 1200 ±300 cps | ar-afff foam concentrate | 11900.0 | Ltr
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee, reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 150 NB | gi pipes | size: 150 NB | class: c (heavy class), standard: indian standard 1239, fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, clamps, ms brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, above ground, specification: as per specifications |  | 371.0 | Mtr
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee, reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 100 NB | gi pipes | size: 100 NB | class: c (heavy class), standard: indian standard 1239, fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, clamps, ms brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, above ground, specification: as per specifications |  | 280.0 | Mtr
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee, reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 80 NB | gi pipes | size: 80 NB | class: c (heavy class), standard: indian standard 1239, fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, clamps, ms brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, above ground, specification: as per specifications |  | 182.0 | Mtr
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee, reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 65 NB | gi pipes | size: 65 NB | class: c (heavy class), standard: indian standard 1239, fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, clamps, ms brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, above ground, specification: as per specifications |  | 227.0 | Mtr
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee, reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 50 NB | gi pipes | size: 50 NB | class: c (heavy class), standard: indian standard 1239, fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, clamps, ms brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, above ground, specification: as per specifications |  | 120.0 | Mtr
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee, reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 40NB | gi pipes | size: 40NB | class: c (heavy class), standard: indian standard 1239, fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, clamps, ms brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, above ground, specification: as per specifications |  | 454.0 | Mtr
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee, reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 25NB | gi pipes | size: 25NB | class: c (heavy class), standard: indian standard 1239, fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, clamps, ms brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, above ground, specification: as per specifications |  | 2043.0 | Mtr
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall of grooved with groove couplings. All escavations, pedestal supports, structural supports shall be of vendor's scope. 150 mm NB | ms black steel pipe | size: 150 mm NB, thickness: 5.4mm | grade: heavy, standard: indian standard 1239 part-1, fittings included: elbows, tees, flanges, reducers, clamps, ms support, dash fasteners, painting: two coats approved primer, two coats approved paint, joints: grooved with groove couplings, scope: all excavations, pedestal supports, structural supports by vendor |  | 46.0 | Mtr
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall of grooved with groove couplings. All escavations, pedestal supports, structural supports shall be of vendor's scope. 100 mm NB | ms black steel pipe | size: 100 mm NB, thickness: 5.4mm | grade: heavy, standard: indian standard 1239 part-1, fittings included: elbows, tees, flanges, reducers, clamps, ms support, dash fasteners, painting: two coats approved primer, two coats approved paint, joints: grooved with groove couplings, scope: all excavations, pedestal supports, structural supports by vendor |  | 75.0 | Mtr
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing & commissioning of Air Buffer tank complete with necessary components. The compressor shall be of capacity 15 M³/Hr( FAD), discharge pressure 10 bar, single stage, reciprocating type. | air buffer tank | compressor capacity: 15 M³/Hr (FAD), discharge pressure: 10 bar | compressor type: single stage, reciprocating |  | 1.0 | Nos
D ¦ SOLVENT PLANT > D3 ¦ WATER CURTAIN | Supply, erection and testing of heavy grade(class-C) pipes conforming to IS-1239 including all fittings viz. tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer and structural steels for pipe supports. Hanger support with anchor fasteners and clamps shall be supplied to fix the pipes on ceiling wall etc. including supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners) as per specification. Cutting of floors, walls etc and making it good after erection of pipes shall be of vendor's scope. Necessary painting with 2 coats of primer and 2 coats of synthetic enamel paints to be done and supply of paints shall be with vendor's scope. 50 NB | pipes | size: 50 NB | grade: heavy (class-c), standard: indian standard 1239, fittings included: tees, elbows, reducers, union, flanges, rubber gaskets, gi nuts, bolts, washer, structural steels, hanger support: anchor fasteners, clamps, fixing: floor/wall/ceiling, painting: 2 coats primer, 2 coats synthetic enamel, supply of paints: vendor's scope, making good after erection: vendor's scope |  | 106.0 | Mtr
D ¦ SOLVENT PLANT > D3 ¦ WATER CURTAIN | Supply, erection and testing of heavy grade(class-C) pipes conforming to IS-1239 including all fittings viz. tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer and structural steels for pipe supports. Hanger support with anchor fasteners and clamps shall be supplied to fix the pipes on ceiling wall etc. including supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners) as per specification. Cutting of floors, walls etc and making it good after erection of pipes shall be of vendor's scope. Necessary painting with 2 coats of primer and 2 coats of synthetic enamel paints to be done and supply of paints shall be with vendor's scope. 65 NB | pipes | size: 65 NB | grade: heavy (class-c), standard: indian standard 1239, fittings included: tees, elbows, reducers, union, flanges, rubber gaskets, gi nuts, bolts, washer, structural steels, hanger support: anchor fasteners, clamps, fixing: floor/wall/ceiling, painting: 2 coats primer, 2 coats synthetic enamel, supply of paints: vendor's scope, making good after erection: vendor's scope |  | 126.0 | Mtr
D ¦ SOLVENT PLANT > D3 ¦ WATER CURTAIN | Supply, erection and testing of heavy grade(class-C) pipes conforming to IS-1239 including all fittings viz. tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer and structural steels for pipe supports. Hanger support with anchor fasteners and clamps shall be supplied to fix the pipes on ceiling wall etc. including supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners) as per specification. Cutting of floors, walls etc and making it good after erection of pipes shall be of vendor's scope. Necessary painting with 2 coats of primer and 2 coats of synthetic enamel paints to be done and supply of paints shall be with vendor's scope. 80 NB | pipes | size: 80 NB | grade: heavy (class-c), standard: indian standard 1239, fittings included: tees, elbows, reducers, union, flanges, rubber gaskets, gi nuts, bolts, washer, structural steels, hanger support: anchor fasteners, clamps, fixing: floor/wall/ceiling, painting: 2 coats primer, 2 coats synthetic enamel, supply of paints: vendor's scope, making good after erection: vendor's scope |  | 120.0 | Mtr
D ¦ SOLVENT PLANT > D3 ¦ WATER CURTAIN | Supply, erection and testing of heavy grade(class-C) pipes conforming to IS-1239 including all fittings viz. tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer and structural steels for pipe supports. Hanger support with anchor fasteners and clamps shall be supplied to fix the pipes on ceiling wall etc. including supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners) as per specification. Cutting of floors, walls etc and making it good after erection of pipes shall be of vendor's scope. Necessary painting with 2 coats of primer and 2 coats of synthetic enamel paints to be done and supply of paints shall be with vendor's scope. 100 NB | pipes | size: 100 NB | grade: heavy (class-c), standard: indian standard 1239, fittings included: tees, elbows, reducers, union, flanges, rubber gaskets, gi nuts, bolts, washer, structural steels, hanger support: anchor fasteners, clamps, fixing: floor/wall/ceiling, painting: 2 coats primer, 2 coats synthetic enamel, supply of paints: vendor's scope, making good after erection: vendor's scope |  | 66.0 | Mtr
D ¦ SOLVENT PLANT > D3 ¦ WATER CURTAIN | Providing & fixing Cast Iron Y Strainer. Size 80 NB | y strainer | size: 80 NB | material: cast iron |  | 3.0 | Nos
D ¦ SOLVENT PLANT > D3 ¦ WATER CURTAIN | Providing & fixing Cast Iron Y Strainer. Size 100 NB | y strainer | size: 100 NB | material: cast iron |  | 5.0 | Nos
D ¦ SOLVENT PLANT > D3 ¦ WATER CURTAIN | Supply & fixing of SS Water Curtain Nozzle with (K>=71). UL/FM Approved. | water curtain nozzle |  | material: ss(stainless steel), k-factor: >=71, certification: UL(underwriters laboratories), certification: FM(factory mutual) |  | 119.0 | Nos
D ¦ SOLVENT PLANT > D3 ¦ WATER CURTAIN | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, Class 150 with matching flanges complete with nuts & bolts. Size 80 NB | gate valve | size: 80 NB | material: cs(carbon steel), standard: API 600, class: 150, ends: matching flanges, included: nuts & bolts |  | 9.0 | Nos
D ¦ SOLVENT PLANT > D3 ¦ WATER CURTAIN | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, Class 150 with matching flanges complete with nuts & bolts. Size 100 NB | gate valve | size: 100 NB | material: cs(carbon steel), standard: API 600, class: 150, ends: matching flanges, included: nuts & bolts |  | 15.0 | Nos
D ¦ SOLVENT PLANT > D4 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be with grooved couplings. Necesary supports of all kind shall be of vendor's scope. 80 mm NB | ms black steel pipe | size: 80 mm NB | material: ms(mild steel), finish: black, grade: heavy, thickness: 5.4mm, standard: IS 1239 Part -1, fittings included: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats approved primer, two coats approved paint, joints: grooved couplings, supports: all kinds, vendor's scope |  | 18.0 | Mtr
D ¦ SOLVENT PLANT > D4 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be with grooved couplings. Necesary supports of all kind shall be of vendor's scope. 65 mm NB | ms black steel pipe | size: 65 mm NB | material: ms(mild steel), finish: black, grade: heavy, thickness: 5.4mm, standard: IS 1239 Part -1, fittings included: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats approved primer, two coats approved paint, joints: grooved couplings, supports: all kinds, vendor's scope |  | 12.0 | Mtr
D ¦ SOLVENT PLANT > D4 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be with grooved couplings. Necesary supports of all kind shall be of vendor's scope. 50 mm NB | ms black steel pipe | size: 50 mm NB | material: ms(mild steel), finish: black, grade: heavy, thickness: 5.4mm, standard: IS 1239 Part -1, fittings included: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats approved primer, two coats approved paint, joints: grooved couplings, supports: all kinds, vendor's scope |  | 12.0 | Mtr
D ¦ SOLVENT PLANT > D4 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be with grooved couplings. Necesary supports of all kind shall be of vendor's scope. 40 mm NB | ms black steel pipe | size: 40 mm NB | material: ms(mild steel), finish: black, grade: heavy, thickness: 5.4mm, standard: IS 1239 Part -1, fittings included: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats approved primer, two coats approved paint, joints: grooved couplings, supports: all kinds, vendor's scope |  | 18.0 | Mtr
D ¦ SOLVENT PLANT > D4 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be with grooved couplings. Necesary supports of all kind shall be of vendor's scope. 25 mm NB | ms black steel pipe | size: 25 mm NB | material: ms(mild steel), finish: black, grade: heavy, thickness: 5.4mm, standard: IS 1239 Part -1, fittings included: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats approved primer, two coats approved paint, joints: grooved couplings, supports: all kinds, vendor's scope |  | 36.0 | Mtr
D ¦ SOLVENT PLANT > D4 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. Size 65 mm NB | butterfly valve | size: 65 mm NB | standard: BS 5155, type: wafer, ends: matching flanges, included: nuts & bolts, fittings: provided by erection vendor |  | 2.0 | Nos
D ¦ SOLVENT PLANT > D4 ¦ AUTOMATIC SPRINKLER SYSTEM | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts. Size 65 mm NB | non return valve | size: 65 mm NB | type: wafer, ends: matching flanges, included: nuts & bolts |  | 1.0 | Nos
D ¦ SOLVENT PLANT > D4 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & fixing of Paddle type Flow Switch | paddle type flow switch |  |  |  | 1.0 | Nos
D ¦ SOLVENT PLANT > D4 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Fixing of Sprinkler Head Pendent type for K factor-80. Temp rating 68 deg C. UL/FM Approved. | sprinkler head pendent type |  | k-factor: 80, temperature rating: 68 deg C, certification: UL(underwriters laboratories), certification: FM(factory mutual) |  | 16.0 | Nos
D ¦ SOLVENT PLANT > D4 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, installation of automatic 25 NB Air Release Valve | air release valve | size: 25 NB | type: automatic |  | 1.0 | Nos
D ¦ SOLVENT PLANT > D4 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends a Size 25NB | globe valve | size: 25 NB | material: bronze, standard: IS 778, end connection: screwed |  | 2.0 | Nos
D ¦ SOLVENT PLANT > D4 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends b Size 40NB | globe valve | size: 40 NB | material: bronze, standard: IS 778, end connection: screwed |  | 1.0 | Nos
D ¦ SOLVENT PLANT > D4 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Erection and testing of Installation Control Valve complete with trims & gong. a Size 80 mm NB | installation control valve | size: 80 mm NB | feature: complete with trims & gong |  | 1.0 | Nos
D ¦ SOLVENT PLANT > D4 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, Class 150 with matching flanges complete with nuts & bolts. a Size 80 NB | cs(carbon steel) gate valve | size: 80 NB | material: cs(carbon steel), standard: API 600, class: 150, end connection: matching flanges, feature: complete with nuts & bolts |  | 1.0 | Nos
D ¦ SOLVENT PLANT > D5 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | multicriteria detector |  | type: analogue addressable |  | 12.0 | Nos
D ¦ SOLVENT PLANT > D5 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of IR Detector | ir(infrared) detector |  |  | ir detector | 15.0 | Nos
D ¦ SOLVENT PLANT > D5 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable explosion proof Manual Call point | manual call point |  | type: analogue addressable, feature: explosion proof |  | 12.0 | Nos
D ¦ SOLVENT PLANT > D5 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of explosion proof Hooter | hooter |  | feature: explosion proof |  | 12.0 | Nos
D ¦ SOLVENT PLANT > D5 ¦ FDA SYSTEM | Supply, erction, testing & commissioning of analogue addressable Control Module | control module |  | type: analogue addressable |  | 26.0 | Nos
D ¦ SOLVENT PLANT > D5 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Isolator Module | isolator module |  | type: analogue addressable |  | 4.0 | Nos
D ¦ SOLVENT PLANT > D5 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Monitor module | monitor module |  | type: analogue addressable |  | 38.0 | Nos
D ¦ SOLVENT PLANT > D5 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. a ¦ 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cabling | configuration: 2C x 1.5 mm2 | feature: complete with lugs, laying and termination of both ends, type: loop cable |  | 690.0 | Mtr
D ¦ SOLVENT PLANT > D5 ¦ FDA SYSTEM | Providing & fixing FRLS CABLING complete with lugs, laying and termination of both ends. a ¦ 2C x 0.5 mm2 Armoured ( Telephone cable) | frls cabling | configuration: 2C x 0.5 mm2 | feature: complete with lugs, laying and termination of both ends, type: telephone cable, type: armoured |  | 86.0 | Mtr
D ¦ SOLVENT PLANT > D5 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. a ¦ 2C x 1.5 mm2 Armoured ( Power cable) | armoured cabling | configuration: 2C x 1.5 mm2 | feature: complete with lugs, laying and termination of both ends, type: power cable |  | 620.0 | Mtr
D ¦ SOLVENT PLANT > D5 ¦ FDA SYSTEM | Supply, erection, fabrication, testing and commission of VOC detector with range of 1 – 1000 ppm isobutylene equivalent.and following accessoriesa) DigiPID internal dust filter (Pack of 5) b) Waterproof Filter Assy, RAEGuard2 PID, Pack of 5 c) DigiPID Teflon UV electrode shield pack of 10 d) DigiPID Dust Cover e) Air Drying Pre Filter Kit f) DigiPID external water trap filter (Pack of 5) | voc detector | range: 1 – 1000 ppm isobutylene equivalent | accessories: DigiPID internal dust filter (Pack of 5), Waterproof Filter Assy, RAEGuard2 PID, Pack of 5, DigiPID Teflon UV electrode shield pack of 10, DigiPID Dust Cover, Air Drying Pre Filter Kit, DigiPID external water trap filter (Pack of 5) |  | 16.0 | Nos
D ¦ SOLVENT PLANT > D5 ¦ FDA SYSTEM | Supply, installation, testing and commissioning of aspiration detector with CMOS imager combined with multiple photodiode for reliable very early warning in a wide range of environments with minimal nuisance alarms. The detector should have 4 pipe inlet and min 100m pipelength support per inlet.The detector should have Smart on-board filter retains dust count and remaining filter life for predictable maintenance& coverage area of min 5000 Sq. | aspiration detector | pipe inlet: 4, pipelength support per inlet: min 100m, coverage area: min 5000 Sq. | imager: CMOS, sensor: multiple photodiode, feature: very early warning, feature: minimal nuisance alarms, feature: smart on-board filter retains dust count and remaining filter life for predictable maintenance |  | 4.0 | Nos
D ¦ SOLVENT PLANT > D5 ¦ FDA SYSTEM | Supply,Installation,Testing & Commissioning of UL/VDS listed CPVC Pipe 25 mm Dia & Pipe Accessories for the Aspiration detection. | cpvc pipe | diameter: 25 mm | certification: UL(underwriters laboratories), certification: VDS, feature: listed, feature: for the aspiration detection |  | 846.0 | Mtr
D ¦ SOLVENT PLANT > D5 ¦ FDA SYSTEM | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable trays |  | material: gi(galvanized iron), feature: for laying all type of cables, feature: including all necessary structural supports |  | 894.0 | Mtr
D ¦ SOLVENT PLANT > D6 ¦ PA SYSTEM | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | ip based networkable touch screen paging station |  | feature: selection of zones, feature: supervision of system status, feature: setting of scheduled broadcasts, feature: central exchange with stand by CPU, feature: built-in monitoring loudspeaker, feature: goose-neck microphone, feature: LCD touchscreen display, feature: audio input |  | 1.0 | Nos
D ¦ SOLVENT PLANT > D6 ¦ PA SYSTEM | 15 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | horn type speaker | power: 15 W | feature: high efficiency, protection: IP 65, feature: weatherproof type, feature: suitable for outdoor area |  | 8.0 | Nos
D ¦ SOLVENT PLANT > D6 ¦ PA SYSTEM | 30 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | horn type speaker | power: 30 W | feature: high efficiency, protection: IP 65, feature: weatherproof type, feature: suitable for outdoor area |  | 8.0 | Nos
D ¦ SOLVENT PLANT > D6 ¦ PA SYSTEM | Rack Mounted 500 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | power amplifier | power: 500 watt | feature: rack mounted, feature: battery back up, feature: wattage shall be as per requirement |  | 1.0 | Nos
D ¦ SOLVENT PLANT > D6 ¦ PA SYSTEM | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | xlpe cu cable | configuration: 2C x 1.5 mm2 | feature: multi stranded, feature: shielded, feature: armoured, application: power & signal |  | 440.0 | Mtr