## Sheet1
section_context_for_this_product_block | full_product_description | core_product_name | size | feature_or_specifications | acronymed_core_product_name | quantity | unit
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection , testing & commissioning of Deluge valve with wet pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 3/2 way Solenoid Valve, air filter regulator etc. & manual release unit. The valve shall be electro-pneumatic type. 80 mm NB | deluge valve | size: 80 mm NB | assembly: wet pilot trim, fitted with: strainer, drain valve, pressure gauge, pressure switch, solenoid valve: flame proof 3/2 way, air filter regulator: included, manual release unit: included, type: electro-pneumatic |  | 2.0 | Nos
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. 80 mm NB | gate valve | size: 80 mm NB | material: cs(carbon steel), standard: api 600, class: 150, flanges: matching, included: nuts & bolts |  | 6.0 | Nos
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, installation, testing of Y- Stainer . 80 mm NB | y-stainer | size: 80 mm NB |  |  | 2.0 | Nos
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply,installation,testing and commissioning of HVWS NOZZLE with necessary threaded fittings as per drawing. K26, SPRAY ANGLE=100° | hvws nozzle |  | model: K26, spray angle: 100°, fittings: necessary threaded fittings as per drawing |  | 32.0 | Nos
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply,installation and commissioning of UL/FM approved Quartzoid Bulb Detector for K factor-80. Temp rating 68 deg C | quartzoid bulb detector |  | certification: UL(underwriters laboratories), certification: FM(factory mutual), k factor: 80, temperature rating: 68 deg C |  | 32.0 | Nos
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 80 NB | gi pipe | size: 80 NB | class: c class(heavy class), standard: IS 1239(indian standard 1239), fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, fixing: clamps to ms(mild steel) brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, application: above ground pipes, as per fire authorities requirement |  | 36.0 | Mtr
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 65 NB | gi pipe | size: 65 NB | class: c class(heavy class), standard: IS 1239(indian standard 1239), fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, fixing: clamps to ms(mild steel) brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, application: above ground pipes, as per fire authorities requirement |  | 12.0 | Mtr
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 50 NB | gi pipe | size: 50 NB | class: c class(heavy class), standard: IS 1239(indian standard 1239), fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, fixing: clamps to ms(mild steel) brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, application: above ground pipes, as per fire authorities requirement |  | 78.0 | Mtr
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 40NB | gi pipe | size: 40NB | class: c class(heavy class), standard: IS 1239(indian standard 1239), fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, fixing: clamps to ms(mild steel) brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, application: above ground pipes, as per fire authorities requirement |  | 42.0 | Mtr
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 25NB | gi pipe | size: 25NB | class: c class(heavy class), standard: IS 1239(indian standard 1239), fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, fixing: clamps to ms(mild steel) brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, application: above ground pipes, as per fire authorities requirement |  | 78.0 | Mtr
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | analogue addressable multicriteria detector |  |  |  | 34.0 | Nos
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing & commissioning of analogue addressable Manual Call point | analogue addressable manual call point |  |  |  | 4.0 | Nos
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing & commissioning of Hooter cum strobe | hooter cum strobe |  |  |  | 4.0 | Nos
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erction, testing & commissioning of analogue addressable Control Module | analogue addressable control module |  |  |  | 4.0 | Nos
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing & commissioning of analogue addressable Isolator Module | analogue addressable isolator module |  |  |  | 2.0 | Nos
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing & commissioning of analogue addressable Monitor module | analogue addressable monitor module |  |  |  | 2.0 | Nos
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cabling | configuration: 2C x 1.5 mm2 | feature: complete with lugs, laying and termination of both ends, type: loop cable |  | 240.0 | Mtr
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Power cable) | armoured cabling | configuration: 2C x 1.5 mm2 | feature: complete with lugs, laying and termination of both ends, type: power cable |  | 110.0 | Mtr
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable trays |  | feature: for laying all type of cables as indicated above, feature: including all necessary structural supports |  | 240.0 | Mtr