## Sheet1
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
242 | 0 | 01II | INSTRUMENTATION
243 | 0 | 01II.30 | PRESSURE INSTRUMENTS (Excl. supply Impulse pipe/Tubing materials)
244 | 0 | 01II.30.10 | Installation of Pressure Transmitters/ Pressure Switches (with or without Pulsation Dampener, Over-range Protector)/ Diaphragm seal type Pressure Transmitters/ Diaphragm seal type Pressure Switches including mounting on Yoke/ Surface, supply of supports for capillary, supply and erection of supports for impulse lines wherever required, fabrication and installation of manifolds/ impulse lines with supports as per Standard indicated below, laying of capillary on supports, hydraulic testing and painting of supports but exclusive of Supply of Instrument, Piping/tubing materials, all Electrical/ Pneumatic connections, Yoke and Calibration.
245 | 0 | 01II.30.10.1V31 | In Carbon Steel as per Standard 7-52-1221 | 3 | nos
246 | 0 | 01II.260 | RADAR LEVEL INSTRUMENTS
247 | 0 | 01II.260.10 | Installation of radar sensor and antenna, flanged type connection on equipment nozzle/ rail mounting with/without still well, but exclusive of supply of instruments. Installation of electronics units (total system for indication, transmission, marshalling etc. for one tank), including mounting on Yoke, supply of angle tray with supports, fabrication and erection of supports and laying of cable up to instrument/probe with clamps, termination of cables at both ends, but exclusive of supply of Instruments, supply of yokes and Calibration.
248 | 0 | 01II.260.10.2 | Installation of Top Mounted Radar | 9 | nos
249 | 0 | 01II.260.10.4 | Installation of Still well (8") of Carbon/Stainless steel | 9 | nos
250 | 0 | 01II.297 | DISMANTLING OF EXISTING INSTRUMENTS
251 | 0 | 01II.297.10 | Disconnection, Dismantling, removal of existing instruments with associated accessories presently installed on the equipment, associated piping, connecting stairs, structures/ stairways/ operating platforms, etc., which are getting dismantled/ modified and transportation of the same to stores as per tender specifications, approved drawings, and instruction of Engineer-in-charge. This also includes removal of impulse lines/ lead lines/ purge gas lines/ purge oil lines with pipe fittings, tubes, tube fittings, accessories, supports, trays, cables, cable glands, etc.,
252 | 0 | 01II.297.10.1 | Instruments | 50 | nos
253 | 0 | 01II.330 | TEMPERATURE INSTRUMENTS
254 | 0 | 01II.330.10 | Installation of Temperature Indicators/ Gauges (Filled system/ Bimetallic) RTD/ Thermocouple/ Temperature Switches/ Temperature transmitters with flanged and installation of Instruments, Electrical/ Pneumatic connection but exclusive of Supply of Instruments/ Elements/ Thermowell, and Calibration.
255 | 0 | 01II.330.10.2 | Temperature Indicator/ Gauges (Bimetallic Type) with thermowell on flanged wells | 3 | nos
256 | 0 | 01II.330.10.5 | RTD with Thermowell on flanged wells | 3 | nos
257 | 0 | 01II.330.10.6 | Test Thermowell (flanged) | 2 | nos
258 | 0 | 01II.340 | TEMPERATURE TRANSMITTERS (REMOTE MOUNTED)
259 | 0 | 01II.340.10 | Thermocouple/ RTD element with thermowell, along with Temperature Transmitter remote mounted. Installation of transmitter including mounting on yoke, fabrication and erection of supports with clamps and laying of extension/RTD cable upto thermocouple, termination of cables at both ends, painting of supports but exclusive of Supply of Instruments, Cable, Yoke and Calibration.
260 | 0 | 01II.340.10.1 | Temperature Transmitter and Thermocouple with flanged well | 3 | nos
261 | 0 | 01II.440 | DETECTOR SYSTEMS
262 | 0 | 01II.440.10 | Installation of LEL and H2S detectors/monitors, beacon lights and hooters including supply of supports but exclusive of Supply of Detectors, Yoke and Calibration.
263 | 0 | 01II.440.10.10 | LEL Detectors. | 6 | nos
264 | 0 | 01II.440.10.50 | Beacon Lights | 1 | nos
265 | 0 | 01II.440.10.60 | Hooters | 1 | nos
266 | 0 | 01II.450 | MISCELLANEOUS ITEMS AND DEVICES
267 | 0 | 01II.450.10 | Mounting of Miscellaneous instrument items as listed below on Yoke; fabrication and erection of Supports and including installation of instrument items, painting of supports but exclusive of Supply of Instrument items, Piping/ Tubing material / Calibration and supply and erection of Yoke support.
268 | 0 | 01II.450.10.5 | Flame-proof Push Button Station/ Selector Switches /Lamps. | 3 | nos
269 | 0 | 01II.450.10.17 | 3 way/ 4 way Junction Boxes. | 3 | nos
270 | 0 | 01II.450.10.19 | Electronic Local Indicator. | 9 | nos
271 | 0 | 01II.500 | CALIBRATION/ TESTING
272 | 0 | 01II.500.60 | Cleaning, calibration of the instruments listed below including removal of instrument from reinstalled locations like panels, enclosures, racks, field etc., and fixing them back in respective places, providing equipments, necessary test jig, Instrument Air, Nitrogen Cylinders, test reports, all consumable, except for special imported test equipments for electronic instruments to be supplied by owner if available.
273 | 0 | 01II.500.60.13 | Diaphragm Seal Pressure Transmitters | 3 | nos
274 | 0 | 01II.500.60.33 | Temperature gauges | 3 | nos
275 | 0 | 01II.500.60.39 | Temperature Transmitters | 3 | nos
276 | 0 | 01II.500.60.44 | Tank Level Instrument (Radar type) | 9 | nos
277 | 0 | 01II.500.60.61 | Electronic Local Indicator | 9 | nos
278 | 0 | 01II.500.60.81 | LEL Detectors | 6 | nos
279 | 0 | 01II.510 | LOOP CHECKING
280 | 0 | 01II.510.10 | Loop checking (excluding calibration/ testing) of the instruments listed below including verifying the functional performance of all elements comprising the loop, thereby ensuring proper interconnections and operation, with all other specifications inline with clause 4.13 of Standard specification for Erection tender 6-52-0060.
281 | 0 | 01II.510.10.3 | Diaphragm Seal Pressure transmitters | 3 | nos
282 | 0 | 01II.510.10.10 | Temperature Transmitters | 3 | nos
283 | 0 | 01II.510.10.13 | Tank Level Instruments (Radar type) | 9 | nos
284 | 0 | 01II.510.10.15 | Electronic Local Indicator | 9 | nos
285 | 0 | 01II.510.10.17 | Gas Detectors | 6 | nos
286 | 0 | 01II.510.10.35 | Push Button/Selector Switches/Lamps | 3 | nos
287 | 0 | 01II.510.10.40 | Hooter / Beacon | 2 | nos
288 | 0 | 01II.550 | SUPPLY ITEMS
289 | 0 | 01II.550.10 | Supply of Instrument items as per specifications enclosed elsewhere in the Tender.
290 | 0 | 01II.550.10.22 | 1/2 " GI Conduit | 20 | m
291 | 0 | 01II.550.10.23 | 3/4 " GI Conduit | 20 | m
292 | 0 | 01II.550.10.24 | 1 " GI Conduit | 20 | m
293 | 0 | 01II.550.10.32V1 | Weatherproof & Flameproof Adapter for cable gland suitable for Gas Gr.IIC : ISO M20 x 1/2" NPT(F) | 5 | nos
294 | 0 | 01II.550.10.32V2 | Weatherproof & Flameproof Adapter for cable gland suitable for Gas Gr.IIC : ISO M16 x 1/2" NPT(F) | 5 | nos
295 | 0 | 01II.550.10.32V3 | Weatherproof & Flameproof Adapter for cable gland suitable for Gas Gr.IIC : ISO M20 x 3/4" NPT(F) | 5 | nos
296 | 0 | 01II.550.10.32V4 | Weatherproof & Flameproof Adapter for cable gland suitable for Gas Gr.IIC : 3/4"NPT(M) x 1/2" NPT(F) | 5 | nos
297 | 0 | 01II.550.10.32V5 | Weatherproof & Flameproof Adapter for cable gland suitable for Gas Gr.IIC : 1/2"NPT(M) x 3/4" NPT(F) | 5 | nos
298 | 0 | 01II.550.10.32V6 | Weatherproof & Flameproof Adapter for cable gland suitable for Gas Gr.IIC : 1"NPT(M) x 1/2" NPT(F) | 5 | nos
299 | 0 | 01II.550.10.32V7 | Weatherproof & Flameproof Adapter for cable gland suitable for Gas Gr.IIC : 1.5" NPT(M) x 1" NPT(F) | 5 | nos
300 | 0 | 01II.550.20 | Supply of Junction boxes of various types and specifications
301 | 0 | 01II.550.20.2V2 | Junction Box, Weatherproof + Flameproof (Gas Groups - IIC) type 3 Way | 3 | nos
302 | 0 | 01II.550.20.2V3 | Junction Box, Weatherproof + Flameproof (Gas Groups - IIC) type for 12 Pair Cable | 3 | nos
303 | 0 | 01II.550.20.2V4 | Junction Box, Weatherproof + Flameproof (Gas Groups - IIC) type for 8 Triad Cable | 3 | nos
304 | 0 | 01II.550.20.2V7 | Junction Box, Weatherproof + Flameproof (Gas Groups - IIC) type for 6 Pair Cable | 2 | nos
305 | 0 | 01II.550.20.3V2 | Junction Box Weatherproof + Flameproof (Gas Groups - IIC) for 2 Core X 10/16/35 mm2 Power Cable including | 2 | nos
306 | 0 | 01II.550.20.3V3 | Junction Box Weatherproof + Flameproof (Gas Groups - IIC) for 2 Core X 50/70 mm2 Power Cable including | 1 | nos
307 | 0 | 01II.550.30 | Supply of Cable glands of various types and specifications
308 | 0 | 01II.550.30.6V5 | Double compression type Cable gland, weatherproof + Flameproof (Gas Group IIC) type, SS 304 material with PVC shroud 1/2" NPTM | 80 | nos
309 | 0 | 01II.550.30.6V6 | Double compression type Cable gland, weatherproof + Flameproof (Gas Group IIC) type, SS 304 material with PVC shroud 1" NPTM | 10 | nos
310 | 0 | 01II.550.30.6V7 | Double compression type Cable gland, weatherproof + Flameproof (Gas Group IIC) type, SS 304 material with PVC shroud 1 1/2" NPTM | 5 | nos
311 | 0 | 01II.550.30.6V8 | Double compression type Cable gland, weatherproof + Flameproof (Gas Group IIC) type, SS 304 material with PVC shroud 3/4" NPTM | 15 | nos
312 | 0 | 01II.550.30.6V10 | Double compression type Cab le gland, weatherproof + Flameproof (Gas Group IIC) type, SS 304 material with PVC shroud 1 1/4" NPTM | 5 | nos
313 | 0 | 01II.550.30.8V1 | Double compression type Cable gland, weatherproof + Flameproof (Gas Group IIC) type, SS 304 material with PVC shroud 3/4" ET with check nut | 4 | nos
314 | 0 | 01II.550.30.8V6 | Double compression type Cable gland, weatherproof + Flameproof (Gas Group IIC) type, SS 304 material with PVC shroud 1" ET with check nut | 4 | nos
315 | 0 | 01II.550.30.8V7 | Double compression type Cable gland, weatherproof + Flameproof (Gas Group IIC) type, SS 304 material with PVC shroud 1 1/4" ET with check nut | 4 | nos
316 | 0 | 01II.550.30.8V8 | Double compression type Cable gland, weatherproof + Flameproof (Gas Group IIC) type, SS 304 material with PVC shroud 1 1/2" ET with check nut | 5 | nos
317 | 0 | 01II.550.30.9V1 | M20 Double compression type Cable gland, weatherproof + Flameproof ( Gas Group IIC),Ni plated Brass material | 2 | nos
318 | 0 | 01II.550.30.9V2 | M25 Double compression type Cable gland, weatherproof + Flameproof ( Gas Group IIC),Ni plated Brass material | 2 | nos
319 | 0 | 01II.550.30.9V3 | M32 Double compression type Cable gland, weatherproof + Flameproof ( Gas Group IIC),Ni plated Brass material | 2 | nos
320 | 0 | 01II.550.40 | Supply of plugs for cable entries of various types and specifications
321 | 0 | 01II.550.40.4V4 | Plug, weatherproof + flameproof (Gas Group IIC) type, SS 304 material, 1/2" NPTM | 30 | nos
322 | 0 | 01II.550.40.4V5 | Plug, weatherproof + flameproof (Gas Group IIC) type, SS 304 material, 1" NPTM | 4 | nos
323 | 0 | 01II.550.40.4V6 | Plug, weatherproof + flameproof (Gas Group IIC) type, SS 304 material, 1 1/2" NPTM | 4 | nos
324 | 0 | 01II.550.40.4V8 | Plug, weatherproof + flameproof (Gas Group IIC) type, SS 304 material, 3/4" NPTM | 10 | nos
325 | 0 | 01II.550.40.4V9 | Plug, weatherproof + flameproof (Gas Group IIC) type, SS 304 material, 1 1/4" NPTM | 4 | nos
326 | 0 | 01II.550.50 | Supply of compression tube fittings in Stainless Steel of various types and specifications
327 | 0 | 01II.550.50.1V2 | Male Connector: Material: SS-316 : Size: 1/2" NPTM X 1/2" OD 153 Bar | 30 | nos
328 | 0 | 01II.550.50.1V19 | Male Connector: Material: SS-316 : Size: 1/2" NPTM X 12 mm OD 153 Bar | 10 | nos
329 | 0 | 01II.550.50.1V20 | Male Connector: Material: SS-316 : Size: 1/2" NPTM X 6 mm OD 153 Bar | 20 | nos
330 | 0 | 01II.550.50.1V21 | Male Connector: Material: SS-316 : Size: 1/4" NPTM X 6 mm OD 153 Bar | 20 | nos
331 | 0 | 01II.550.50.1V22 | Male Connector: Material: SS-316 : Size: 1/4" NPTM X 12 mm OD 153 Bar | 10 | nos
332 | 0 | 01II.550.50.1V50 | Female Connector: Material: SS-316 : Size: 1/2" NPTF X 1/2" OD 153 Bar | 20 | nos
333 | 0 | 01II.550.50.3V1 | Tube Union: Material: SS-316 ; Size: 1/2" OD x 1/2" OD 153 Bar | 10 | nos
334 | 0 | 01II.550.50.3V2 | Tube Union: Material: SS-316 ; Size: 1/4" OD x 1/4" OD 153 Bar | 10 | nos
335 | 0 | 01II.550.50.3V4 | Tube Union: Material: SS-316 ; Size: 12 mm OD x 12 mm OD 153 Bar | 10 | nos
336 | 0 | 01II.550.50.3V5 | Tube Union: Material: SS-316 ; Size: 6 mm OD x 6 mm OD 153 Bar | 10 | nos
337 | 0 | 01II.550.50.3V10 | Tube Union: Material: SS-316 ; Size: 3/4" OD x 3/4" OD 153 Bar | 1 | nos
338 | 0 | 01II.550.50.4V1 | Tube Cap; Material: SS-316 ; Size : 1/2" OD 153 Bar | 20 | nos
339 | 0 | 01II.550.50.4V3 | Tube Cap; Material: SS-316 ; Size : 1/4" OD 153 Bar | 10 | nos
340 | 0 | 01II.550.50.5 | SS 316 Ball Valve 1/2" NB OD 41 Bar | 20 | nos
341 | 0 | 01II.550.50.MC15 | Tube Plug; Material: SS-316 ; Size : 6mm OD 153 Bar | 80 | nos
342 | 0 | 01II.550.54 | Supply of Miniaturized Globe Pattern Needle Valve 1/2" NB forged bar-stock type with inside screwed bonnet,back seated blow-out proof system , 1/2"NPTF threaded connection, approximate dimension 76mm end to end length , 135 mm height, Line pressure class upto 600#,with minimum cold working pressure of 102 Kg/cm2g, seat leak test pressure 112Kg/cm2g , shell leakage test pressure of 153kg/cm2g
343 | 0 | 01II.550.54.1V1 | Body MOC SS316 | 5 | nos
344 | 0 | 01II.550.60 | Supply of compression tube fittings in Brass of various types and specifications
345 | 0 | 01II.550.60.1V2 | Female Connector : Material: Brass : Size: 1/2" NPTF X 1/4" OD , 80 bar | 1 | nos
346 | 0 | 01II.550.60.3V2 | Tube Union ; Material: Brass ; Size: 1/4" OD x 1/4" OD , 80 bar | 1 | nos
347 | 0 | 01II.550.70 | Supply of instrument tubes of different types and specifications
348 | 0 | 01II.550.70.2V2 | SS316L tube 1/2" OD 153 Bar | 50 | m
349 | 0 | 01II.550.70.2V3 | SS316L tube 1/4" OD 153 Bar | 50 | m
350 | 0 | 01II.550.70.2V5 | SS316L tube 12 mm OD 153 Bar | 20 | m
351 | 0 | 01II.550.70.MC15 | Bare Copper Tube, 1/4"" OD, 1.0mm THK, 80 bar | 5 | m
352 | 0 | 01II.600 | JUNCTION BOX INSTALLATION
353 | 0 | 01II.600.20 | Installation of weatherproof and flameproof junction boxes including supply, fabrication and installation of supports, installation of junction boxes, supply of 14 SWG GI wire (max. length 10 m per Junction Box), laying and connection, screwing plugs for unused entries and painting but exclusive of supply of junction boxes and glands/ fittings.
354 | 0 | 01II.600.20.1 | For cable size 6P x 0.5/1.0/1.5/2.5 mm²/16 AWG Signal/FF/Alarm/ Control | 2 | nos
355 | 0 | 01II.600.20.5 | For cable size 12P x 0.5/1.0/1.5/2.5 mm²/16 AWG Signal/FF/Alarm/ Control | 3 | nos
356 | 0 | 01II.600.20.43 | For cable size 8T x 1.5/ 2.5 mm² RTD/ Gas Detector | 3 | nos
357 | 0 | 01II.600.40 | Installation of weatherproof and flameproof three way junction boxes for Power including supply, fabrication and installation of supports, installation of junction boxes, supply of 14 SWG GI wire (max. length 10 m per Junction Box), laying and connection, screwing plugs for unused entries and painting but exclusive of supply of junction boxes and glands/ fittings.
358 | 0 | 01II.600.40.1V5 | For cable size 2C x 10 mm² | 2 | nos
359 | 0 | 01II.600.40.1V9 | For cable size 2C x 4 mm² | 1 | nos
360 | 0 | 01II.600.40.1V11 | For cable size 2C x 6 mm² | 1 | nos
361 | 0 | 01II.600.50 | Installation of Multi Cable transit frames complete with all insert blocks, stay plates, unused blocks with cables piece inserted, end packing etc. on wall for Cable entry including necessary civil works, welding, supply and installation of additional steel plate for unused portion of cutouts, fixing of frames, pulling cables to blocks and installation of blocks on frames as per manufacturer's recommendation.
362 | 0 | 01II.600.50.1 | 8 + 8 x 10 | 1 | nos
363 | 0 | 01II.600.50.4 | 8 + 8 x 4 | 1 | nos
364 | 0 | 01II.610 | LAYING OF CABLES
365 | 0 | 01II.610.10 | Laying of instrumentation cables for signal, alarm, shutdown, control and signal cable on ducts, main trays, perforated trays, angle trays, trenches (including opening of cable duct covers if required through IRCs {Instrument Road Crossings}) including clamping, glanding the cables, termination at both ends including shield/ drain/ communication wire, providing and fixing identifying tags and megger testing but exclusive of supply of cables and erection of ducts, main tray, perforated tray/ angle trays and preparation of cable trench.
366 | 0 | 01II.610.10.1 | Signal / Alarm / Control Cables of cable sizes 1P x 1.5 / 2.5 mm² | 2500 | m
367 | 0 | 01II.610.10.4 | Signal/ Alarm/ Control Cables of cable sizes 12C / 6P x 1.5 / 2.5 mm² | 500 | m
368 | 0 | 01II.610.10.9 | Signal/ Alarm/ Control Cables of cable sizes 24C /12P x 1.5/ 2.5 mm² | 500 | m
369 | 0 | 01II.610.10.12 | Special armoured serial link MODBUS TCP/IP/RS485 Serial/ cable | 1000 | m
370 | 0 | 01II.610.30 | Laying of thermocouple/ RTD/ LEL Detector/ H2S Detector cables on ducts, main trays, perforated trays, angle trays, trenches (including through IRCs {Instrument Road Crossings}) including opening of cable duct covers if required clamping, glanding the cables, termination at both ends including shield/ drain/communication wire providing and fixing of identifying tags and megger testing but exclusive of supply of multi cables and erection of ducts, main tray, perforated tray/angle tray and preparation of cable trench.
371 | 0 | 01II.610.30.21 | 1 Pair / 2 Pair x 16/20 AWG Thermocouple Cable | 200 | m
372 | 0 | 01II.610.30.41 | 1 Triad/ Quad x 1.5 mm² RTD/ LEL Cable | 400 | m
373 | 0 | 01II.610.30.54 | 8 Triad/ Quad x 2.5 mm² RTD/ LEL Cable | 1500 | m
374 | 0 | 01II.610.80 | Laying of power cables on ducts, main trays, perforated trays, angle trays, trenches (including through IRCs) including opening of cable duct covers if required clamping, glanding the cables, termination at both ends including shield/ drain/ communication wire providing and fixing of identifying tags and megger testing but exclusive of supply of multi cables and erection of ducts, main tray, perforated tray/ angle tray and preparation of cable trench
375 | 0 | 01II.610.80.1V2 | For cable size 2C x 6 mm² | 800 | m
376 | 0 | 01II.610.80.1V3 | For cable size 2C x 10 mm² | 800 | m
377 | 0 | 01II.610.80.1V7 | For cable size 2C x 2.5 mm² | 400 | m
378 | 0 | 01II.610.80.1V10 | For cable size 2C x 4 mm² | 800 | m
379 | 0 | 01II.630 | SAND FILLING IN TRENCHES
380 | 0 | 01II.630.10 | Supply of sand and filling of concrete cable trenches with sand after cable laying is completed including levelling of sand and fixing back of precast concrete slabs on the trench.
381 | 0 | 01II.630.10.4V4 | Trench Size 2000 mm (W) x 1500 mm (D, total for trench, not depth of sand) | 50 | m
382 | 0 | 01II.650 | EARTHING
383 | 0 | 01II.650.10 | Supply, laying and termination of both ends of earthing cables from earth grid pit to the DCS/ Local panels/ Barrier earth bus bars in trays/ conduits/ trenches as required.
384 | 0 | 01II.650.10.1 | At both ends of earth grid/ Instruments of GI wire (12 AWG) in trays and conduits as required excluding earth-pit preparation and electrode installation. | 500 | m
385 | 0 | 01II.650.10.3 | For earthing cable 25 mm² size with PVC insulation. | 30 | m
386 | 0 | 01II.700 | PIPING / TUBING / FABRICATION WORK
387 | 0 | 01II.700.5 | Laying of copper tube for steam tracing of Instruments, primary impulse lines with steam traps/valve accessories including clamping, supply of clamps termination at both ends, providing and fixing metallic tags and hydraulic testing as per Standard given below but exclusive of supply of tube/ fitting and insulation as per standards
388 | 0 | 01II.700.5.MC10 | For sizes 1/4"/ 6 mm | 100 | m
389 | 0 | 01II.750 | DRILLING AND THREADING OF BLIND FLANGES
390 | 0 | 01II.750.10 | Making of 1/2" screwed connections on 1-1/2" blind flanges of specified materials/ ratings, by drilling holes and tapping
391 | 0 | 01II.750.10.1V1 | In Carbon Steel , 150# flange | 1 | nos
392 | 0 | 01II.750.10.1V2 | In Carbon Steel , 300# flange | 1 | nos
393 | 0 | 01II.750.20 | Making of 1/2" screwed connections on 2" blind flanges of specified materials/ ratings, by drilling holes and tapping
394 | 0 | 01II.750.20.1V1 | In Carbon Steel , 150# flange | 1 | nos
395 | 0 | 01II.750.20.1V2 | In Carbon Steel , 300# flange | 1 | nos
396 | 0 | 01II.750.50 | Making of 1/2" screwed connections on 3" blind flanges of specified materials/ ratings, by drilling holes and tapping
397 | 0 | 01II.750.50.1V1 | In Carbon Steel , 150# flange | 1 | nos
398 | 0 | 01II.780 | PWHT/ STRESS RELIEF - CARBON STEEL
399 | 0 | 01II.780.10 | Post-weld Heat Treatment (PWHT)/ Stress Relieving of all weld joints in impulse piping of Pressure Gauges installations.
400 | 0 | 01II.780.10.2 | Installation standard 7-52-0434/ 0435/1121/1122 | 1 | nos
401 | 0 | 01II.780.30 | Post-weld Heat Treatment (PWHT)/ Stress Relieving of all weld joints in impulse piping of Pressure Instruments installations.
402 | 0 | 01II.780.30.2 | Installation standard 7-52-0439/ 0441/1133/1134 | 2 | nos
403 | 0 | 01II.785 | RADIOGRAPHY - CARBON STEEL WELD JOINTS
404 | 0 | 01II.785.30 | Radiography conforming to the requirements of the Piping Class for all weld joints in impulse piping of Pressure Instruments installations
405 | 0 | 01II.785.30.2 | Installation standard 7-52-0439/ 0441/1133/1134 | 3 | nos
406 | 0 | 01II.800 | STRUCTURAL
407 | 0 | 01II.800.20 | Supply, Fabrication and erection of Galvanised Iron duct and its supports as per standard. Duct configurations include Duct Equal Tee, Duct Expander Tee, Duct Reducer Tee, Duct Offset Bend, Duct with Reducer, Vertical Plane Tee, Vertical Plane Elbow, Duct Bridge (jumpover), Sleeves.
408 | 0 | 01II.800.20.1V4 | Run of Duct 600mm (W) X 300mm (H) | 50 | m
409 | 0 | 01II.800.20.1V5 | Run of Duct 800mm (W) X 300mm (H) | 1000 | m
410 | 0 | 01II.800.52 | Supply, fabrication and erection of angle / channel trays fabricated out of GI angle as per drawing including supply, fabrication and erection of its supports and painting as per painting standard attached including supply of paint.
411 | 0 | 01II.800.52.1V2 | Tray of 50x 50 x 6mm angle | 500 | m
412 | 0 | 01II.800.75 | Supply and erection of prefabricated Anodised Aluminium perforated trays and its supports including tees, bends and elbows , painting of supports including supply of supports,paint as per painting specifications
413 | 0 | 01II.800.75.1V1 | Tray of 60mm (W) X 20mm (H) with cover | 1500 | m
414 | 0 | 01II.800.75.1V2 | Tray of 150mm (W) X 30mm (H) with cover | 300 | m
415 | 0 | 01II.800.75.1V3 | Tray of 300mm (W) X 30mm (H) with cover | 200 | m
416 | 0 | 01II.802 | CANOPY FOR INSTRUMENTS AND JUNCTION BOXES
417 | 0 | 01II.802.20 | Supply of Prefabricated FRP canopies along with mounting accessories for local instruments, Transmitters, Junction Box etc. for mounting on the stanchion and alignment as per standard 7-52-0105
418 | 0 | 01II.802.20.1 | FRP Canopy (All sides closed) - Field Instruments | 40 | nos
419 | 0 | 01II.900 | GENERAL SITE WORK
420 | 0 | 01II.900.10 | Supply of Yoke supports for transmitters/ preamplifiers (wherever applicable) including supply, fabrication and erection of instrument yoke of all types and painting of yoke supports but exclusive of mounting of Instrument on supports.
421 | 0 | 01II.900.10.1 | 2" Yoke supports as per standard 7-52-0101 | 50 | nos
422 | 0 | 01II.900.40 | Identification of instrument items wherever required including supply of approved colour of paint/ paints (Fluorescent), painting of tag number (approx 25-50 mm high)on instrument item like transmitter, switches, level gauges, control valves etc. as specified by Engineer-in-Charge.
423 | 0 | 01II.900.40.1 | Identification of instrument items | 100 | nos
424 | 0 | 01II.900.60 | CHIEF CONTROLLER OF EXPLOSIVE( CCE) CERTIFICATES FOR FIELD ELECTRICAL/ ELECTRONIC INSTRUMENTS & ACCESSORIES AND EQUIPMENTS
425 | 0 | 01II.900.60.1 | Obtaining certificate of approval from Chief Controller Of Explosives( CCE) for field electrical/electronic instruments & accessories and equipments based on type test certificate made available from the instrument vendors including submission of application to statutory authorities , necessary fees, all test certificates, equipment drawings in required volumes, interaction with the authorities, follow-up for approval, obtaining necessary approval certificate before energization of field electrical/electronic instruments & accessories and equipments. | 1 | nos