## Sheet1
section_context_for_this_product_block | full_product_description | core_product_name | size | feature_or_specifications | acronymed_core_product_name | quantity | unit
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H1 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection , testing & commissioning of Deluge valve with dry pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 3/2 way Solenoid Valve, air filter regulator etc. & manual release unit. The valve shall be electro-pneumatic double inter lock system as per scheme drawing. | deluge valve |  | trim assembly: dry pilot, included: strainer, included: drain valve, included: pressure gauge, included: pressure switch, included: flame proof 3/2 way solenoid valve, included: air filter regulator, included: manual release unit, system: electro-pneumatic double inter lock
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H1 ¦ FOAM WATER SPRAY SYSTEM | 80 mm NB | deluge valve | size: 80 mm NB |  |  | 3.0 | Nos
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H1 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. | gate valve |  | material: cs(carbon steel), standard: api 600, class: 150, included: matching flanges, included: nuts & bolts
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H1 ¦ FOAM WATER SPRAY SYSTEM | 80 mm NB | gate valve | size: 80 mm NB |  |  | 9.0 | Nos
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H1 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing and commissioning of Y-Strainer.. | y-strainer
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H1 ¦ FOAM WATER SPRAY SYSTEM | Size 80 mm NB | y-strainer | size: 80 mm NB |  |  | 3.0 | Nos
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H1 ¦ FOAM WATER SPRAY SYSTEM | Supply,installation,testing and commissioning of Foam Sprinkler nozzle with necessary threaded fittings as per drawing. The sprinkler shall be Open Aspiration, Pendent type, K-42 with standard spray angle.End connection 1/2" NPT/BSP.UL/FM Approved. | foam sprinkler nozzle |  | fittings: necessary threaded, type: open aspiration, type: pendent, k-factor: 42, spray angle: standard, end connection: 1/2" NPT/BSP, certification: UL(underwriters laboratories), certification: FM(factory mutual)
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H1 ¦ FOAM WATER SPRAY SYSTEM | Spray nozzle K factor -42 | foam sprinkler nozzle | k-factor: 42 |  |  | 17.0 | Nos
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H1 ¦ FOAM WATER SPRAY SYSTEM | Supply,installation and commissioning of UL/FM approved Quartzoid Bulb Detector for K factor-80. Temp rating 68 deg C | quartzoid bulb detector | k-factor: 80 | certification: UL(underwriters laboratories), certification: FM(factory mutual), temperature rating: 68 deg C |  | 17.0 | Nos
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H1 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing and commissioning of Ratio Controller. | ratio controller
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H1 ¦ FOAM WATER SPRAY SYSTEM | 80NB | ratio controller | size: 80NB |  |  | 3.0 | Nos
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H1 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing and commissioning of Foam bladder tank vertical type ,manufacturing as per ASME, section-VIII part- I. The bladder material shall be BUNA-N. The Bladder Tank shall be supplied along with all necessary valves, Hydraulically Operated Foam Concentrae Control Valve ,fittingss & instruments as per Technical data sheet attached with Tender documents. | foam bladder tank |  | type: vertical, standard: ASME(american society of mechanical engineers) section-VIII part-I, bladder material: BUNA-N, included: all necessary valves, included: hydraulically operated foam concentrate control valve, included: fittings & instruments
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H1 ¦ FOAM WATER SPRAY SYSTEM | Capacity of 500 ltr. | foam bladder tank | capacity: 500 ltr. |  |  | 1.0 | Nos
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H1 ¦ FOAM WATER SPRAY SYSTEM | Supply of AR-AFFF(3%) foam concentrate(PFOS/PFAS free) having sp. Gravity 1.0±.02 g/mlat 20⁰C , PH 7.0-8.5 & viscosity 1200 ±300 cps. | ar-afff foam concentrate |  | concentration: 3%, feature: PFOS/PFAS free, specific gravity: 1.0±.02 g/ml at 20⁰C, pH: 7.0-8.5, viscosity: 1200 ±300 cps | ar-afff foam concentrate | 500.0 | Ltr
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H1 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. | ms black steel pipe | thickness: 5.4mm | grade: heavy, standard: IS 1239 Part -1 (indian standard 1239 part -1), fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, coating: two coats of approved primer, coating: two coats of approved paint, joint: grooved with groove coupling, included: all related civil work, supports etc of vendor's scope
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H1 ¦ FOAM WATER SPRAY SYSTEM | 100 mm NB | ms black steel pipe | size: 100 mm NB |  |  | 12.0 | Mtr
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H1 ¦ FOAM WATER SPRAY SYSTEM | 80 mm NB | ms black steel pipe | size: 80 mm NB |  |  | 36.0 | Mtr
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H2 ¦ FOAM GENERATOR | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications | gi pipes |  | class: C Class(Heavy Class), standard: IS 1239(indian standard 1239), fittings: threaded or grooved, included: cutting pipes to correct lengths, included: fittings like elbow, tee, reducer and welding flanges, included: fixing with clamps to MS brackets / hangers, included: steel supports, coating: zinc chromate primer, coating: 2 coats red enamel paint, requirement: as per fire authorities, application: above ground pipes
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H2 ¦ FOAM GENERATOR | 150 NB | gi pipes | size: 150 NB |  |  | 34.0 | Mtr
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H2 ¦ FOAM GENERATOR | 100 NB | gi pipes | size: 100 NB |  |  | 89.0 | Mtr
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H2 ¦ FOAM GENERATOR | Supply, erection , testing & commissioning of Deluge valve with dry pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch,dry pilot actuator, air filter regulator etc. & manual release unit. | deluge valve |  | trim assembly: dry pilot, included: strainer, included: drain valve, included: pressure gauge, included: pressure switch, included: dry pilot actuator, included: air filter regulator, included: manual release unit
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H2 ¦ FOAM GENERATOR | Size 150 NB | deluge valve | size: 150 NB |  |  | 2.0 | Nos
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H2 ¦ FOAM GENERATOR | Providing & fixing Cast Iron Y Strainer. | y strainer |  | material: cast iron
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H2 ¦ FOAM GENERATOR | Size 150 NB | y strainer | size: 150 NB |  |  | 2.0 | Nos
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H2 ¦ FOAM GENERATOR | Supply & fixing of SS-304 FOAM GENERATOR with Minimum flow 120lpm | foam generator | minimum flow: 120 lpm | material: SS-304(stainless steel 304) |  | 4.0 | Nos
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H2 ¦ FOAM GENERATOR | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. | gate valve |  | material: CS(carbon steel), standard: API 600, class: 150, included: matching flanges, included: nuts & bolts
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H2 ¦ FOAM GENERATOR | Size 150 NB | gate valve | size: 150 NB |  |  | 6.0 | Nos
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H2 ¦ FOAM GENERATOR | Supply, installation, testing and commissioning of Atmospheric Foam tank vertical type ,manufacturing as per ASME, section-VIII part- I. Tank shall be supplied along with all necessary valves, fittingss & instruments as per Technical data sheet attached with Tender documents. | atmospheric foam tank vertical type |  | standard: ASME section-VIII part-I, included: all necessary valves, fittings & instruments as per technical data sheet attached with tender documents
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H2 ¦ FOAM GENERATOR | Capacity of 250 ltr. | atmospheric foam tank vertical type | tank capacity: 250 ltr. |  |  | 2.0 | Nos
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H2 ¦ FOAM GENERATOR | Supply of AR-AFFF(3%) foam concentrate (PFOS/PFAS free) having sp. Gravity 1.0±.02 g/mlat 20⁰C , pH 7.0-8.5 & viscosity 1200 ±300 cps. | ar-afff foam concentrate |  | concentration: 3%, feature: PFOS/PFAS free, specific gravity: 1.0±.02 g/ml at 20⁰C, pH: 7.0-8.5, viscosity: 1200 ±300 cps | ar-afff foam concentrate | 500.0 | Ltr
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H2 ¦ FOAM GENERATOR | Supply, erection, testing & commissioning of analogue addressable Monitor module | monitor module |  | feature: analogue addressable |  | 4.0 | Nos
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H2 ¦ FOAM GENERATOR | Supply, erection, testing & commissioning of IR Detector | ir detector |  |  | ir detector | 4.0 | Nos
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H2 ¦ FOAM GENERATOR | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. | armoured cabling |  | feature: complete with lugs, laying and termination of both ends
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H2 ¦ FOAM GENERATOR | 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cabling | size: 2C x 1.5 mm2 | feature: loop cable |  | 106.0 | Mtr
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H2 ¦ FOAM GENERATOR | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable trays |  | feature: for laying all type of cables as indicated above including all necessary structural supports |  | 106.0 | Mtr