## Sheet1
section_context_for_this_product_block | full_product_description | core_product_name | size | feature_or_specifications | acronymed_core_product_name | quantity | unit
K ¦ RAW MATERIAL STORE > K1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 100 mm NB | ms black steel pipe | size: 100 mm NB | material: ms(mild steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 Part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, scope: all related civil work, supports of vendor's scope |  | 36.0 | Mtr
K ¦ RAW MATERIAL STORE > K1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 80 mm NB | ms black steel pipe | size: 80 mm NB | material: ms(mild steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 Part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, scope: all related civil work, supports of vendor's scope |  | 12.0 | Mtr
K ¦ RAW MATERIAL STORE > K1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 25 mm NB | ms black steel pipe | size: 25 mm NB | material: ms(mild steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 Part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, scope: all related civil work, supports of vendor's scope |  | 6.0 | Mtr
K ¦ RAW MATERIAL STORE > K1 ¦ HYDRANT SYSTEM | Supply & installation of SS oblique type single headed Landing valve with 80 mm inlet and 63 mm outlet SS instantaneous male coupling with rubber cap and chain conforming to IS : 5290 including matching flanges, gasket, nuts and bolts complete. | landing valve | inlet: 80 mm, outlet: 63 mm | material: ss(stainless steel), type: oblique, head: single, coupling: ss(stainless steel) instantaneous male, accessories: rubber cap and chain, standard: indian standard 5290, accessories: matching flanges, gasket, nuts and bolts |  | 4.0 | Nos
K ¦ RAW MATERIAL STORE > K1 ¦ HYDRANT SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. Size 80 mm NB | butterfly valve | size: 80 mm NB | standard: british standard 5155, type: wafer, accessories: matching flanges, nuts and bolts, fittings: necessary fittings by erection vendor |  | 4.0 | Nos
K ¦ RAW MATERIAL STORE > K1 ¦ HYDRANT SYSTEM | Supply & installation of SS branch pipe with 20 mm nozzle conforming to IS : 903 complete | branch pipe | nozzle: 20 mm | material: ss(stainless steel), standard: indian standard 903 |  | 4.0 | Nos
K ¦ RAW MATERIAL STORE > K1 ¦ HYDRANT SYSTEM | Supply & installation of 63 mm dia rubberized reinforced rubber line hose pipe in 15 m length conforming to IS : 636 Type II ISI marked with gunmetal male and female instantaneous coupling conforming to IS 903 wounded with 18 SWG copper wire complete | hose pipe | diameter: 63 mm, length: 15 m | material: rubberized reinforced rubber, standard: indian standard 636 Type II, certification: ISI, coupling: gunmetal male and female instantaneous, coupling standard: indian standard 903, wire: 18 SWG copper wire |  | 8.0 | Nos
K ¦ RAW MATERIAL STORE > K1 ¦ HYDRANT SYSTEM | Supply & installation of MS Hose Box of fabricated from 16 SWG CRCA sheet double door with lockable arrangements to accommodate 2 RRL hose of 15 m length and one branch pipe painted white inside and red outside with one key. (750X600X250 mm). | hose box | dimensions: 750X600X250 mm | material: ms(mild steel), sheet: 16 SWG CRCA, door: double, lockable: yes, capacity: 2 RRL hose of 15 m length and one branch pipe, painting: white inside and red outside, accessories: one key |  | 4.0 | Nos
K ¦ RAW MATERIAL STORE > K1 ¦ HYDRANT SYSTEM | Supply & installation of swinging type hose reel drum fabricated from 14 SWG CRCA sheets painted with red colour stove paint 2 coats over 1 coat of primer with 30 m long 20 mm dia rubber hose pipe with with SS self closing shut – off nozzle of 5 mm outlet fixed on wall. | hose reel drum | hose length: 30 m, hose diameter: 20 mm, nozzle outlet: 5 mm | type: swinging, material: 14 SWG CRCA sheets, painting: red colour stove paint 2 coats over 1 coat of primer, hose material: rubber, nozzle: ss(stainless steel) self closing shut-off, mounting: fixed on wall |  | 4.0 | Nos
K ¦ RAW MATERIAL STORE > K1 ¦ HYDRANT SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends Size 25NB | globe valve | size: 25NB | material: bronze, standard: indian standard 778, ends: screwed |  | 4.0 | Nos
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 50 mm NB | ms black steel pipe | size: 50 mm NB | material: ms(mild steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 Part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, scope: all related civil work, supports of vendor's scope |  | 293.0 | Mtr
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 40 mm NB | ms black steel pipe | size: 40 mm NB | material: ms(mild steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 Part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, scope: all related civil work, supports of vendor's scope |  | 384.0 | Mtr
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. Size150 mm NB | butterfly valve | size: 150 mm NB | standard: british standard 5155, type: wafer, fittings: matching flanges, nuts & bolts, feature: necessary fittings provided by erection vendor |  | 3.0 | Nos
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. Size100 mm NB | butterfly valve | size: 100 mm NB | standard: british standard 5155, type: wafer, fittings: matching flanges, nuts & bolts, feature: necessary fittings provided by erection vendor |  | 1.0 | Nos
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts confirming IS:5312(PN16). Size150 mm NB | non return valve | size: 150 mm NB | type: wafer, fittings: matching flanges, nuts & bolts, standard: indian standard 5312(PN16) |  | 3.0 | Nos
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts confirming IS:5312(PN16). Size100 mm NB | non return valve | size: 100 mm NB | type: wafer, fittings: matching flanges, nuts & bolts, standard: indian standard 5312(PN16) |  | 1.0 | Nos
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & fixing of paddle type Flow Switch | flow switch |  | type: paddle |  | 4.0 | Nos
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Fixing of Sprinkler Head Pendent type for K factor-160 Temp rating 68 deg. CUL/FM Approved. | sprinkler head pendent type | k factor: 160 | temperature rating: 68 deg, certification: cul(underwriters laboratories), certification: fm(factory mutual) |  | 316.0 | Nos
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, installation of automatic 25 NB Air Release Valve | air release valve | size: 25 NB | feature: automatic |  | 1.0 | Nos
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends Size 40NB | globe valve | size: 40 NB | material: bronze, standard: indian standard 778, end connection: screwed |  | 2.0 | Nos
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends Size 25NB | globe valve | size: 25 NB | material: bronze, standard: indian standard 778, end connection: screwed |  | 2.0 | Nos
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Erection and testing of Installation Control Valve complete with trims & gong. Size 150 mm NB | installation control valve | size: 150 mm NB | feature: complete with trims & gong |  | 1.0 | Nos
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | a ¦ 50 NB | pipe | size: 50 NB |  |  | 18.0 | Mtr
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | b ¦ 65 NB | pipe | size: 65 NB |  |  | 18.0 | Mtr
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | c ¦ 80 NB | pipe | size: 80 NB |  |  | 16.0 | Mtr
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | 2 ¦ Supply, erection , testing & commissioning of Deluge valve with wet pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 2 way Solenoid Valve, air filter regulator etc. & manual release unit. | deluge valve |  | feature: wet pilot trim assembly, strainer, drain valve, pressure gauge, pressure switch, flame proof 2 way solenoid valve, air filter regulator, manual release unit
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | a ¦ Size 80 NB | deluge valve | size: 80 NB |  |  | 2.0 | Nos
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | 3 ¦ Providing & fixing Cast Iron Y Strainer. | y strainer |  | material: cast iron
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | a ¦ Size 80 NB | y strainer | size: 80 NB |  |  | 2.0 | Nos
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | 4 ¦ Supply & fixing of SS Water Curtain Nozzle (K>=71)).UL/FM Approved. | water curtain nozzle |  | material: ss(stainless steel), certification: UL(underwriters laboratories), certification: FM(factory mutual), feature: K>=71 |  | 20.0 | Nos
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | 5 ¦ Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. | gate valve |  | material: cs(carbon steel), standard: API 600, class: 150, fittings: matching flanges, nuts & bolts
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | a ¦ Size 80 NB | gate valve | size: 80 NB |  |  | 6.0 | Nos
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | 6 ¦ Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. | ms black steel pipe |  | grade: heavy, thickness: 5.4mm, standard: indian standard 1239 Part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, pipe joints: grooved with groove coupling, civil work: all related civil work, supports etc shall be of vendor's scope
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | a ¦ 150 mm NB | ms black steel pipe | size: 150 mm NB |  |  | 18.0 | Mtr
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | b ¦ 100 mm NB | ms black steel pipe | size: 100 mm NB |  |  | 24.0 | Mtr
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | c ¦ 80 mm NB | ms black steel pipe | size: 80 mm NB |  |  | 12.0 | Mtr
K ¦ RAW MATERIAL STORE > K4 ¦ FDA SYSTEM | 1 ¦ Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | multicriteria detector |  | type: analogue addressable |  | 89.0 | Nos
K ¦ RAW MATERIAL STORE > K4 ¦ FDA SYSTEM | 2 ¦ Supply, erection, testing & commissioning of analogue addressable Manual Call point | manual call point |  | type: analogue addressable |  | 7.0 | Nos
K ¦ RAW MATERIAL STORE > K4 ¦ FDA SYSTEM | 3 ¦ Supply, erection, testing & commissioning of Hooter cum strobe | hooter cum strobe |  |  |  | 7.0 | Nos
K ¦ RAW MATERIAL STORE > K4 ¦ FDA SYSTEM | 5 ¦ Supply, erction, testing & commissioning of analogue addressable Control Module | control module |  | type: analogue addressable |  | 3.0 | Nos
K ¦ RAW MATERIAL STORE > K4 ¦ FDA SYSTEM | 6 ¦ Supply, erection, testing & commissioning of analogue addressable Isolator Module | isolator module |  | type: analogue addressable |  | 2.0 | Nos
K ¦ RAW MATERIAL STORE > K4 ¦ FDA SYSTEM | 7 ¦ Supply, erection, testing & commissioning of analogue addressable Monitor module | monitor module |  | type: analogue addressable |  | 2.0 | Nos
K ¦ RAW MATERIAL STORE > K4 ¦ FDA SYSTEM | 8a ¦ 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cable | configuration: 2C x 1.5 mm2 | type: armoured, application: loop cable |  | 754.0 | Mtr
K ¦ RAW MATERIAL STORE > K4 ¦ FDA SYSTEM | 9a ¦ 2C x 1.5 mm2 Armoured ( Power cable) | armoured cable | configuration: 2C x 1.5 mm2 | type: armoured, application: power cable |  | 297.0 | Mtr
K ¦ RAW MATERIAL STORE > K4 ¦ FDA SYSTEM | 10a ¦ 2C x 0.5 mm2 Armoured ( Telephone cable) | armoured cable | configuration: 2C x 0.5 mm2 | type: armoured, application: telephone cable, type: FRLS (flame retardant low smoke) |  | 20.0 | Mtr
K ¦ RAW MATERIAL STORE > K4 ¦ FDA SYSTEM | 11 ¦ Supply, installation, testing and commissioning of aspiration detector with CMOS imager combined with multiple photodiode for reliable very early warning in a wide range of environments with minimal nuisance alarms. The detector should have 4 pipe inlet and min 100m pipelength support per inlet.The detector should have Smart on-board filter retains dust count and remaining filter life for predictable maintenance& coverage area of min 5000 Sq. | aspiration detector | pipe inlet: 4, pipelength support per inlet: min 100m, coverage area: min 5000 Sq. | imager: CMOS, sensor: multiple photodiode, feature: very early warning, feature: minimal nuisance alarms, feature: smart on-board filter retains dust count and remaining filter life for predictable maintenance |  | 6.0 | Nos
K ¦ RAW MATERIAL STORE > K4 ¦ FDA SYSTEM | 12 ¦ Supply,Installation,Testing & Commissioning of UL/VDS listed CPVC Pipe 25 mm Dia & Pipe Accessories for the Aspiration detection. | cpvc pipe | diameter: 25 mm | certification: UL(underwriters laboratories), certification: VDS, application: aspiration detection, material: CPVC (chlorinated polyvinyl chloride) |  | 441.0 | Mtr
K ¦ RAW MATERIAL STORE > K4 ¦ FDA SYSTEM | 13 ¦ Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable trays |  | material: GI (galvanized iron), application: laying all type of cables, feature: including all necessary structural supports |  | 754.0 | Mtr
K ¦ RAW MATERIAL STORE > K5 ¦ PA SYSTEM | 1 ¦ IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | paging station |  | type: IP based networkable, feature: touch screen, feature: selection of zones, feature: supervision of system status, feature: scheduled broadcasts, feature: central exchange with standby CPU, feature: built-in monitoring loudspeaker, feature: goose-neck microphone, feature: LCD touchscreen display, feature: audio input |  | 1.0 | Nos
K ¦ RAW MATERIAL STORE > K5 ¦ PA SYSTEM | 2 ¦ 30 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | horn speaker | power: 30 W | efficiency: high, protection: IP 65, feature: weatherproof, application: suitable for outdoor area |  | 8.0 | Nos
K ¦ RAW MATERIAL STORE > K5 ¦ PA SYSTEM | 3 ¦ 15 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | horn speaker | power: 15 W | efficiency: high, protection: IP 65, feature: weatherproof, application: suitable for outdoor area |  | 1.0 | Nos
K ¦ RAW MATERIAL STORE > K5 ¦ PA SYSTEM | 5 ¦ 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | xlpe cu cable | core: 2C, cross section: 1.5 mm2 | conductor: multi stranded, feature: shielded, feature: armoured, application: power & signal |  | 250.0 | Mtr
K ¦ RAW MATERIAL STORE > K5 ¦ PA SYSTEM | 6 ¦ DVD player with features to hook up to amplifiers of PA system for music in the common areas. | dvd player |  | feature: hook up to amplifiers of PA system for music in the common areas |  | 1.0 | Nos
K ¦ RAW MATERIAL STORE > K5 ¦ PA SYSTEM | 7 ¦ Paging Loudspeaker | paging loudspeaker |  |  |  | 1.0 | Nos