## Sheet1
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
O | SECURITY ROOM
O1 | FDA SYSTEM
1 | Supply, installation, testing and commissioning of Microprocessor based 6 Loop expandable upto 10 loops,Networkable analogue addressable type fire alarm control panel with 640 character LCD display.Detectors can be any mix of ion, photo, laser photo,thermal, or multi-sensor detectors; modules can be addressable pull stations, normally open contact devices,two-wire smoke, notification, or relay modules. Four access levels, Printer Port,RS-485 port for repeater/mimic panel communication,240 volts AC power supply, automatic battery charger, 24 volts sealed lead acid batteries sufficient for 24 hours normal working and then be capable of operating the system for 10 Min during an emergency conditions as required. The Panel shall have compatibility with BACKNET/MODBUS CARD for integration. | Nos | 1
2 | Providing & fixing of PA console with selector zone facility with necessary accessories. | Nos | 1
3 | Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | Nos | 6
4 | Supply, erection, testing & commissioning of analogue addressable Manual Call point | Nos | 2
5 | Supply, erection, testing & commissioning of Hooter cum strobe | Nos | 2
6 | Supply, erection, testing & commissioning of Telephone jack. | Nos | 1
7 | Supply, erction, testing & commissioning of analogue addressable Control Module | Nos | 1
8 | Supply, erection, testing & commissioning of analogue addressable Isolator Module | Nos | 2
9 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Loop cable) | Mtr | 38
10 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Power cable) | Mtr | 29
11 | Providing & fixing FRLS CABLING complete with lugs, laying and termination of both ends.
a | 2C x 0.5 mm2 Armoured ( Telephone cable) | Mtr | 12
12 | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | Mtr | 38
O2 | PA SYSTEM
1 | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | Nos | 1
2 | 6 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | Nos | 3
3 | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | Mtr | 19
4 | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | Nos | 1
5 | Paging Loudspeaker | Nos | 1
TOTAL