## Sheet1
section_context_for_this_product_block | full_product_description | core_product_name | size | feature_or_specifications | acronymed_core_product_name | quantity | unit
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, erection , testing & commissioning of Deluge valve with wet pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 3/2 way Solenoid Valve, air filter regulator etc. & manual release unit. The valve shall be electro-pneumatic type. | deluge valve |  | trim assembly: wet pilot, included: strainer, included: drain valve, included: pressure gauge, included: pressure switch, included: flame proof 3/2 way solenoid valve, included: air filter regulator, included: manual release unit, type: electro-pneumatic
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | 150 mm NB | deluge valve | size: 150 mm NB |  |  | 1.0 | Nos
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. | gate valve |  | material: cs(carbon steel), standard: API 600, class: 150, included: matching flanges, included: nuts & bolts
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | 150 mm NB | gate valve | size: 150 mm NB |  |  | 3.0 | Nos
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, installation, testing of Y- Stainer | y-stainer
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | 150 mm NB | y-stainer | size: 150 mm NB |  |  | 1.0 | Nos
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply,installation and commissioning of UL/FM approved Medium Velocity Water Spray Nozzle | medium velocity water spray nozzle |  | certification: UL(underwriters laboratories), certification: FM(factory mutual)
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | MVWS nozzle K factor 18, spray angle 100⁰ | medium velocity water spray nozzle |  | K factor: 18, spray angle: 100⁰ |  | 90.0 | Nos
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply,installation and commissioning of UL/FM approved Quartzoid Bulb Detector for K factor-80. Temp rating 68 deg C | quartzoid bulb detector |  | certification: UL(underwriters laboratories), certification: FM(factory mutual), K factor: 80, temperature rating: 68 deg C |  | 90.0 | Nos
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications | gi "c" class pipes |  | class: heavy, standard: IS 1239, fittings: threaded or grooved, included: elbow, included: tee, included: reducer, included: welding flanges, included: clamps, included: MS brackets/hangers, included: steel supports, primer: zinc chromate, paint: 2 coats red enamel, application: above ground pipes, as per fire authorities requirement
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | 150 NB | gi "c" class pipes | size: 150 NB |  |  | 12.0 | Mtr
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | 100 NB | gi "c" class pipes | size: 100 NB |  |  | 14.0 | Mtr
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | 80 NB | gi "c" class pipes | size: 80 NB |  |  | 64.0 | Mtr
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | 65 NB | gi "c" class pipes | size: 65 NB |  |  | 52.0 | Mtr
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. | ms black steel pipe |  | grade: heavy, thickness: 5.4mm, standard: IS 1239 Part-1, fittings: elbows, fittings: tees, fittings: flanges, fittings: reducers, fittings: clamps, fittings: MS support dash fasteners, paint: two coats approved primer, paint: two coats approved paint, pipe joints: grooved with groove coupling, civil work: vendor's scope
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | 150 mm NB | ms black steel pipe | size: 150 mm NB |  |  | 24.0 | Mtr
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | 25 NB | ms black steel pipe | size: 25 NB |  |  | 146.0 | Mtr
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, erction, testing & commissioning of analogue addressable Control Module | analogue addressable control module |  |  |  | 1.0 | Nos
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, erction, testing & commissioning of analogue addressable Monitor Module | analogue addressable monitor module |  |  |  | 1.0 | Nos
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable trays |  | feature: for laying all type of cables, feature: including all necessary structural supports |  | 24.0 | Mtr
N ¦ DEG & MEG TANK > N2 ¦ FOAM GENERATOR | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications a ¦ 150 NB | gi pipe | size: 150 NB | class: c class (heavy class), standard: IS 1239 (indian standard 1239), fittings: threaded or grooved, fittings: elbow, tee, reducer, welding flanges, fixing: clamps to ms brackets/hangers, supports: steel, coating: zinc chromate primer, coating: 2 coats red enamel paint, requirement: as per fire authorities, application: above ground pipes |  | 12.0 | Mtr
N ¦ DEG & MEG TANK > N2 ¦ FOAM GENERATOR | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications b ¦ 100 NB | gi pipe | size: 100 NB | class: c class (heavy class), standard: IS 1239 (indian standard 1239), fittings: threaded or grooved, fittings: elbow, tee, reducer, welding flanges, fixing: clamps to ms brackets/hangers, supports: steel, coating: zinc chromate primer, coating: 2 coats red enamel paint, requirement: as per fire authorities, application: above ground pipes |  | 42.0 | Mtr
N ¦ DEG & MEG TANK > N2 ¦ FOAM GENERATOR | Supply, erection , testing & commissioning of Deluge valve with dry pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch,dry pilot actuator, air filter regulator etc. & manual release unit. a ¦ Size 150 NB | deluge valve | size: 150 NB | trim assembly: dry pilot, fitted with: strainer, drain valve, pressure gauge, pressure switch, dry pilot actuator, air filter regulator, manual release unit |  | 1.0 | Nos
N ¦ DEG & MEG TANK > N2 ¦ FOAM GENERATOR | Providing & fixing Cast Iron Y Strainer. a ¦ Size 150 NB | y strainer | size: 150 NB | material: cast iron |  | 1.0 | Nos
N ¦ DEG & MEG TANK > N2 ¦ FOAM GENERATOR | Supply & fixing of SS-304 FOAM GENERATOR with Minimum flow 120lpm | foam generator | minimum flow: 120 lpm | material: ss-304 (stainless steel 304) |  | 2.0 | Nos
N ¦ DEG & MEG TANK > N2 ¦ FOAM GENERATOR | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. a ¦ Size 150 NB | gate valve | size: 150 NB | material: cs (carbon steel), standard: API 600, class: 150, flanges: matching, complete with: nuts & bolts |  | 3.0 | Nos
N ¦ DEG & MEG TANK > N2 ¦ FOAM GENERATOR | Supply, installation, testing and commissioning of Atmospheric Foam tank vertical type ,manufacturing as per ASME, section-VIII part- I. Tank shall be supplied along with all necessary valves, fittingss & instruments as per Technical data sheet attached with Tender documents. a ¦ Capacity of 250 ltr. | atmospheric foam tank vertical type | capacity: 250 ltr. | manufacturing standard: ASME section-VIII part-I, supplied with: all necessary valves, fittings & instruments, reference: technical data sheet attached with tender documents |  | 1.0 | Nos
N ¦ DEG & MEG TANK > N2 ¦ FOAM GENERATOR | Supply of AR-AFFF(3%) foam concentrate (PFOS/PFAS free) having sp. Gravity 1.0±.02 g/mlat 20⁰C , pH 7.0-8.5 & viscosity 1200 ±300 cps. | ar-afff foam concentrate |  | concentration: 3%, feature: PFOS/PFAS free, specific gravity: 1.0±.02 g/ml at 20⁰C, pH: 7.0-8.5, viscosity: 1200 ±300 cps | ar-afff foam concentrate | 250.0 | Ltr
N ¦ DEG & MEG TANK > N2 ¦ FOAM GENERATOR | Supply, erection, testing & commissioning of analogue addressable Monitor module | monitor module |  | feature: analogue addressable |  | 4.0 | Nos
N ¦ DEG & MEG TANK > N2 ¦ FOAM GENERATOR | Supply, erection, testing & commissioning of IR Detector | ir detector |  |  |  | 4.0 | Nos
N ¦ DEG & MEG TANK > N2 ¦ FOAM GENERATOR | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. | armoured cabling |  | feature: complete with lugs, laying and termination of both ends
N ¦ DEG & MEG TANK > N2 ¦ FOAM GENERATOR | 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cable | size: 2C x 1.5 mm2 | feature: loop cable |  | 56.0 | Mtr
N ¦ DEG & MEG TANK > N2 ¦ FOAM GENERATOR | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable trays |  | feature: for laying all type of cables as indicated above including all necessary structural supports |  | 56.0 | Mtr