## Sheet1
section_context_for_this_product_block | full_product_description | core_product_name | size | feature_or_specifications | acronymed_core_product_name | quantity | unit
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, erection, testing & commissioning of Electrical Motor driven main pump, VERTICAL TURBINE type, capable of deliver 410 M3/HR at 105 MWC. The bowl assembly shall consist of suction bell, impellers, bowl shaft and column. Column depth shall be minimum 4.5 mtr. Pump shall be coupled with TEFC motor of suitable KW with speed of 1450 RPM with all accessories. The quoted rate shall include all fixing parts necessary to couple the pump with motor. Civil foundation like mounting base etc will be client's scope. (FOR HYDRANT SYSTEM) | vertical turbine main pump | capacity: 410 M3/HR, head: 105 MWC, column depth: 4.5 mtr, speed: 1450 RPM | drive: electrical motor, coupling: TEFC motor, accessories: all fixing parts necessary to couple the pump with motor, application: hydrant system |  | R/O | Nos
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, erection, testing & commissioning of Electrical Motor driven main pump, centrifugal horizontal type, with gland packing capable of deliver 410 M3/HR at 105 MWC. The pump shall be coupled with TEFC motor of suitable KW with speed of 1450 RPM with all accessories and complete set shall mounted on common base frame. The quoted rate shall include fixing of coupling, coupling guard and foudation bolts etc. Civil foundation will be client's scope.(FOR HYDRANT SYSTEM) | centrifugal horizontal main pump | capacity: 410 M3/HR, head: 105 MWC, speed: 1450 RPM | drive: electrical motor, coupling: TEFC motor, mounting: common base frame, packing: gland packing, accessories: coupling, coupling guard, foundation bolts, application: hydrant system |  | 1 | Nos
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, erection, testing & commissioning of Electrical Motor driven main pump, VERTICAL TURBINE type, capable of deliver 410 M3/HR at 105 MWC. The bowl assembly shall consists of suction bell, impellers, bowl shaft and column. Column depth shall be minimum 4.5 mtr. Pump shall be coupled with TEFC motor of suitable KW with speed of 1450 RPM with all accessories. The quoted rate shall include all fixing parts necessary to couple the pump with motor. Civil foundation like mounting base etc will be client's scope. (FOR SPRINKLER SYSTEM) | vertical turbine main pump | capacity: 410 M3/HR, head: 105 MWC, column depth: 4.5 mtr, speed: 1450 RPM | drive: electrical motor, coupling: TEFC motor, accessories: all fixing parts necessary to couple the pump with motor, application: sprinkler system |  | R/O | Nos
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, erection, testing & commissioning of Electrical Motor driven main pump, centrifugal horizontal type, with gland packing capable of deliver 410 M3/HR at 105 MWC. The pump shall be coupled with TEFC motor of suitable KW with speed of 1450 RPM with all accessories and complete set shall mounted on common base frame. The quoted rate shall include fixing of coupling, coupling guard and foudation bolts etc. Civil foundation will be client's scope.(FOR SPRINKLER SYSTEM) | centrifugal horizontal main pump | capacity: 410 M3/HR, head: 105 MWC, speed: 1450 RPM | drive: electrical motor, coupling: TEFC motor, mounting: common base frame, packing: gland packing, accessories: coupling, coupling guard, foundation bolts, application: sprinkler system |  | 1 | Nos
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, erection, testing & commissioning of diesel engine driven standby pump, VERTICAL TURBINE type, capable of deliver 410 M3/HR at 105 MWC. The bowl assembly shall consists of suction bell, impellers, bowl shaft and column. Column depth shall be minimum 4.5 mtr. Pump shall be coupled with diesel engine of suitable HP with speed of 1500 RPM with all accessories. The quoted rate shall include all fixing parts necessary to couple the pump with engine. Civil foundation like mounting base etc will be client's scope. | vertical turbine standby pump | capacity: 410 M3/HR, head: 105 MWC, column depth: 4.5 mtr, speed: 1500 RPM | drive: diesel engine, coupling: diesel engine, accessories: all fixing parts necessary to couple the pump with engine |  | R/O | Nos
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, erection,testing & commissioning of diesel engine driven stand by pump, centrifugal horizontal type with gland packing and capable of delivering 410 M3/HR at 105 MWC. The pump shall be coupled to suitable HP of Diesel Engine radiator water cooled type having speed of 1500 RPM with all accessories including diesel engine control panel and complete set shall be mounted on common base frame.Other accessories viz Batteries & battery leads with stand, fuel tank(for 4 hrs operation) with stand and gauge glass, fuel piping with valves etc to be supplied. The quoted rate shall include radiator water cooling piping(if required), coupling guard and other standard accessories, RCC foundation(as recommended by manufacturer) and foundation bolts, etc, complete ( civil foundation shall be client's scope). | centrifugal horizontal standby pump | capacity: 410 M3/HR, head: 105 MWC, speed: 1500 RPM | drive: diesel engine, cooling: radiator water cooled, mounting: common base frame, packing: gland packing, accessories: diesel engine control panel, batteries & battery leads with stand, fuel tank(for 4 hrs operation) with stand and gauge glass, fuel piping with valves, radiator water cooling piping, coupling guard, RCC foundation, foundation bolts |  | 2 | Nos
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, erection, testing & commissioning of electric motor driven Jockey Pump,VERTICAL TURBINE type capable to deliver 25 M3/HR at 105 MWC. | vertical turbine jockey pump | capacity: 25 M3/HR, head: 105 MWC | drive: electric motor |  | R/O | Nos
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, erection, testing & commissioning of electric motor driven Jockey Pump,centrifugal horizontal type capable to deliver 25 M3/HR at 105 MWC. The pump shall coupled to TEFC motor of suitable KW with speed of 2900 RPM with all accessories mounted on common base frame. | centrifugal horizontal jockey pump | capacity: 25 M3/HR, head: 105 MWC, speed: 2900 RPM | drive: electric motor, coupling: TEFC motor, mounting: common base frame |  | 2 | Nos
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, erection, testing & commissioning of compartmentalised common control panel for above pumps as per technical specification attached with this tender document. All components shall be housed in a common cubicals made of 16 swg. M.S. sheet with required stiffners(if required). The panel shall be powder coated of approved colour both inside and out side. The panel shall have both bottom and top cable entry provisions and panel shall be mounted on pedestal of 300mm height. | compartmentalised common control panel | pedestal height: 300mm, sheet thickness: 16 swg | application: for above pumps, material: M.S.(mild steel) sheet, finish: powder coated, entry provisions: bottom and top cable entry, mounting: pedestal, construction: common cubicals, stiffners: as required |  | 1 | Nos
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, laying, testing & commissioning of FRLS, PVC outer sheath, steel armoured, aluminium / copper conductor, 1100 Volt Grade power cables with gland etc for above pumps. The cable shall be laid in tray / hume pipe / in trenches / on walls / floors etc as required. Cables laid out doors shall include the price of earth escavation providing brick and sand protection, refilling and compacting the earth. | power cables | voltage: 1100 Volt Grade | type: FRLS(fire retardant low smoke), sheath: PVC outer sheath, armouring: steel armoured, conductor: aluminium or copper, accessories: gland, laying: tray, hume pipe, trenches, walls, floors, outdoor protection: brick and sand protection, refilling, compacting |  | 1 | Lot
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | GI earthing strips of 50mm x 6mm thick, strips shall run on floor / ceiling / walls, from pump to control panel with necessary accessories as required. | gi earthing strips | strip size: 50mm x 6mm | material: GI(galvanized iron), application: from pump to control panel, accessories: as required |  | 30 | Mtr
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | 25 Sq.mm single core multistrand copper cable shall be run on floor / ceiling / walls, from the nearest earth bar to the pump control panel with necessary accessories as required. | single core multistrand copper cable | cross section: 25 Sq.mm | core: single, type: multistrand, material: copper, application: from nearest earth bar to pump control panel, accessories: as required |  | 40 | Mtr
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply and installation of pressure gauge, 1/2 inch bottom entry, of suitable range with ball valves and other accessories. | pressure gauge | bottom entry size: 1/2 inch | range: suitable, accessories: ball valves and other accessories, entry: bottom |  | 8 | Nos
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply and installation of double flanged vertical air vessel fabricated from M.S. Plate with dished ends (M.S. plate to be of required thickness to sustain the indicated test pressure), one standard pressure tight manhole, painted inside with bitumastic or anti-corrosive paint and outside with one coast of primer and two coats of synthetic enamel paint complete with approved quality of pressure switches, pressure gauge and all other required accessories to operate commonly main/sprinkler/diesel fire pump & jockey pump at drop of pressure, automatically at required pressure setting (Air vessel, pressure switch, pressure gauge, air release valve, piping and accessories to suit the pressure requirement of individual pressure zone) | vertical air vessel |  | flange-type: double flanged, orientation: vertical, material: m.s.(mild steel) plate, end-type: dished ends, plate-thickness: required thickness to sustain indicated test pressure, manhole: standard pressure tight, internal-paint: bitumastic or anti-corrosive paint, external-paint: one coat of primer and two coats of synthetic enamel paint, accessories: pressure switches, pressure gauge, air release valve, piping and accessories to suit pressure requirement of individual pressure zone, operation: automatic at required pressure setting, application: for main/sprinkler/diesel fire pump & jockey pump at drop of pressure |  | 2 | Nos
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, installation, testing & commissioning of CS Gate Valve as per API 600 with matching flanges complete with nuts & bolts. Pressure Class 150. Size 300 mm NB | gate valve | size: 300 mm NB | material: cs(carbon steel), standard: API 600, flanges: matching, accessories: nuts & bolts, pressure class: 150 |  | 1 | Nos
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, installation, testing & commissioning of CS Gate Valve as per API 600 with matching flanges complete with nuts & bolts. Pressure Class 150. Size 200 mm NB | gate valve | size: 200 mm NB | material: cs(carbon steel), standard: API 600, flanges: matching, accessories: nuts & bolts, pressure class: 150 |  | 2 | Nos
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, installation, testing & commissioning of CS Gate Valve as per API 600 with matching flanges complete with nuts & bolts. Pressure Class 150. Size 250 mm NB | gate valve | size: 250 mm NB | material: cs(carbon steel), standard: API 600, flanges: matching, accessories: nuts & bolts, pressure class: 150 |  | 4 | Nos
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, installation, testing & commissioning of CS Gate Valve as per API 600 with matching flanges complete with nuts & bolts. Pressure Class 150. Size 80 mm NB | gate valve | size: 80 mm NB | material: cs(carbon steel), standard: API 600, flanges: matching, accessories: nuts & bolts, pressure class: 150 |  | 2 | Nos
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, installation, testing and commissioning of CS Non return valve as per BS 1868 with companion flanges,nuts & bolts and gaskets. Pressure Class 150. Size 300 mm NB(Swing type) | non return valve | size: 300 mm NB | material: cs(carbon steel), standard: BS 1868, flanges: companion, accessories: nuts & bolts and gaskets, pressure class: 150, type: swing |  | 1 | Nos
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, installation, testing and commissioning of CS Non return valve as per BS 1868 with companion flanges,nuts & bolts and gaskets. Pressure Class 150. Size 250 mm NB(Swing type) | non return valve | size: 250 mm NB | material: cs(carbon steel), standard: BS 1868, flanges: companion, accessories: nuts & bolts and gaskets, pressure class: 150, type: swing |  | 4 | Nos
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, installation, testing and commissioning of CS Non return valve as per BS 1868 with companion flanges,nuts & bolts and gaskets. Pressure Class 150. Size 80 mm NB(Swing type) | non return valve | size: 80 mm NB | material: cs(carbon steel), standard: BS 1868, flanges: companion, accessories: nuts & bolts and gaskets, pressure class: 150, type: swing |  | 3 | Nos
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, installation, testing and commissioning of CS Non return valve as per BS 1868 with companion flanges,nuts & bolts and gaskets. Pressure Class 150. Size 50 mm NB(Swing type) | non return valve | size: 50 mm NB | material: cs(carbon steel), standard: BS 1868, flanges: companion, accessories: nuts & bolts and gaskets, pressure class: 150, type: swing |  | 6 | Nos
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, installation, testing and commissioning of Rubber bellow. Size 80 mm NB | rubber bellow | size: 80 mm NB |  |  | 2 | Nos
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, installation, testing and commissioning of Rubber bellow. Size 250 mm NB | rubber bellow | size: 250 mm NB |  |  | 4 | Nos
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, Installation, testing & commissioning of CS Globe Valve as per IS:9338(PN16 rating) complete including matching flanges, nuts & bolts complete. Size 150 mm NB | globe valve | size: 150 mm NB | material: cs(carbon steel), standard: IS 9338, pressure rating: PN16, flanges: matching, accessories: nuts & bolts |  | 4 | Nos
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, Installation, testing & commissioning of CS Globe Valve as per IS:9338(PN16 rating) complete including matching flanges, nuts & bolts complete. Size 80 mm NB ( PRIMING LINE) | globe valve | size: 80 mm NB | material: cs(carbon steel), standard: IS 9338, pressure rating: PN16, flanges: matching, accessories: nuts & bolts, application: priming line |  | 1 | Nos
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, Installation, testing & commissioning of CS Globe Valve as per IS:9338(PN16 rating) complete including matching flanges, nuts & bolts complete. Size 50 mm NB (PRIMING LINE) | globe valve | size: 50 mm NB | material: cs(carbon steel), standard: IS 9338, pressure rating: PN16, flanges: matching, accessories: nuts & bolts, application: priming line |  | 7 | Nos
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, installation of automatic 25 NB Air Release Valve | air release valve | size: 25 NB | operation: automatic |  | 2 | Nos
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. Size 150 mm NB | butterfly valve | size: 150 mm NB | standard: BS 5155, type: wafer, flanges: matching, accessories: nuts & bolts, fittings: necessary fittings by erection vendor |  | 2 | Nos
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 & 7 mm Heavy grade conforming to IS : 3589 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 350 mm NB x 7 mm thk | ms black steel pipe | size: 350 mm NB, thickness: 7 mm | material: ms(black steel), grade: heavy, thickness: 7 mm, standard: indian standard 3589 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved with groove coupling, civil work: all related civil work, supports etc of vendor's scope |  | 12 | Mtr
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 & 7 mm Heavy grade conforming to IS : 3589 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 300 mm NB x 7 mm thk | ms black steel pipe | size: 300 mm NB, thickness: 7 mm | material: ms(black steel), grade: heavy, thickness: 7 mm, standard: indian standard 3589 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved with groove coupling, civil work: all related civil work, supports etc of vendor's scope |  | 24 | Mtr
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 & 7 mm Heavy grade conforming to IS : 3589 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 250 mm NB x 7 mm thk | ms black steel pipe | size: 250 mm NB, thickness: 7 mm | material: ms(black steel), grade: heavy, thickness: 7 mm, standard: indian standard 3589 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved with groove coupling, civil work: all related civil work, supports etc of vendor's scope |  | 12 | Mtr
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 & 7 mm Heavy grade conforming to IS : 3589 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 200 mm NB x 7 mm thk | ms black steel pipe | size: 200 mm NB, thickness: 7 mm | material: ms(black steel), grade: heavy, thickness: 7 mm, standard: indian standard 3589 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved with groove coupling, civil work: all related civil work, supports etc of vendor's scope |  | 18 | Mtr
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 & 7 mm Heavy grade conforming to IS : 3589 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 150 mm NB | ms black steel pipe | size: 150 mm NB | material: ms(black steel), grade: heavy, thickness: 5.4 mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved with groove coupling, civil work: all related civil work, supports etc of vendor's scope |  | 12 | Mtr
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 & 7 mm Heavy grade conforming to IS : 3589 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 100 mm NB | ms black steel pipe | size: 100 mm NB | material: ms(black steel), grade: heavy, thickness: 5.4 mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved with groove coupling, civil work: all related civil work, supports etc of vendor's scope |  | 24 | Mtr
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 & 7 mm Heavy grade conforming to IS : 3589 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 80 mm NB | ms black steel pipe | size: 80 mm NB | material: ms(black steel), grade: heavy, thickness: 5.4 mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved with groove coupling, civil work: all related civil work, supports etc of vendor's scope |  | 42 | Mtr
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 & 7 mm Heavy grade conforming to IS : 3589 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 50 mm NB | ms black steel pipe | size: 50 mm NB | material: ms(black steel), grade: heavy, thickness: 5.4 mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved with groove coupling, civil work: all related civil work, supports etc of vendor's scope |  | 36 | Mtr
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 & 7 mm Heavy grade conforming to IS : 3589 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 25 mm NB | ms black steel pipe | size: 25 mm NB | material: ms(black steel), grade: heavy, thickness: 5.4 mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved with groove coupling, civil work: all related civil work, supports etc of vendor's scope |  | 24 | Mtr
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply & installation of SS 4 way collecting head with 63 mm dia instantaneous type inlet 150 dia flanged outlet with built in check valve for fire brigade connection to fire reservoir (IS : 904). | 4 way collecting head | inlet diameter: 63 mm, outlet diameter: 150 mm | material: ss(stainless steel), inlet-type: instantaneous, outlet-type: flanged, feature: built in check valve, application: fire brigade connection to fire reservoir, standard: indian standard 904 |  | 1 | Nos
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply & installation of SS Fire Brigade Draw out connection with necessary foot valve (150NB) for reservoir. | fire brigade draw out connection | size: 150 NB | material: ss(stainless steel), accessories: necessary foot valve, application: for reservoir |  | 1 | Nos
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Priming arrangement of 8000ltrs capacity for negative suction to be provided by the erection vendor including necessary tank and other structural support. Valves required are indicated elsewhere. | priming arrangement | capacity: 8000 ltrs | feature: for negative suction, vendor: erection vendor, accessories: necessary tank and other structural support, valves: required are indicated elsewhere |  | 1 | Nos
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply,Installation, testing & commisssioning of CI Foot valve with Strainer 100 mm NB | foot valve with strainer | size: 100 mm NB | material: ci(cast iron) |  | 2 | Nos
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply,Installation, testing & commisssioning of CI Foot valve with Strainer 300 mm NB | foot valve with strainer | size: 300 mm NB | material: ci(cast iron) |  | 4 | Nos
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable trays |  | material: gi(galvanized iron), application: for laying all type of cables, accessories: all necessary structural supports |  | 400 | Mtr