## Sheet1
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
G | MONOMER COLD ROOM
G1 | HIGH VELOCITY WATER SPRAY SYSTEM
1 | Supply, erection , testing & commissioning of Deluge valve with wet pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 3/2 way Solenoid Valve, air filter regulator etc. & manual release unit. The valve shall be electro-pneumatic type.
a | 80 mm NB | Nos | 1
2 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts.
a | 80 mm NB | Nos | 3
3 | Supply, installation, testing & commissioning of Y- Stainer
a | 80 mm NB | Nos | 1
4 | Supply,installation,testing and commissioning of HVWS NOZZLE with necessary threaded fittings as per drawing.
a | K26, SPRAY ANGLE=100° | Nos | 12
5 | Supply,installation and commissioning of UL/FM approved Quartzoid Bulb Detector for K factor-80. Temp rating 68 deg C | Nos | 12
6 | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications
a | 80 NB | Mtr | 9
b | 65 NB | Mtr | 6
c | 50 NB | Mtr | 6
d | 40NB | Mtr | 17
e | 25NB | Mtr | 56
7 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope.
a | 100 mm NB | Mtr | 12
b | 80 mm NB | Mtr | 12
G2 | FDA SYSTEM
1 | Supply, erection, testing & commissioning of analogue addressable ROR(Rate of Rise) type Heat Detector | Nos | 4
2 | Supply, erection, testing & commissioning of analogue addressable Manual Call point | Nos | 1
3 | Supply, erection, testing & commissioning of Hooter cum strobe | Nos | 1
4 | Supply, erction, testing & commissioning of analogue addressable Control Module | Nos | 2
5 | Supply, erection, testing & commissioning of analogue addressable Isolator Module | Nos | 1
6 | Supply, erection, testing & commissioning of analogue addressable Monitor module | Nos | 1
7 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Loop cable) | Mtr | 32
8 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Power cable) | Mtr | 12
9 | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | Mtr | 32
G3 | PA SYSTEM
1 | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | Nos | 1
2 | 6 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | Nos | 2
3 | Rack Mounted 125 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | Nos | 1
4 | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | Mtr | 18
5 | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | Nos | 1
6 | Paging Loudspeaker | Nos | 1
TOTAL