## Sheet1
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
V | RESIN TANK
V1 | FOAM GENERATOR
1 | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications
a | 150 NB | Mtr | 75
b | 100 NB | Mtr | 106
2 | Supply, erection , testing & commissioning of Deluge valve with dry pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch,dry pilot actuator, air filter regulator etc. & manual release unit.
a | Size 150 NB | Nos | 2
b | Size 100 NB | Nos | 2
3 | Providing & fixing Cast Iron Y Strainer.
a | Size 150 NB | Nos | 2
b | Size 100 NB | Nos | 2
4 | Supply & fixing of SS-304 FOAM GENERATOR with Minimum flow 120lpm | Nos | 6
5 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts.
a | Size 150 NB | Nos | 6
b | Size 100 NB | Nos | 6
6 | Supply, installation, testing and commissioning of Atmospheric Foam tank vertical type ,manufacturing as per ASME, section-VIII part- I. Tank shall be supplied along with all necessary valves, fittingss & instruments as per Technical data sheet attached with Tender documents.
a | Capacity of 250 ltr. | Nos | 2
b | Capacity of 150 ltr. | Nos | 2
7 | Supply of AR-AFFF(3%) foam concentrate (PFOS/PFAS free) having sp. Gravity 1.0±.02 g/mlat 20⁰C , pH 7.0-8.5 & viscosity 1200 ±300 cps. | Ltr | 800
8 | Supply, installation, testing and commissioning of Inline Inductor
a | 150NB | Nos | 2
b | 100 NB | Nos | 2
V2 | MEDIUM VELOCITY WATER SPRAY SYSTEM
1 | Supply, erection , testing & commissioning of Deluge valve with wet pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 3/2 way Solenoid Valve, air filter regulator etc. & manual release unit. The valve shall be electro-pneumatic type.
a | 100 NB | Mtr | 1
b | 80 NB | Mtr | 3
2 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts.
a | 100 NB | Mtr | 3
b | 80 NB | Mtr | 9
3 | Y- Strainer
a | 100 NB | Mtr | 1
b | 80 NB | Mtr | 3
4 | Supply,installation and commissioning of UL/FM approved Medium Velocity Water Spray Nozzle. UL/FM Approved.
a | MVWS nozzle K factor 18, spray angle 100⁰ | Nos | 91
5 | Supply,installation and commissioning of UL/FM approved Quartzoid Bulb Detector for K factor-80. Temp rating 68 deg C | Nos | 91
6 | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications
a | 100 NB | Mtr | 14
b | 80 NB | Mtr | 60
c | 65 NB | Mtr | 210
7 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope.
a | 100 mm NB | Mtr | 24
b | 80 mm NB | Mtr | 86
c | 25 mm NB | Mtr | 230
8 | Supply, erction, testing & commissioning of analogue addressable Control Module | Nos | 4
9 | Supply, erction, testing & commissioning of analogue addressable Monitor Module | Nos | 4
V3 | FDA SYSTEM
1 | Supply, erection, testing & commissioning of analogue addressable Monitor module | Nos | 9
2 | Supply, erection, testing & commissioning of IR Detector | Nos | 9
3 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Loop cable) | Mtr | 60
4 | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | Mtr | 62
TOTAL