## Sheet1
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
F | R & D BUILDING
F1 | HYDRANT SYSTEM
1 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be of groove with grooved coupling. All escavation, pedestal support, structural support shall be of vendor's scope.
a. | 100 mm NB | Mtr | 36
b | 80 mm NB | Mtr | 36
c | 25 mm NB | Mtr | 18
2 | Supply & installation of swinging type hose reel drum fabricated from 14 SWG CRCA sheets painted with red colour stove paint 2 coats over 1 coat of primer with 30 m long 20 mm dia rubber hose pipe with with SS self closing shut – off nozzle of 5 mm outlet fixed on wall. | Nos | 3
3 | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends
a | Size 25NB | Nos | 3
4 | Supply & installation of SS oblique type single headed Landing valve with 80 mm inlet and 63 mm outlet SS instantaneous male coupling with rubber cap and chain conforming to IS : 5290 including matching flanges, gasket, nuts and bolts complete. | Nos | 2
5 | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor.
a | Size 80 mm NB | Nos | 2
6 | Supply & installation of SS branch pipe with 20 mm nozzle conforming to IS : 903 complete | Nos | 2
7 | Supply & installation of 63 mm dia rubberized reinforced rubber line hose pipe in 15 m length conforming to IS : 636 Type II ISI marked with gunmetal male and female instantaneous coupling conforming to IS 903 wounded with 18 SWG copper wire complete | Nos | 4
8 | Supply & installation of MS Hose Box of fabricated from 16 SWG CRCA sheet double door with lockable arrangements to accommodate 2 RRL hose of 15 m length and one branch pipe painted white inside and red outside with one key. (750X600X250 mm) | Nos | 2
F2 | AUTOMATIC SPRINKLER SYSTEM
1 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope.
a | 150 mm NB | Mtr | 18
b | 100 mm NB | Mtr | 36
c | 80 mm NB | Mtr | 12
d | 65 mm NB | Mtr | 24
e | 50 mm NB | Mtr | 12
f | 40 mm NB | Mtr | 12
g | 25 mm NB | Mtr | 66
2 | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor.
a | Size150 mm NB | Nos | 2
b | Size50 mm NB | Nos | 1
3 | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts confirming to API 594.
a | Size150 mm NB | Nos | 2
b | Size50 mm NB | Nos | 1
4 | Supply & fixing of Paddle type Flow Switch | Nos | 2
5 | Supply,Fixing of Sprinkler Head Pendent type for K factor-80. Temp rating 68 deg C. UL/FM Approved. | Nos | 108
6 | Supply, installation of automatic 25 NB Air Release Valve | Nos | 1
7 | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends
a | Size 40NB | Nos | 2
b | Size 25NB | Nos | 2
8 | Supply,Erection and testing of Installation Control Valve complete with trims & gong.
a | Size 100 mm NB | Nos | 1
9 | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts.
a | Size 100 mm NB | Nos | 1
F3 | FDA SYSTEM
1 | Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | Nos | 25
2 | Supply, erection, testing & commissioning of analogue addressable Manual Call point | Nos | 4
3 | Supply, erection, testing & commissioning of Hooter cum strobe | Nos | 4
4 | Supply, erection, testing & commissioning of Telephone jack. | Nos | 2
5 | Supply, erction, testing & commissioning of analogue addressable Control Module | Nos | 2
6 | Supply, erection, testing & commissioning of analogue addressable Isolator Module | Nos | 1
7 | Supply, erection, testing & commissioning of analogue addressable Monitor module | Nos | 3
8 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Loop cable) | Mtr | 170
9 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Power cable) | Mtr | 104
10 | Providing & fixing FRLS CABLING complete with lugs, laying and termination of both ends.
a | 2C x 0.5 mm2 Armoured ( Telephone cable) | Mtr | 28
11 | Providing & fixing 200Watt Amplifier with necessary accessories. | Nos | 1
12 | Supply, erection, testing & commissioning of Repeater Panel | Nos | 1
13 | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | Mtr | 170
F4 | PA SYSTEM
1 | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | Nos | 1
2 | 6 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | Nos | 21
3 | Rack Mounted 200 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | Nos | 1
4 | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | Mtr | 164
5 | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | Nos | 1
6 | Paging Loudspeaker | Nos | 1
Total