## Sheet1
section_context_for_this_product_block | full_product_description | core_product_name | size | feature_or_specifications | acronymed_core_product_name | quantity | unit | sheet_name
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, erection, testing & commissioning of Electrical Motor driven main pump, VERTICAL TURBINE type, capable of deliver 410 M3/HR at 105 MWC. The bowl assembly shall consist of suction bell, impellers, bowl shaft and column. Column depth shall be minimum 4.5 mtr. Pump shall be coupled with TEFC motor of suitable KW with speed of 1450 RPM with all accessories. The quoted rate shall include all fixing parts necessary to couple the pump with motor. Civil foundation like mounting base etc will be client's scope. (FOR HYDRANT SYSTEM) | vertical turbine main pump | capacity: 410 M3/HR, head: 105 MWC, column depth: 4.5 mtr, speed: 1450 RPM | drive: electrical motor, coupling: TEFC motor, accessories: all fixing parts necessary to couple the pump with motor, application: hydrant system |  | R/O | Nos | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, erection, testing & commissioning of Electrical Motor driven main pump, centrifugal horizontal type, with gland packing capable of deliver 410 M3/HR at 105 MWC. The pump shall be coupled with TEFC motor of suitable KW with speed of 1450 RPM with all accessories and complete set shall mounted on common base frame. The quoted rate shall include fixing of coupling, coupling guard and foudation bolts etc. Civil foundation will be client's scope.(FOR HYDRANT SYSTEM) | centrifugal horizontal main pump | capacity: 410 M3/HR, head: 105 MWC, speed: 1450 RPM | drive: electrical motor, coupling: TEFC motor, mounting: common base frame, packing: gland packing, accessories: coupling, coupling guard, foundation bolts, application: hydrant system |  | 1 | Nos | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, erection, testing & commissioning of Electrical Motor driven main pump, VERTICAL TURBINE type, capable of deliver 410 M3/HR at 105 MWC. The bowl assembly shall consists of suction bell, impellers, bowl shaft and column. Column depth shall be minimum 4.5 mtr. Pump shall be coupled with TEFC motor of suitable KW with speed of 1450 RPM with all accessories. The quoted rate shall include all fixing parts necessary to couple the pump with motor. Civil foundation like mounting base etc will be client's scope. (FOR SPRINKLER SYSTEM) | vertical turbine main pump | capacity: 410 M3/HR, head: 105 MWC, column depth: 4.5 mtr, speed: 1450 RPM | drive: electrical motor, coupling: TEFC motor, accessories: all fixing parts necessary to couple the pump with motor, application: sprinkler system |  | R/O | Nos | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, erection, testing & commissioning of Electrical Motor driven main pump, centrifugal horizontal type, with gland packing capable of deliver 410 M3/HR at 105 MWC. The pump shall be coupled with TEFC motor of suitable KW with speed of 1450 RPM with all accessories and complete set shall mounted on common base frame. The quoted rate shall include fixing of coupling, coupling guard and foudation bolts etc. Civil foundation will be client's scope.(FOR SPRINKLER SYSTEM) | centrifugal horizontal main pump | capacity: 410 M3/HR, head: 105 MWC, speed: 1450 RPM | drive: electrical motor, coupling: TEFC motor, mounting: common base frame, packing: gland packing, accessories: coupling, coupling guard, foundation bolts, application: sprinkler system |  | 1 | Nos | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, erection, testing & commissioning of diesel engine driven standby pump, VERTICAL TURBINE type, capable of deliver 410 M3/HR at 105 MWC. The bowl assembly shall consists of suction bell, impellers, bowl shaft and column. Column depth shall be minimum 4.5 mtr. Pump shall be coupled with diesel engine of suitable HP with speed of 1500 RPM with all accessories. The quoted rate shall include all fixing parts necessary to couple the pump with engine. Civil foundation like mounting base etc will be client's scope. | vertical turbine standby pump | capacity: 410 M3/HR, head: 105 MWC, column depth: 4.5 mtr, speed: 1500 RPM | drive: diesel engine, coupling: diesel engine, accessories: all fixing parts necessary to couple the pump with engine |  | R/O | Nos | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, erection,testing & commissioning of diesel engine driven stand by pump, centrifugal horizontal type with gland packing and capable of delivering 410 M3/HR at 105 MWC. The pump shall be coupled to suitable HP of Diesel Engine radiator water cooled type having speed of 1500 RPM with all accessories including diesel engine control panel and complete set shall be mounted on common base frame.Other accessories viz Batteries & battery leads with stand, fuel tank(for 4 hrs operation) with stand and gauge glass, fuel piping with valves etc to be supplied. The quoted rate shall include radiator water cooling piping(if required), coupling guard and other standard accessories, RCC foundation(as recommended by manufacturer) and foundation bolts, etc, complete ( civil foundation shall be client's scope). | centrifugal horizontal standby pump | capacity: 410 M3/HR, head: 105 MWC, speed: 1500 RPM | drive: diesel engine, cooling: radiator water cooled, mounting: common base frame, packing: gland packing, accessories: diesel engine control panel, batteries & battery leads with stand, fuel tank(for 4 hrs operation) with stand and gauge glass, fuel piping with valves, radiator water cooling piping, coupling guard, RCC foundation, foundation bolts |  | 2 | Nos | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, erection, testing & commissioning of electric motor driven Jockey Pump,VERTICAL TURBINE type capable to deliver 25 M3/HR at 105 MWC. | vertical turbine jockey pump | capacity: 25 M3/HR, head: 105 MWC | drive: electric motor |  | R/O | Nos | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, erection, testing & commissioning of electric motor driven Jockey Pump,centrifugal horizontal type capable to deliver 25 M3/HR at 105 MWC. The pump shall coupled to TEFC motor of suitable KW with speed of 2900 RPM with all accessories mounted on common base frame. | centrifugal horizontal jockey pump | capacity: 25 M3/HR, head: 105 MWC, speed: 2900 RPM | drive: electric motor, coupling: TEFC motor, mounting: common base frame |  | 2 | Nos | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, erection, testing & commissioning of compartmentalised common control panel for above pumps as per technical specification attached with this tender document. All components shall be housed in a common cubicals made of 16 swg. M.S. sheet with required stiffners(if required). The panel shall be powder coated of approved colour both inside and out side. The panel shall have both bottom and top cable entry provisions and panel shall be mounted on pedestal of 300mm height. | compartmentalised common control panel | pedestal height: 300mm, sheet thickness: 16 swg | application: for above pumps, material: M.S.(mild steel) sheet, finish: powder coated, entry provisions: bottom and top cable entry, mounting: pedestal, construction: common cubicals, stiffners: as required |  | 1 | Nos | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, laying, testing & commissioning of FRLS, PVC outer sheath, steel armoured, aluminium / copper conductor, 1100 Volt Grade power cables with gland etc for above pumps. The cable shall be laid in tray / hume pipe / in trenches / on walls / floors etc as required. Cables laid out doors shall include the price of earth escavation providing brick and sand protection, refilling and compacting the earth. | power cables | voltage: 1100 Volt Grade | type: FRLS(fire retardant low smoke), sheath: PVC outer sheath, armouring: steel armoured, conductor: aluminium or copper, accessories: gland, laying: tray, hume pipe, trenches, walls, floors, outdoor protection: brick and sand protection, refilling, compacting |  | 1 | Lot | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | GI earthing strips of 50mm x 6mm thick, strips shall run on floor / ceiling / walls, from pump to control panel with necessary accessories as required. | gi earthing strips | strip size: 50mm x 6mm | material: GI(galvanized iron), application: from pump to control panel, accessories: as required |  | 30 | Mtr | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | 25 Sq.mm single core multistrand copper cable shall be run on floor / ceiling / walls, from the nearest earth bar to the pump control panel with necessary accessories as required. | single core multistrand copper cable | cross section: 25 Sq.mm | core: single, type: multistrand, material: copper, application: from nearest earth bar to pump control panel, accessories: as required |  | 40 | Mtr | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply and installation of pressure gauge, 1/2 inch bottom entry, of suitable range with ball valves and other accessories. | pressure gauge | bottom entry size: 1/2 inch | range: suitable, accessories: ball valves and other accessories, entry: bottom |  | 8 | Nos | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply and installation of double flanged vertical air vessel fabricated from M.S. Plate with dished ends (M.S. plate to be of required thickness to sustain the indicated test pressure), one standard pressure tight manhole, painted inside with bitumastic or anti-corrosive paint and outside with one coast of primer and two coats of synthetic enamel paint complete with approved quality of pressure switches, pressure gauge and all other required accessories to operate commonly main/sprinkler/diesel fire pump & jockey pump at drop of pressure, automatically at required pressure setting (Air vessel, pressure switch, pressure gauge, air release valve, piping and accessories to suit the pressure requirement of individual pressure zone) | vertical air vessel |  | flange-type: double flanged, orientation: vertical, material: m.s.(mild steel) plate, end-type: dished ends, plate-thickness: required thickness to sustain indicated test pressure, manhole: standard pressure tight, internal-paint: bitumastic or anti-corrosive paint, external-paint: one coat of primer and two coats of synthetic enamel paint, accessories: pressure switches, pressure gauge, air release valve, piping and accessories to suit pressure requirement of individual pressure zone, operation: automatic at required pressure setting, application: for main/sprinkler/diesel fire pump & jockey pump at drop of pressure |  | 2 | Nos | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, installation, testing & commissioning of CS Gate Valve as per API 600 with matching flanges complete with nuts & bolts. Pressure Class 150. Size 300 mm NB | gate valve | size: 300 mm NB | material: cs(carbon steel), standard: API 600, flanges: matching, accessories: nuts & bolts, pressure class: 150 |  | 1 | Nos | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, installation, testing & commissioning of CS Gate Valve as per API 600 with matching flanges complete with nuts & bolts. Pressure Class 150. Size 200 mm NB | gate valve | size: 200 mm NB | material: cs(carbon steel), standard: API 600, flanges: matching, accessories: nuts & bolts, pressure class: 150 |  | 2 | Nos | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, installation, testing & commissioning of CS Gate Valve as per API 600 with matching flanges complete with nuts & bolts. Pressure Class 150. Size 250 mm NB | gate valve | size: 250 mm NB | material: cs(carbon steel), standard: API 600, flanges: matching, accessories: nuts & bolts, pressure class: 150 |  | 4 | Nos | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, installation, testing & commissioning of CS Gate Valve as per API 600 with matching flanges complete with nuts & bolts. Pressure Class 150. Size 80 mm NB | gate valve | size: 80 mm NB | material: cs(carbon steel), standard: API 600, flanges: matching, accessories: nuts & bolts, pressure class: 150 |  | 2 | Nos | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, installation, testing and commissioning of CS Non return valve as per BS 1868 with companion flanges,nuts & bolts and gaskets. Pressure Class 150. Size 300 mm NB(Swing type) | non return valve | size: 300 mm NB | material: cs(carbon steel), standard: BS 1868, flanges: companion, accessories: nuts & bolts and gaskets, pressure class: 150, type: swing |  | 1 | Nos | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, installation, testing and commissioning of CS Non return valve as per BS 1868 with companion flanges,nuts & bolts and gaskets. Pressure Class 150. Size 250 mm NB(Swing type) | non return valve | size: 250 mm NB | material: cs(carbon steel), standard: BS 1868, flanges: companion, accessories: nuts & bolts and gaskets, pressure class: 150, type: swing |  | 4 | Nos | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, installation, testing and commissioning of CS Non return valve as per BS 1868 with companion flanges,nuts & bolts and gaskets. Pressure Class 150. Size 80 mm NB(Swing type) | non return valve | size: 80 mm NB | material: cs(carbon steel), standard: BS 1868, flanges: companion, accessories: nuts & bolts and gaskets, pressure class: 150, type: swing |  | 3 | Nos | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, installation, testing and commissioning of CS Non return valve as per BS 1868 with companion flanges,nuts & bolts and gaskets. Pressure Class 150. Size 50 mm NB(Swing type) | non return valve | size: 50 mm NB | material: cs(carbon steel), standard: BS 1868, flanges: companion, accessories: nuts & bolts and gaskets, pressure class: 150, type: swing |  | 6 | Nos | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, installation, testing and commissioning of Rubber bellow. Size 80 mm NB | rubber bellow | size: 80 mm NB |  |  | 2 | Nos | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, installation, testing and commissioning of Rubber bellow. Size 250 mm NB | rubber bellow | size: 250 mm NB |  |  | 4 | Nos | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, Installation, testing & commissioning of CS Globe Valve as per IS:9338(PN16 rating) complete including matching flanges, nuts & bolts complete. Size 150 mm NB | globe valve | size: 150 mm NB | material: cs(carbon steel), standard: IS 9338, pressure rating: PN16, flanges: matching, accessories: nuts & bolts |  | 4 | Nos | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, Installation, testing & commissioning of CS Globe Valve as per IS:9338(PN16 rating) complete including matching flanges, nuts & bolts complete. Size 80 mm NB ( PRIMING LINE) | globe valve | size: 80 mm NB | material: cs(carbon steel), standard: IS 9338, pressure rating: PN16, flanges: matching, accessories: nuts & bolts, application: priming line |  | 1 | Nos | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, Installation, testing & commissioning of CS Globe Valve as per IS:9338(PN16 rating) complete including matching flanges, nuts & bolts complete. Size 50 mm NB (PRIMING LINE) | globe valve | size: 50 mm NB | material: cs(carbon steel), standard: IS 9338, pressure rating: PN16, flanges: matching, accessories: nuts & bolts, application: priming line |  | 7 | Nos | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, installation of automatic 25 NB Air Release Valve | air release valve | size: 25 NB | operation: automatic |  | 2 | Nos | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. Size 150 mm NB | butterfly valve | size: 150 mm NB | standard: BS 5155, type: wafer, flanges: matching, accessories: nuts & bolts, fittings: necessary fittings by erection vendor |  | 2 | Nos | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 & 7 mm Heavy grade conforming to IS : 3589 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 350 mm NB x 7 mm thk | ms black steel pipe | size: 350 mm NB, thickness: 7 mm | material: ms(black steel), grade: heavy, thickness: 7 mm, standard: indian standard 3589 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved with groove coupling, civil work: all related civil work, supports etc of vendor's scope |  | 12 | Mtr | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 & 7 mm Heavy grade conforming to IS : 3589 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 300 mm NB x 7 mm thk | ms black steel pipe | size: 300 mm NB, thickness: 7 mm | material: ms(black steel), grade: heavy, thickness: 7 mm, standard: indian standard 3589 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved with groove coupling, civil work: all related civil work, supports etc of vendor's scope |  | 24 | Mtr | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 & 7 mm Heavy grade conforming to IS : 3589 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 250 mm NB x 7 mm thk | ms black steel pipe | size: 250 mm NB, thickness: 7 mm | material: ms(black steel), grade: heavy, thickness: 7 mm, standard: indian standard 3589 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved with groove coupling, civil work: all related civil work, supports etc of vendor's scope |  | 12 | Mtr | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 & 7 mm Heavy grade conforming to IS : 3589 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 200 mm NB x 7 mm thk | ms black steel pipe | size: 200 mm NB, thickness: 7 mm | material: ms(black steel), grade: heavy, thickness: 7 mm, standard: indian standard 3589 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved with groove coupling, civil work: all related civil work, supports etc of vendor's scope |  | 18 | Mtr | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 & 7 mm Heavy grade conforming to IS : 3589 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 150 mm NB | ms black steel pipe | size: 150 mm NB | material: ms(black steel), grade: heavy, thickness: 5.4 mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved with groove coupling, civil work: all related civil work, supports etc of vendor's scope |  | 12 | Mtr | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 & 7 mm Heavy grade conforming to IS : 3589 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 100 mm NB | ms black steel pipe | size: 100 mm NB | material: ms(black steel), grade: heavy, thickness: 5.4 mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved with groove coupling, civil work: all related civil work, supports etc of vendor's scope |  | 24 | Mtr | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 & 7 mm Heavy grade conforming to IS : 3589 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 80 mm NB | ms black steel pipe | size: 80 mm NB | material: ms(black steel), grade: heavy, thickness: 5.4 mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved with groove coupling, civil work: all related civil work, supports etc of vendor's scope |  | 42 | Mtr | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 & 7 mm Heavy grade conforming to IS : 3589 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 50 mm NB | ms black steel pipe | size: 50 mm NB | material: ms(black steel), grade: heavy, thickness: 5.4 mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved with groove coupling, civil work: all related civil work, supports etc of vendor's scope |  | 36 | Mtr | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 & 7 mm Heavy grade conforming to IS : 3589 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 25 mm NB | ms black steel pipe | size: 25 mm NB | material: ms(black steel), grade: heavy, thickness: 5.4 mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved with groove coupling, civil work: all related civil work, supports etc of vendor's scope |  | 24 | Mtr | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply & installation of SS 4 way collecting head with 63 mm dia instantaneous type inlet 150 dia flanged outlet with built in check valve for fire brigade connection to fire reservoir (IS : 904). | 4 way collecting head | inlet diameter: 63 mm, outlet diameter: 150 mm | material: ss(stainless steel), inlet-type: instantaneous, outlet-type: flanged, feature: built in check valve, application: fire brigade connection to fire reservoir, standard: indian standard 904 |  | 1 | Nos | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply & installation of SS Fire Brigade Draw out connection with necessary foot valve (150NB) for reservoir. | fire brigade draw out connection | size: 150 NB | material: ss(stainless steel), accessories: necessary foot valve, application: for reservoir |  | 1 | Nos | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Priming arrangement of 8000ltrs capacity for negative suction to be provided by the erection vendor including necessary tank and other structural support. Valves required are indicated elsewhere. | priming arrangement | capacity: 8000 ltrs | feature: for negative suction, vendor: erection vendor, accessories: necessary tank and other structural support, valves: required are indicated elsewhere |  | 1 | Nos | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply,Installation, testing & commisssioning of CI Foot valve with Strainer 100 mm NB | foot valve with strainer | size: 100 mm NB | material: ci(cast iron) |  | 2 | Nos | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply,Installation, testing & commisssioning of CI Foot valve with Strainer 300 mm NB | foot valve with strainer | size: 300 mm NB | material: ci(cast iron) |  | 4 | Nos | FIRE PUMP ROOM
['A.', 'FIRE PUMP ROOM', 'FIRE WATER PUMPING SYSTEM'] | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable trays |  | material: gi(galvanized iron), application: for laying all type of cables, accessories: all necessary structural supports |  | 400 | Mtr | FIRE PUMP ROOM
B. ¦ EXTERNAL HYDRANT, SPRINKLER LINE & FDA | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cabling | core: 2C, cross section: 1.5 mm2 | feature: complete with lugs, laying and termination of both ends, type: loop cable |  | 1820 | Mtr | EXTERNAL HYDRANT,SPRINKLER LINE
B. ¦ EXTERNAL HYDRANT, SPRINKLER LINE & FDA | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Power cable) | armoured cabling | core: 2C, cross section: 1.5 mm2 | feature: complete with lugs, laying and termination of both ends, type: power cable |  | 1320 | Mtr | EXTERNAL HYDRANT,SPRINKLER LINE
B. ¦ EXTERNAL HYDRANT, SPRINKLER LINE & FDA | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 0.5 mm2 Armoured ( Telephone cable) | armoured cabling | core: 2C, cross section: 0.5 mm2 | feature: complete with lugs, laying and termination of both ends, type: telephone cable |  | 1200 | Mtr | EXTERNAL HYDRANT,SPRINKLER LINE
B. ¦ EXTERNAL HYDRANT, SPRINKLER LINE & FDA | Supply, erection, fabrication, testing of MS black steel pipe of 7 mm Heavy grade conforming to IS : 3589 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipes shall be erected with grooved joints only. All sorts of escavation, pedestal support and structural support shall be of vendor's scope. 200 NB(FOR REVAMPING OF HYDRANT LINE) | ms black steel pipe | diameter: 200 NB, thickness: 7 mm | material: ms(mild steel), finish: black, grade: heavy, standard: indian standard 3589 part-1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved, feature: all sorts of excavation, pedestal support and structural support of vendor's scope, application: revamping of hydrant line |  | 250 | Mtr | EXTERNAL HYDRANT,SPRINKLER LINE
B. ¦ EXTERNAL HYDRANT, SPRINKLER LINE & FDA | Supply, erection, fabrication, testing of MS black steel pipe of 7 mm Heavy grade conforming to IS : 3589 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipes shall be erected with grooved joints only. All sorts of escavation, pedestal support and structural support shall be of vendor's scope. 200 NB(FOR EXTERNAL SPRINKLER LINE) | ms black steel pipe | diameter: 200 NB, thickness: 7 mm | material: ms(mild steel), finish: black, grade: heavy, standard: indian standard 3589 part-1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved, feature: all sorts of excavation, pedestal support and structural support of vendor's scope, application: external sprinkler line |  | 1040 | Mtr | EXTERNAL HYDRANT,SPRINKLER LINE
B. ¦ EXTERNAL HYDRANT, SPRINKLER LINE & FDA | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, Class 150, with matching flanges complete with nuts & bolts. (IN SPRINKLER LINE) 200 mm NB | gate valve | diameter: 200 mm NB | material: cs(carbon steel), standard: api 600, class: 150, fittings: matching flanges, nuts & bolts, application: in sprinkler line |  | 3 | Nos | EXTERNAL HYDRANT,SPRINKLER LINE
B. ¦ EXTERNAL HYDRANT, SPRINKLER LINE & FDA | Supply, fabrication and erection of MS Structural material for various kind of supports consistes of angle, channels, I sections, plates etc including nuts, bolts and washers. | ms structural material |  | material: ms(mild steel), components: angle, channels, I sections, plates, nuts, bolts, washers, application: supports |  | 35000 | kg | EXTERNAL HYDRANT,SPRINKLER LINE
B. ¦ EXTERNAL HYDRANT, SPRINKLER LINE & FDA | Supply, erection, testing & commissioning of analogue addressable outdoor type Manual Call point explosion proof complete with fittings and accessories. | manual call point |  | type: analogue addressable, installation: outdoor, feature: explosion proof, fittings: complete with fittings and accessories |  | 52 | Nos | EXTERNAL HYDRANT,SPRINKLER LINE
B. ¦ EXTERNAL HYDRANT, SPRINKLER LINE & FDA | Supply, erection, testing & commissioning of External Hooter cum strobe(IP 67 rating) complete with fittings and accessories. | external hooter cum strobe |  | rating: IP 67, fittings: complete with fittings and accessories |  | 52 | Nos | EXTERNAL HYDRANT,SPRINKLER LINE
B. ¦ EXTERNAL HYDRANT, SPRINKLER LINE & FDA | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable trays |  | material: gi(galvanized iron), application: laying all type of cables, feature: including all necessary structural supports |  | 1820 | Mtr | EXTERNAL HYDRANT,SPRINKLER LINE
B. ¦ EXTERNAL HYDRANT, SPRINKLER LINE & FDA | Supply & installation of portable foam tank of 250 ltr. | portable foam tank | tank capacity: 250 ltr |  |  | R/O | Nos | EXTERNAL HYDRANT,SPRINKLER LINE
B. ¦ EXTERNAL HYDRANT, SPRINKLER LINE & FDA | Supply & installation of FOAM WATER MONITOR 65NB water passage with 32nb Nozzle bore having 1750 lpm flow and 360 degree rotation with compaitable accessories. | foam water monitor | water passage: 65NB, nozzle bore: 32nb, flow: 1750 lpm | feature: 360 degree rotation, accessories: compatible accessories |  | R/O | Nos | EXTERNAL HYDRANT,SPRINKLER LINE
B. ¦ EXTERNAL HYDRANT, SPRINKLER LINE & FDA | Supply, erection, testing & commissioning of Air Compressor with motor,mounted on a common base frame with air receiver tank. The set shall be fitted with dry suction filter, diaphragm,automatic venting device, safety valve, pressure gauge cooler, motor starter etc. The compressor shall be of capacity 25 M³/Hr( FAD), discharge pressure 10 bar, single stage, reciprocating type | air compressor | capacity: 25 M³/Hr (FAD), discharge pressure: 10 bar | mounting: common base frame with air receiver tank, accessories: dry suction filter, diaphragm, automatic venting device, safety valve, pressure gauge cooler, motor starter, type: single stage, reciprocating |  | 2 | Nos | EXTERNAL HYDRANT,SPRINKLER LINE
B. ¦ EXTERNAL HYDRANT, SPRINKLER LINE & FDA | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 50 NB | gi pipe | diameter: 50 NB | class: C Class (Heavy Class), standard: IS 1239, fittings: threaded or grooved, accessories: elbow, tee, reducer, welding flanges, clamps to MS brackets/hangers, steel supports, coating: zinc chromate primer, finish: 2 coats red enamel paint, requirement: as per Fire authorities, application: above ground pipes |  | 1800 | Mtr | EXTERNAL HYDRANT,SPRINKLER LINE
B. ¦ PA SYSTEM | Main IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | ip based networkable touch screen paging station |  | feature: selection of zones, supervision of system status, scheduled broadcasts, central exchange with standby CPU, built-in monitoring loudspeaker, goose-neck microphone, LCD touchscreen display, audio input |  | 2 | Nos | EXTERNAL HYDRANT,SPRINKLER LINE
B. ¦ PA SYSTEM | High Efficiency SIREN with weather protection IP 21C (Weatherproof Type, Suitable for Outdoor Area), 3km range. | siren | range: 3km | efficiency: high, weather protection: IP 21C, type: weatherproof, application: suitable for outdoor area |  | 2 | Nos | EXTERNAL HYDRANT,SPRINKLER LINE
B. ¦ PA SYSTEM | Supply, erection, testing & commissioning of 3 tone controller for high frequency siren. | 3 tone controller |  | application: high frequency siren |  | 1 | Nos | EXTERNAL HYDRANT,SPRINKLER LINE
B. ¦ PA SYSTEM | Rack Mounted 125 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | power amplifier | power: 125 watt | mounting: rack mounted, backup: battery backup, wattage: as per requirement |  | 1 | Nos | EXTERNAL HYDRANT,SPRINKLER LINE
B. ¦ PA SYSTEM | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | xlpe cu cable | core: 2C, cross section: 1.5 mm2 | construction: multi stranded, shielded, armoured, application: power & signal |  | 2 | Mtr | EXTERNAL HYDRANT,SPRINKLER LINE
B. ¦ PA SYSTEM | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | dvd player |  | feature: hook up to amplifiers of PA system, application: music in common areas |  | 2 | Nos | EXTERNAL HYDRANT,SPRINKLER LINE
B. ¦ PA SYSTEM | Paging Loudspeaker | paging loudspeaker |  |  |  | 2 | Nos | EXTERNAL HYDRANT,SPRINKLER LINE
B. ¦ PA SYSTEM | Optical Fibre Cable (Armoured) with all accessories. | optical fibre cable |  | construction: armoured, accessories: all accessories |  | 1700 | Nos | EXTERNAL HYDRANT,SPRINKLER LINE
C ¦ RESIN PLANT, RISHRA; C1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Groove joints to be done for erection of pipes with proper couplings and fasteners. All escavations, pedestal supports, structural supports shall be of vendor's scope. 150 mm NB | ms black steel pipe | size: 150 mm NB | grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint: groove joints with proper couplings and fasteners, scope: all escavations, pedestal supports, structural supports of vendor's scope |  | 12 | Mtr | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Groove joints to be done for erection of pipes with proper couplings and fasteners. All escavations, pedestal supports, structural supports shall be of vendor's scope. 80 mm NB | ms black steel pipe | size: 80 mm NB | grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint: groove joints with proper couplings and fasteners, scope: all escavations, pedestal supports, structural supports of vendor's scope |  | 6 | Mtr | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Groove joints to be done for erection of pipes with proper couplings and fasteners. All escavations, pedestal supports, structural supports shall be of vendor's scope. 25 mm NB | ms black steel pipe | size: 25 mm NB | grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint: groove joints with proper couplings and fasteners, scope: all escavations, pedestal supports, structural supports of vendor's scope |  | 6 | Mtr | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C1 ¦ HYDRANT SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, Class 150 with matching flanges, bolts, nuts and gaskets. Size 150 mm NB | gate valve | size: 150 mm NB | material: cs(carbon steel), standard: api 600, class: 150, accessories: matching flanges, bolts, nuts and gaskets |  | 1 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C1 ¦ HYDRANT SYSTEM | Supply, installation, testing and commissioning of CS Non return valve as per BS 1868, Class 150, with companion flanges,nuts & bolts and gaskets. Size 150 mm NB | non return valve | size: 150 mm NB | material: cs(carbon steel), standard: bs 1868, class: 150, accessories: companion flanges, nuts & bolts and gaskets |  | 1 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C1 ¦ HYDRANT SYSTEM | Supply & installation of SS oblique type single headed Landing valve with 80 mm inlet and 63 mm outlet SS instantaneous male coupling with rubber cap and chain conforming to IS : 5290 including matching flanges, gasket, nuts and bolts complete. | landing valve | inlet: 80 mm, outlet: 63 mm | material: ss(stainless steel), type: oblique, head: single headed, coupling: ss(stainless steel) instantaneous male, accessories: rubber cap and chain, standard: indian standard 5290, accessories: matching flanges, gasket, nuts and bolts |  | 3 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C1 ¦ HYDRANT SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. Size 80 mm NB | butterfly valve | size: 80 mm NB | standard: bs 5155, type: wafer type, accessories: matching flanges, nuts & bolts, fittings: necessary fittings by erection vendor |  | 3 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C1 ¦ HYDRANT SYSTEM | Supply & installation of SS branch pipe with 20 mm nozzle conforming to IS : 903 complete | branch pipe | nozzle: 20 mm | material: ss(stainless steel), standard: indian standard 903 |  | 3 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C1 ¦ HYDRANT SYSTEM | Supply & installation of 63 mm dia rubberized reinforced rubber line hose pipe in 15 m length conforming to IS : 636 Type II ISI marked with gunmetal male and female instantaneous coupling conforming to IS 903 wounded with 18 SWG copper wire complete | hose pipe | diameter: 63 mm, length: 15 m | type: rubberized reinforced rubber line, standard: indian standard 636 type ii, certification: isi marked, coupling: gunmetal male and female instantaneous, coupling standard: indian standard 903, wire: 18 swg copper wire |  | 6 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C1 ¦ HYDRANT SYSTEM | Supply & installation of MS Hose Box of fabricated from 16 SWG CRCA sheet double door with lockable arrangements to accommodate 2 RRL hose of 15 m length and one branch pipe painted white inside and red outside with one key. (750X600X250 mm) | hose box | dimensions: 750X600X250 mm | material: ms(mild steel), fabrication: 16 swg crca sheet, door: double door with lockable arrangements, capacity: accommodate 2 rrl hose of 15 m length and one branch pipe, painting: white inside and red outside, accessories: one key |  | 3 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C1 ¦ HYDRANT SYSTEM | Supply & installation of swinging type hose reel drum fabricated from 14 SWG CRCA sheets painted with red colour stove paint 2 coats over 1 coat of primer with 30 m long 20 mm dia rubber hose pipe with with SS self closing shut – off nozzle of 5 mm outlet fixed on wall. | hose reel drum | hose length: 30 m, hose diameter: 20 mm, nozzle outlet: 5 mm | type: swinging, fabrication: 14 swg crca sheets, painting: red colour stove paint 2 coats over 1 coat of primer, hose: rubber, nozzle: ss(stainless steel) self closing shut-off, installation: fixed on wall |  | 3 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C1 ¦ HYDRANT SYSTEM | Supply and installation of pressure gauge, 1/2 inch bottom entry, of suitable range with ball valves and other accessories. | pressure gauge | bottom entry: 1/2 inch | range: suitable range, accessories: ball valves and other accessories |  | 1 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C1 ¦ HYDRANT SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends, Size 25NB | globe valve | size: 25NB | material: bronze, standard: indian standard 778, end-connection: screwed |  | 5 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C1 ¦ HYDRANT SYSTEM | Supply & installation of 250ltr portable foam tank filled with 3% ARFFF foam concentrate with foam making branch and pick up tube. | portable foam tank | tank capacity: 250ltr | foam concentrate: 3% ARFFF(aqueous film forming foam), feature: foam making branch and pick up tube |  | 1 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection , testing & commissioning of Deluge valve, with dry pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 2 way Solenoid Valve, and other accessories etc. & manual release unit., 150 mm NB | deluge valve | size: 150 mm NB | feature: dry pilot trim assembly, feature: fitted with strainer, feature: drain valve, feature: pressure gauge, feature: pressure switch, feature: flame proof 2 way solenoid valve, feature: manual release unit |  | 1 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection , testing & commissioning of Deluge valve, with dry pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 2 way Solenoid Valve, and other accessories etc. & manual release unit., 80 mm NB | deluge valve | size: 80 mm NB | feature: dry pilot trim assembly, feature: fitted with strainer, feature: drain valve, feature: pressure gauge, feature: pressure switch, feature: flame proof 2 way solenoid valve, feature: manual release unit |  | 2 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, Class 150 with matching flanges complete with nuts, bolts and gaskets., 150 mm NB | gate valve | size: 150 mm NB | material: cs(carbon steel), standard: API 600, pressure class: 150, end-connection: matching flanges, accessories: nuts, bolts and gaskets |  | 3 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, Class 150 with matching flanges complete with nuts, bolts and gaskets., 80 mm NB | gate valve | size: 80 mm NB | material: cs(carbon steel), standard: API 600, pressure class: 150, end-connection: matching flanges, accessories: nuts, bolts and gaskets |  | 6 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing and commissioning of Y-Strainer., Size 150 mm NB | y-strainer | size: 150 mm NB |  |  | 1 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing and commissioning of Y-Strainer., Size 80 mm NB | y-strainer | size: 80 mm NB |  |  | 2 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply,installation,testing and commissioning of Foam Sprinkler nozzle with necessary threaded fittings as per drawing. The sprinkler shall be Open Aspiration, Pendent type, K-42 with standard spray angle.End connection 1/2" NPT/BSP.UL/FM Approved., Spray nozzle K factor -42 | foam sprinkler nozzle | k factor: 42 | feature: open aspiration, type: pendent, spray angle: standard, end-connection: 1/2" NPT/BSP, certification: UL(underwriters laboratories), certification: FM(factory mutual) |  | 123 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply,installation and commissioning of UL/FM approved Quartzoid Bulb Detector for K factor-80. Temp rating 68 deg C. | quartzoid bulb detector | k factor: 80 | certification: UL(underwriters laboratories), certification: FM(factory mutual), temperature rating: 68 deg C |  | 123 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing and commissioning of Ratio Controller., 150NB | ratio controller | size: 150NB |  |  | 1 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing and commissioning of Ratio Controller., 80NB | ratio controller | size: 80NB |  |  | 2 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing and commissioning of Foam bladder tank vertical type ,manufacturing as per ASME, section-VIII part- I. The bladder material shall be BUNA-N. The Bladder Tank shall be supplied along with all necessary valves, Hydraulically Operated Foam Concentrae Control Valve ,fittingss & instruments as per Technical data sheet attached with Tender documents. Capacity of 2100 ltr. | foam bladder tank | capacity: 2100 ltr. | type: vertical, manufacturing standard: ASME(american society of mechanical engineers) section-VIII part-I, bladder material: BUNA-N, accessories: all necessary valves, accessories: hydraulically operated foam concentrate control valve, accessories: fittings & instruments, reference: technical data sheet attached with tender documents |  | 1 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply of AR-AFFF(3%) foam concentrate(PFOS/PFAS free) having sp. Gravity 1.0±.02 g/mlat 20⁰C , PH 7.0-8.5 & viscosity 1200 ±300 cps. | foam concentrate |  | type: AR-AFFF(3%), feature: PFOS/PFAS free, specific gravity: 1.0±.02 g/ml at 20⁰C, PH: 7.0-8.5, viscosity: 1200 ±300 cps |  | 2100 | Ltr | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 150 NB | gi c class pipe | size: 150 NB | class: C (heavy class), material: GI(galvanized iron), standard: IS 1239(indian standard 1239), fittings: threaded or grooved, accessories: elbows, accessories: tees, accessories: reducers, accessories: welding flanges, accessories: clamps, accessories: MS(mild steel) brackets/hangers, accessories: steel supports, coating: zinc chromate primer, coating: 2 coats red enamel paint, reference: as per fire authorities requirement, location: above ground pipes, reference: as per specifications |  | 32 | Mtr | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 100 NB | gi c class pipe | size: 100 NB | class: C (heavy class), material: GI(galvanized iron), standard: IS 1239(indian standard 1239), fittings: threaded or grooved, accessories: elbows, accessories: tees, accessories: reducers, accessories: welding flanges, accessories: clamps, accessories: MS(mild steel) brackets/hangers, accessories: steel supports, coating: zinc chromate primer, coating: 2 coats red enamel paint, reference: as per fire authorities requirement, location: above ground pipes, reference: as per specifications |  | 16 | Mtr | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 80 NB | gi c class pipe | size: 80 NB | class: C (heavy class), material: GI(galvanized iron), standard: IS 1239(indian standard 1239), fittings: threaded or grooved, accessories: elbows, accessories: tees, accessories: reducers, accessories: welding flanges, accessories: clamps, accessories: MS(mild steel) brackets/hangers, accessories: steel supports, coating: zinc chromate primer, coating: 2 coats red enamel paint, reference: as per fire authorities requirement, location: above ground pipes, reference: as per specifications |  | 92 | Mtr | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 65 NB | gi c class pipe | size: 65 NB | class: C (heavy class), material: GI(galvanized iron), standard: IS 1239(indian standard 1239), fittings: threaded or grooved, accessories: elbows, accessories: tees, accessories: reducers, accessories: welding flanges, accessories: clamps, accessories: MS(mild steel) brackets/hangers, accessories: steel supports, coating: zinc chromate primer, coating: 2 coats red enamel paint, reference: as per fire authorities requirement, location: above ground pipes, reference: as per specifications |  | 36 | Mtr | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 50 NB | gi c class pipe | size: 50 NB | class: C (heavy class), material: GI(galvanized iron), standard: IS 1239(indian standard 1239), fittings: threaded or grooved, accessories: elbows, accessories: tees, accessories: reducers, accessories: welding flanges, accessories: clamps, accessories: MS(mild steel) brackets/hangers, accessories: steel supports, coating: zinc chromate primer, coating: 2 coats red enamel paint, reference: as per fire authorities requirement, location: above ground pipes, reference: as per specifications |  | 46 | Mtr | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 40NB | gi c class pipe | size: 40 NB | class: C (heavy class), material: GI(galvanized iron), standard: IS 1239(indian standard 1239), fittings: threaded or grooved, accessories: elbows, accessories: tees, accessories: reducers, accessories: welding flanges, accessories: clamps, accessories: MS(mild steel) brackets/hangers, accessories: steel supports, coating: zinc chromate primer, coating: 2 coats red enamel paint, reference: as per fire authorities requirement, location: above ground pipes, reference: as per specifications |  | 129 | Mtr | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 25NB | gi c class pipe | size: 25 NB | class: C (heavy class), material: GI(galvanized iron), standard: IS 1239(indian standard 1239), fittings: threaded or grooved, accessories: elbows, accessories: tees, accessories: reducers, accessories: welding flanges, accessories: clamps, accessories: MS(mild steel) brackets/hangers, accessories: steel supports, coating: zinc chromate primer, coating: 2 coats red enamel paint, reference: as per fire authorities requirement, location: above ground pipes, reference: as per specifications |  | 952 | Mtr | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved red oxide primer and two coats of approved red enamel paint. Pipe joints shall be with grooved coupling. All escavation, pedestal supports, structural supports shall be of vendor's scope. 150 mm NB | ms black steel pipe | size: 150 mm NB, thickness: 5.4mm | material: MS(mild steel) black steel, grade: heavy, standard: IS 1239(indian standard 1239) part-1, fittings: elbows, fittings: tees, fittings: flanges, fittings: reducers, fittings: clamps, fittings: MS(mild steel) support dash fasteners, coating: two coats approved red oxide primer, coating: two coats approved red enamel paint, joint type: grooved coupling, scope: all excavation, pedestal supports, structural supports by vendor |  | 18 | Mtr | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved red oxide primer and two coats of approved red enamel paint. Pipe joints shall be with grooved coupling. All escavation, pedestal supports, structural supports shall be of vendor's scope. 100 mm NB | ms black steel pipe | size: 100 mm NB, thickness: 5.4mm | material: MS(mild steel) black steel, grade: heavy, standard: IS 1239(indian standard 1239) part-1, fittings: elbows, fittings: tees, fittings: flanges, fittings: reducers, fittings: clamps, fittings: MS(mild steel) support dash fasteners, coating: two coats approved red oxide primer, coating: two coats approved red enamel paint, joint type: grooved coupling, scope: all excavation, pedestal supports, structural supports by vendor |  | 12 | Mtr | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved red oxide primer and two coats of approved red enamel paint. Pipe joints shall be with grooved coupling. All escavation, pedestal supports, structural supports shall be of vendor's scope. 80 mm NB | ms black steel pipe | size: 80 mm NB, thickness: 5.4mm | material: MS(mild steel) black steel, grade: heavy, standard: IS 1239(indian standard 1239) part-1, fittings: elbows, fittings: tees, fittings: flanges, fittings: reducers, fittings: clamps, fittings: MS(mild steel) support dash fasteners, coating: two coats approved red oxide primer, coating: two coats approved red enamel paint, joint type: grooved coupling, scope: all excavation, pedestal supports, structural supports by vendor |  | 12 | Mtr | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing & commissioning of Air Buffer tank complete with necessary components. The compressor shall be of capacity 15 M³/Hr( FAD), discharge pressure 10 bar, single stage, reciprocating type. | air buffer tank | compressor capacity: 15 M³/Hr (FAD), discharge pressure: 10 bar | feature: complete with necessary components, compressor type: single stage, compressor type: reciprocating |  | 1 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C3 ¦ AUTOMATIC SPRINKLER SYSTEM | a ¦ Size 80 mm NB |  | size: 80 mm NB |  |  | 1 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C3 ¦ AUTOMATIC SPRINKLER SYSTEM | b ¦ Size 50 mm NB |  | size: 50 mm NB |  |  | 1 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C3 ¦ AUTOMATIC SPRINKLER SYSTEM | 3 ¦ Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts confirming to API 594. a ¦ Size 80 mm NB | non return valve | size: 80 mm NB | type: wafer, flanges: matching, fasteners: nuts & bolts, standard: API 594(american petroleum institute 594) |  | 1 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C3 ¦ AUTOMATIC SPRINKLER SYSTEM | 3 ¦ Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts confirming to API 594. b ¦ Size 50 mm NB | non return valve | size: 50 mm NB | type: wafer, flanges: matching, fasteners: nuts & bolts, standard: API 594(american petroleum institute 594) |  | 1 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C3 ¦ AUTOMATIC SPRINKLER SYSTEM | 4 ¦ Supply & fixing of Paddle type Flow Switch | paddle type flow switch |  |  |  | 2 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C3 ¦ AUTOMATIC SPRINKLER SYSTEM | 5 ¦ Supply,Fixing of Sprinkler Head Pendent type for K factor-80. Temp rating 68 deg C.UL/FM Approved. | sprinkler head pendent type | K factor: 80 | temperature rating: 68 deg C, certification: UL(underwriters laboratories), certification: FM(factory mutual) |  | 37 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C3 ¦ AUTOMATIC SPRINKLER SYSTEM | 6 ¦ Supply, installation of automatic 25 NB Air Release Valve | air release valve | size: 25 NB | feature: automatic |  | 1 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C3 ¦ AUTOMATIC SPRINKLER SYSTEM | 7 ¦ Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends a ¦ Size 25NB | globe valve | size: 25 NB | material: bronze, standard: IS 778(indian standard 778), ends: screwed |  | 5 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C3 ¦ AUTOMATIC SPRINKLER SYSTEM | 7 ¦ Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends b ¦ Size 40NB | globe valve | size: 40 NB | material: bronze, standard: IS 778(indian standard 778), ends: screwed |  | 2 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C3 ¦ AUTOMATIC SPRINKLER SYSTEM | 8 ¦ Supply,Erection and testing of Installation Control Valve complete with trims & gong. a ¦ Size 80 mm NB | installation control valve | size: 80 mm NB | feature: complete with trims & gong |  | 1 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C3 ¦ AUTOMATIC SPRINKLER SYSTEM | 9 ¦ Supply, installation, testing & commissioning of CS Gate Valve as per API 600 with matching flanges complete with nuts,bolts and gaskets. a ¦ Size 80 NB | gate valve | size: 80 NB | material: CS(carbon steel), standard: API 600(american petroleum institute 600), flanges: matching, fasteners: nuts & bolts, gaskets: complete |  | 1 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C4 ¦ FDA SYSTEM | 1 ¦ Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | multicriteria detector |  | type: analogue addressable |  | 9 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C4 ¦ FDA SYSTEM | 2 ¦ Supply, erection, testing & commissioning of analogue addressable Heat Detector | heat detector |  | type: analogue addressable |  | 2 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C4 ¦ FDA SYSTEM | 3 ¦ Supply, erection, testing & commissioning of IR Detector | ir detector |  |  |  | 8 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C4 ¦ FDA SYSTEM | 4 ¦ Supply, erection, testing & commissioning of analogue addressable explosion proof Manual Call point | manual call point |  | type: analogue addressable, feature: explosion proof |  | 6 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C4 ¦ FDA SYSTEM | 5 ¦ Supply, erection, testing & commissioning of explosion proo Hooter cum strobe | hooter cum strobe |  | feature: explosion proof |  | 10 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C4 ¦ FDA SYSTEM | 6 ¦ Supply, erction, testing & commissioning of analogue addressable Control Module | control module |  | type: analogue addressable |  | 8 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C4 ¦ FDA SYSTEM | 7 ¦ Supply, erection, testing & commissioning of analogue addressable Isolator Module | isolator module |  | type: analogue addressable |  | 3 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C4 ¦ FDA SYSTEM | 8 ¦ Supply, erection, testing & commissioning of analogue addressable Monitor module | monitor module |  | type: analogue addressable |  | 12 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C4 ¦ FDA SYSTEM | 9a ¦ Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cabling | cable: 2C x 1.5 mm2 | feature: complete with lugs, laying and termination of both ends, type: loop cable |  | 389 | Mtr | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C4 ¦ FDA SYSTEM | 10a ¦ Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Power cable) | armoured cabling | cable: 2C x 1.5 mm2 | feature: complete with lugs, laying and termination of both ends, type: power cable |  | 297 | Mtr | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C4 ¦ FDA SYSTEM | 11 ¦ Supply, erection, fabrication, testing and commission of VOC detector with range of 1 – 1000 ppm isobutylene equivalent.and following accessoriesa) DigiPID internal dust filter (Pack of 5) b) Waterproof Filter Assy, RAEGuard2 PID, Pack of 5 c) DigiPID Teflon UV electrode shield pack of 10 d) DigiPID Dust Cover e) Air Drying Pre Filter Kit f) DigiPID external water trap filter (Pack of 5) | voc detector | range: 1 – 1000 ppm isobutylene equivalent | accessories: DigiPID internal dust filter (Pack of 5), Waterproof Filter Assy, RAEGuard2 PID, Pack of 5, DigiPID Teflon UV electrode shield pack of 10, DigiPID Dust Cover, Air Drying Pre Filter Kit, DigiPID external water trap filter (Pack of 5) |  | 11 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C4 ¦ FDA SYSTEM | 12 ¦ Supply, installation, testing and commissioning of aspiration detector with CMOS imager combined with multiple photodiode for reliable very early warning in a wide range of environments with minimal nuisance alarms. The detector should have 4 pipe inlet and min 100m pipelength support per inlet.The detector should have Smart on-board two stage filter retains dust count and remaining filter life for predictable maintenance& coverage area of min 2000 Sq.Mtr | aspiration detector | pipe inlet: 4, pipelength support per inlet: min 100m, coverage area: min 2000 Sq.Mtr | imager: CMOS, sensor: multiple photodiode, feature: very early warning, feature: minimal nuisance alarms, filter: Smart on-board two stage filter retains dust count and remaining filter life for predictable maintenance |  | 4 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C4 ¦ FDA SYSTEM | 13 ¦ Supply,Installation,Testing & Commissioning of UL/VDS listed CPVC Pipe 25 mm Dia & Pipe Accessories for the Aspiration detection. | cpvc pipe | diameter: 25 mm | certification: UL(underwriters laboratories), certification: VDS, feature: listed, accessories: pipe accessories for the aspiration detection |  | 304 | Mtr | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C4 ¦ FDA SYSTEM | 14 ¦ Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable trays |  | feature: for laying all type of cables as indicated above, feature: including all necessary structural supports |  | 389 | Mtr | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C5 ¦ PA SYSTEM | 1 ¦ IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | ip based networkable touch screen paging station |  | feature: selection of zones, feature: supervision of system status, feature: setting of scheduled broadcasts, feature: central exchange with stand by CPU, feature: built-in monitoring loudspeaker, feature: goose-neck microphone, feature: LCD touchscreen display, feature: audio input |  | 1 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C5 ¦ PA SYSTEM | 3 ¦ 9 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | horn type of speaker | power: 9 W | feature: high efficiency, weather protection: IP 65, type: weatherproof, application: suitable for outdoor area |  | 2 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C5 ¦ PA SYSTEM | 4 ¦ 15 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | horn type of speaker | power: 15 W | feature: high efficiency, weather protection: IP 65, type: weatherproof, application: suitable for outdoor area |  | 6 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C5 ¦ PA SYSTEM | 5 ¦ Rack Mounted 200 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | power amplifier | power: 200 watt | mounting: rack mounted, feature: battery back up, feature: wattage shall be as per requirement |  | 1 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C5 ¦ PA SYSTEM | 6 ¦ 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | xlpe cu cable | core: 2C, cross section: 1.5 mm2 | conductor: multi stranded, shielding: shielded, armor: armoured, material: XLPE, material: copper, application: for power & signal |  | 260 | Mtr | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C5 ¦ PA SYSTEM | 7 ¦ DVD player with features to hook up to amplifiers of PA system for music in the common areas. | dvd player |  | feature: features to hook up to amplifiers of PA system for music in the common areas |  | 1 | Nos | RESIN PLANT
C ¦ RESIN PLANT, RISHRA; C5 ¦ PA SYSTEM | 8 ¦ Paging Loudspeaker | paging loudspeaker |  |  |  | 1 | Nos | RESIN PLANT
D ¦ SOLVENT PLANT > D1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall of grooved with groove couplings. All escavations, pedestal supports, structural supports shall be of vendors scope. 100 mm NB | ms black steel pipe | size: 100 mm NB | material: ms(black steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, pipe joints: grooved with groove couplings, scope: all excavations, pedestal supports, structural supports by vendor |  | 166 | Mtr | SOLVENT PLANT
D ¦ SOLVENT PLANT > D1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall of grooved with groove couplings. All escavations, pedestal supports, structural supports shall be of vendors scope. 80 mm NB | ms black steel pipe | size: 80 mm NB | material: ms(black steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, pipe joints: grooved with groove couplings, scope: all excavations, pedestal supports, structural supports by vendor |  | 56 | Mtr | SOLVENT PLANT
D ¦ SOLVENT PLANT > D1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall of grooved with groove couplings. All escavations, pedestal supports, structural supports shall be of vendors scope. 25 mm NB | ms black steel pipe | size: 25 mm NB | material: ms(black steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, pipe joints: grooved with groove couplings, scope: all excavations, pedestal supports, structural supports by vendor |  | 12 | Mtr | SOLVENT PLANT
D ¦ SOLVENT PLANT > D1 ¦ HYDRANT SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. Size 100 mm NB | gate valve | size: 100 mm NB | material: cs(carbon steel), standard: api 600, class: 150, flanges: matching, accessories: nuts & bolts |  | 3 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D1 ¦ HYDRANT SYSTEM | Supply, installation, testing and commissioning of CS Non return valve as per BS 1868, Class 150 with companion flanges,nuts & bolts and gaskets. Size 100 mm NB | non return valve | size: 100 mm NB | material: cs(carbon steel), standard: bs 1868, class: 150, flanges: companion, accessories: nuts & bolts, gaskets |  | 3 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D1 ¦ HYDRANT SYSTEM | Supply & installation of SS oblique type single headed Landing valve with 80 mm inlet and 63 mm outlet SS instantaneous male coupling with rubber cap and chain conforming to IS : 5290 including matching flanges, gasket, nuts and bolts complete. | landing valve | inlet: 80 mm, outlet: 63 mm | material: ss(stainless steel), type: oblique, head: single, coupling: ss(stainless steel) instantaneous male, accessories: rubber cap and chain, standard: indian standard 5290, flanges: matching, accessories: gasket, nuts and bolts |  | 10 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D1 ¦ HYDRANT SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. Size 80 mm NB | butterfly valve | size: 80 mm NB | standard: bs 5155, type: wafer, flanges: matching, accessories: nuts & bolts, fittings: provided by erection vendor |  | 10 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D1 ¦ HYDRANT SYSTEM | Supply & installation of SS branch pipe with 20 mm nozzle conforming to IS : 903 complete | branch pipe | nozzle: 20 mm | material: ss(stainless steel), standard: indian standard 903 |  | 10 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D1 ¦ HYDRANT SYSTEM | Supply & installation of 63 mm dia rubberized reinforced rubber line hose pipe in 15 m length conforming to IS : 636 Type II ISI marked with gunmetal male and female instantaneous coupling conforming to IS 903 wounded with 18 SWG copper wire complete | hose pipe | diameter: 63 mm, length: 15 m | type: rubberized reinforced rubber line, standard: indian standard 636 type ii, certification: isi, coupling: gunmetal male and female instantaneous, coupling standard: indian standard 903, wire: 18 swg copper |  | 20 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D1 ¦ HYDRANT SYSTEM | Supply & installation of MS Hose Box of fabricated from 16 SWG CRCA sheet double door with lockable arrangements to accommodate 2 RRL hose of 15 m length and one branch pipe painted white inside and red outside with one key. (750X600X250 mm) | hose box | dimensions: 750X600X250 mm | material: ms(mild steel), fabrication: 16 swg crca sheet, doors: double, lockable: yes, capacity: 2 rrl hose of 15 m length and one branch pipe, paint: white inside and red outside, accessories: one key |  | 10 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D1 ¦ HYDRANT SYSTEM | Supply & installation of swinging type hose reel drum fabricated from 14 SWG CRCA sheets painted with red colour stove paint 2 coats over 1 coat of primer with 30 m long 20 mm dia rubber hose pipe with with SS self closing shut – off nozzle of 5 mm outlet fixed on wall. | hose reel drum | hose length: 30 m, hose diameter: 20 mm, nozzle outlet: 5 mm | type: swinging, fabrication: 14 swg crca sheets, paint: red colour stove paint 2 coats over 1 coat of primer, hose: rubber, nozzle: ss(stainless steel) self closing shut-off, installation: fixed on wall |  | 10 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D1 ¦ HYDRANT SYSTEM | Supply and installation of pressure gauge, 1/2 inch bottom entry, of suitable range with ball valves and other accessories. | pressure gauge | bottom entry: 1/2 inch | range: suitable, accessories: ball valves and other accessories |  | 1 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D1 ¦ HYDRANT SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends Size 25NB | globe valve | size: 25NB | material: bronze, standard: IS 778, end-type: screwed |  | 16 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D1 ¦ HYDRANT SYSTEM | Supply & installation of 250ltr foam tank filled with 3% ARFFF foam concentrate with foam making branch and pick up tube. | foam tank | tank capacity: 250ltr | foam concentrate: 3% ARFFF, included: foam making branch and pick up tube |  | 2 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection , testing & commissioning of Deluge valve with dry pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 2 way Solenoid Valve, etc. & manual release unit. 150 mm NB | deluge valve | size: 150 mm NB | trim assembly: dry pilot, included: strainer, drain valve, pressure gauge, pressure switch, solenoid valve: flame proof 2 way, manual release unit: included |  | 5 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection , testing & commissioning of Deluge valve with dry pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 2 way Solenoid Valve, etc. & manual release unit. 100 mm NB | deluge valve | size: 100 mm NB | trim assembly: dry pilot, included: strainer, drain valve, pressure gauge, pressure switch, solenoid valve: flame proof 2 way, manual release unit: included |  | 5 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, Class 150 with matching flanges complete with nuts & bolts. 150 mm NB | gate valve | size: 150 mm NB | material: cs(carbon steel), standard: API 600, class: 150, included: matching flanges, nuts & bolts |  | 15 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, Class 150 with matching flanges complete with nuts & bolts. 100 mm NB | gate valve | size: 100 mm NB | material: cs(carbon steel), standard: API 600, class: 150, included: matching flanges, nuts & bolts |  | 15 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing and commissioning of Y-Strainer. 150 mm NB | y-strainer | size: 150 mm NB |  |  | 5 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing and commissioning of Y-Strainer. 100 mm NB | y-strainer | size: 100 mm NB |  |  | 5 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply,installation,testing and commissioning of Foam Sprinkler nozzle with necessary threaded fittings as per drawing. The sprinkler shall be Open Aspiration, Pendent type, K-42 with standard spray angle.End connection 1/2" NPT/BSP.UL/FM Approved. Spray nozzle K factor -42 | foam sprinkler nozzle | k factor: 42, end connection: 1/2" NPT/BSP | type: open aspiration, type: pendent, spray angle: standard, approval: UL(underwriters laboratories)/FM(factory mutual), fittings: necessary threaded fittings as per drawing |  | 517 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply,installation and commissioning of UL/FM approved Quartzoid Bulb Detector for K factor-80. Temp rating 68 deg C. | quartzoid bulb detector | k factor: 80 | approval: UL(underwriters laboratories)/FM(factory mutual), temperature rating: 68 deg C |  | 517 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing and commissioning of Ratio Controller. 150 mm NB | ratio controller | size: 150 mm NB |  |  | 5 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing and commissioning of Ratio Controller. 100 mm NB | ratio controller | size: 100 mm NB |  |  | 5 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing and commissioning of Foam bladder tank vertical type ,manufacturing as per ASME, section-VIII part- I. The bladder material shall be BUNA-N. The Bladder Tank shall be supplied along with all necessary valves, Hydraulically Operated Foam Concentrae Control Valve ,fittingss & instruments as per Technical data sheet attached with Tender documents. Capacity of 1700 ltr. | foam bladder tank | capacity: 1700 ltr. | type: vertical, manufacturing standard: ASME section-VIII part-I, bladder material: BUNA-N, included: all necessary valves, hydraulically operated foam concentrate control valve, fittings & instruments as per technical data sheet |  | 7 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply of AR-AFFF(3%) foam concentrate(PFOS/PFAS free) having sp. Gravity 1.0±.02 g/mlat 20⁰C , PH 7.0-8.5 & viscosity 1200 ±300 cps. | ar-afff foam concentrate |  | concentration: 3%, PFOS/PFAS free: yes, specific gravity: 1.0±.02 g/ml at 20⁰C, pH: 7.0-8.5, viscosity: 1200 ±300 cps | ar-afff foam concentrate | 11900 | Ltr | SOLVENT PLANT
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee, reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 150 NB | gi pipe | diameter: 150 NB | class: C (heavy class), standard: indian standard 1239, fittings: threaded or grooved, included: elbows, tees, reducers, welding flanges, clamps, MS brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, as per fire authorities requirement, for above ground pipes |  | 371 | Mtr | SOLVENT PLANT
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee, reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 100 NB | gi pipe | diameter: 100 NB | class: C (heavy class), standard: indian standard 1239, fittings: threaded or grooved, included: elbows, tees, reducers, welding flanges, clamps, MS brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, as per fire authorities requirement, for above ground pipes |  | 280 | Mtr | SOLVENT PLANT
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee, reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 80 NB | gi pipe | diameter: 80 NB | class: C (heavy class), standard: indian standard 1239, fittings: threaded or grooved, included: elbows, tees, reducers, welding flanges, clamps, MS brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, as per fire authorities requirement, for above ground pipes |  | 182 | Mtr | SOLVENT PLANT
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee, reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 65 NB | gi pipe | diameter: 65 NB | class: C (heavy class), standard: indian standard 1239, fittings: threaded or grooved, included: elbows, tees, reducers, welding flanges, clamps, MS brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, as per fire authorities requirement, for above ground pipes |  | 227 | Mtr | SOLVENT PLANT
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee, reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 50 NB | gi pipe | diameter: 50 NB | class: C (heavy class), standard: indian standard 1239, fittings: threaded or grooved, included: elbows, tees, reducers, welding flanges, clamps, MS brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, as per fire authorities requirement, for above ground pipes |  | 120 | Mtr | SOLVENT PLANT
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee, reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 40NB | gi pipe | diameter: 40 NB | class: C (heavy class), standard: indian standard 1239, fittings: threaded or grooved, included: elbows, tees, reducers, welding flanges, clamps, MS brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, as per fire authorities requirement, for above ground pipes |  | 454 | Mtr | SOLVENT PLANT
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee, reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 25NB | gi pipe | diameter: 25 NB | class: C (heavy class), standard: indian standard 1239, fittings: threaded or grooved, included: elbows, tees, reducers, welding flanges, clamps, MS brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, as per fire authorities requirement, for above ground pipes |  | 2043 | Mtr | SOLVENT PLANT
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall of grooved with groove couplings. All escavations, pedestal supports, structural supports shall be of vendor's scope. 150 mm NB | ms black steel pipe | diameter: 150 mm NB | grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part-1, fittings: elbows, tees, flanges, reducers, clamps, MS support, dash fasteners, painting: two coats approved primer, two coats approved paint, joints: grooved with groove couplings, scope: all excavations, pedestal supports, structural supports by vendor |  | 46 | Mtr | SOLVENT PLANT
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall of grooved with groove couplings. All escavations, pedestal supports, structural supports shall be of vendor's scope. 100 mm NB | ms black steel pipe | diameter: 100 mm NB | grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part-1, fittings: elbows, tees, flanges, reducers, clamps, MS support, dash fasteners, painting: two coats approved primer, two coats approved paint, joints: grooved with groove couplings, scope: all excavations, pedestal supports, structural supports by vendor |  | 75 | Mtr | SOLVENT PLANT
D ¦ SOLVENT PLANT > D2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing & commissioning of Air Buffer tank complete with necessary components. The compressor shall be of capacity 15 M³/Hr( FAD), discharge pressure 10 bar, single stage, reciprocating type. | air buffer tank | compressor capacity: 15 M³/Hr (FAD) | discharge pressure: 10 bar, compressor type: single stage, reciprocating, included: necessary components |  | 1 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D3 ¦ WATER CURTAIN | Supply, erection and testing of heavy grade(class-C) pipes conforming to IS-1239 including all fittings viz. tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer and structural steels for pipe supports. Hanger support with anchor fasteners and clamps shall be supplied to fix the pipes on ceiling wall etc. including supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners) as per specification. Cutting of floors, walls etc and making it good after erection of pipes shall be of vendor's scope. Necessary painting with 2 coats of primer and 2 coats of synthetic enamel paints to be done and supply of paints shall be with vendor's scope. 50 NB | pipe | diameter: 50 NB | grade: heavy (class-C), standard: indian standard 1239, included: tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts, bolts, washer, structural steels for pipe supports, hanger support with anchor fasteners and clamps, supporting/fixing on floor/wall/ceiling with clamps, hangers (using anchor fasteners), painting: 2 coats primer, 2 coats synthetic enamel, supply of paints by vendor, scope: cutting/making good floors/walls by vendor |  | 106 | Mtr | SOLVENT PLANT
D ¦ SOLVENT PLANT > D3 ¦ WATER CURTAIN | Supply, erection and testing of heavy grade(class-C) pipes conforming to IS-1239 including all fittings viz. tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer and structural steels for pipe supports. Hanger support with anchor fasteners and clamps shall be supplied to fix the pipes on ceiling wall etc. including supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners) as per specification. Cutting of floors, walls etc and making it good after erection of pipes shall be of vendor's scope. Necessary painting with 2 coats of primer and 2 coats of synthetic enamel paints to be done and supply of paints shall be with vendor's scope. 65 NB | pipe | diameter: 65 NB | grade: heavy (class-C), standard: indian standard 1239, included: tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts, bolts, washer, structural steels for pipe supports, hanger support with anchor fasteners and clamps, supporting/fixing on floor/wall/ceiling with clamps, hangers (using anchor fasteners), painting: 2 coats primer, 2 coats synthetic enamel, supply of paints by vendor, scope: cutting/making good floors/walls by vendor |  | 126 | Mtr | SOLVENT PLANT
D ¦ SOLVENT PLANT > D3 ¦ WATER CURTAIN | Supply, erection and testing of heavy grade(class-C) pipes conforming to IS-1239 including all fittings viz. tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer and structural steels for pipe supports. Hanger support with anchor fasteners and clamps shall be supplied to fix the pipes on ceiling wall etc. including supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners) as per specification. Cutting of floors, walls etc and making it good after erection of pipes shall be of vendor's scope. Necessary painting with 2 coats of primer and 2 coats of synthetic enamel paints to be done and supply of paints shall be with vendor's scope. 80 NB | pipe | diameter: 80 NB | grade: heavy (class-C), standard: indian standard 1239, included: tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts, bolts, washer, structural steels for pipe supports, hanger support with anchor fasteners and clamps, supporting/fixing on floor/wall/ceiling with clamps, hangers (using anchor fasteners), painting: 2 coats primer, 2 coats synthetic enamel, supply of paints by vendor, scope: cutting/making good floors/walls by vendor |  | 120 | Mtr | SOLVENT PLANT
D ¦ SOLVENT PLANT > D3 ¦ WATER CURTAIN | Supply, erection and testing of heavy grade(class-C) pipes conforming to IS-1239 including all fittings viz. tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer and structural steels for pipe supports. Hanger support with anchor fasteners and clamps shall be supplied to fix the pipes on ceiling wall etc. including supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners) as per specification. Cutting of floors, walls etc and making it good after erection of pipes shall be of vendor's scope. Necessary painting with 2 coats of primer and 2 coats of synthetic enamel paints to be done and supply of paints shall be with vendor's scope. 100 NB | pipe | diameter: 100 NB | grade: heavy (class-C), standard: indian standard 1239, included: tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts, bolts, washer, structural steels for pipe supports, hanger support with anchor fasteners and clamps, supporting/fixing on floor/wall/ceiling with clamps, hangers (using anchor fasteners), painting: 2 coats primer, 2 coats synthetic enamel, supply of paints by vendor, scope: cutting/making good floors/walls by vendor |  | 66 | Mtr | SOLVENT PLANT
D ¦ SOLVENT PLANT > D3 ¦ WATER CURTAIN | Providing & fixing Cast Iron Y Strainer. Size 80 NB | y strainer | size: 80 NB | material: cast iron |  | 3 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D3 ¦ WATER CURTAIN | Providing & fixing Cast Iron Y Strainer. Size 100 NB | y strainer | size: 100 NB | material: cast iron |  | 5 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D3 ¦ WATER CURTAIN | Supply & fixing of SS Water Curtain Nozzle with (K>=71). UL/FM Approved. | water curtain nozzle |  | material: stainless steel, k-factor: >=71, certification: UL(underwriters laboratories), certification: FM(factory mutual) |  | 119 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D3 ¦ WATER CURTAIN | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, Class 150 with matching flanges complete with nuts & bolts. Size 80 NB | gate valve | size: 80 NB | material: cs(carbon steel), standard: API 600, class: 150, ends: matching flanges, supplied with: nuts & bolts |  | 9 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D3 ¦ WATER CURTAIN | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, Class 150 with matching flanges complete with nuts & bolts. Size 100 NB | gate valve | size: 100 NB | material: cs(carbon steel), standard: API 600, class: 150, ends: matching flanges, supplied with: nuts & bolts |  | 15 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D4 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be with grooved couplings. Necesary supports of all kind shall be of vendor's scope. 80 mm NB | ms black steel pipe | size: 80 mm NB | grade: heavy, thickness: 5.4mm, standard: IS(indian standard) 1239 Part -1, supplied with: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved couplings, supports: all kind, vendor's scope |  | 18 | Mtr | SOLVENT PLANT
D ¦ SOLVENT PLANT > D4 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be with grooved couplings. Necesary supports of all kind shall be of vendor's scope. 65 mm NB | ms black steel pipe | size: 65 mm NB | grade: heavy, thickness: 5.4mm, standard: IS(indian standard) 1239 Part -1, supplied with: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved couplings, supports: all kind, vendor's scope |  | 12 | Mtr | SOLVENT PLANT
D ¦ SOLVENT PLANT > D4 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be with grooved couplings. Necesary supports of all kind shall be of vendor's scope. 50 mm NB | ms black steel pipe | size: 50 mm NB | grade: heavy, thickness: 5.4mm, standard: IS(indian standard) 1239 Part -1, supplied with: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved couplings, supports: all kind, vendor's scope |  | 12 | Mtr | SOLVENT PLANT
D ¦ SOLVENT PLANT > D4 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be with grooved couplings. Necesary supports of all kind shall be of vendor's scope. 40 mm NB | ms black steel pipe | size: 40 mm NB | grade: heavy, thickness: 5.4mm, standard: IS(indian standard) 1239 Part -1, supplied with: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved couplings, supports: all kind, vendor's scope |  | 18 | Mtr | SOLVENT PLANT
D ¦ SOLVENT PLANT > D4 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be with grooved couplings. Necesary supports of all kind shall be of vendor's scope. 25 mm NB | ms black steel pipe | size: 25 mm NB | grade: heavy, thickness: 5.4mm, standard: IS(indian standard) 1239 Part -1, supplied with: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved couplings, supports: all kind, vendor's scope |  | 36 | Mtr | SOLVENT PLANT
D ¦ SOLVENT PLANT > D4 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. Size 65 mm NB | butterfly valve | size: 65 mm NB | standard: BS 5155, type: wafer, ends: matching flanges, supplied with: nuts & bolts, fittings: necessary, provided by: erection vendor |  | 2 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D4 ¦ AUTOMATIC SPRINKLER SYSTEM | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts. Size 65 mm NB | non return valve | size: 65 mm NB | type: wafer, ends: matching flanges, supplied with: nuts & bolts |  | 1 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D4 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & fixing of Paddle type Flow Switch | flow switch |  | type: paddle |  | 1 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D4 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Fixing of Sprinkler Head Pendent type for K factor-80. Temp rating 68 deg C. UL/FM Approved. | sprinkler head pendent type |  | k-factor: 80, temperature rating: 68 deg C, certification: UL(underwriters laboratories), certification: FM(factory mutual) |  | 16 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D4 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, installation of automatic 25 NB Air Release Valve | air release valve | size: 25 NB | type: automatic |  | 1 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D4 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends, Size 25NB | globe valve | size: 25 NB | material: bronze, standard: IS 778(indian standard 778), ends: screwed |  | 2 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D4 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends, Size 40NB | globe valve | size: 40 NB | material: bronze, standard: IS 778(indian standard 778), ends: screwed |  | 1 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D4 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Erection and testing of Installation Control Valve complete with trims & gong., Size 80 mm NB | installation control valve | size: 80 mm NB | feature: complete with trims & gong |  | 1 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D4 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, Class 150 with matching flanges complete with nuts & bolts., Size 80 NB | cs(carbon steel) gate valve | size: 80 NB | material: cs(carbon steel), standard: API 600, class: 150, ends: matching flanges, feature: complete with nuts & bolts |  | 1 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D5 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | multicriteria detector |  | type: analogue addressable |  | 12 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D5 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of IR Detector | ir detector |  |  |  | 15 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D5 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable explosion proof Manual Call point | manual call point |  | type: analogue addressable, feature: explosion proof |  | 12 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D5 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of explosion proof Hooter | hooter |  | feature: explosion proof |  | 12 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D5 ¦ FDA SYSTEM | Supply, erction, testing & commissioning of analogue addressable Control Module | control module |  | type: analogue addressable |  | 26 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D5 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Isolator Module | isolator module |  | type: analogue addressable |  | 4 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D5 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Monitor module | monitor module |  | type: analogue addressable |  | 38 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D5 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cabling | core: 2C, size: 1.5 mm2 | feature: complete with lugs, laying and termination of both ends, type: loop cable |  | 690 | Mtr | SOLVENT PLANT
D ¦ SOLVENT PLANT > D5 ¦ FDA SYSTEM | Providing & fixing FRLS CABLING complete with lugs, laying and termination of both ends. 2C x 0.5 mm2 Armoured ( Telephone cable) | frls cabling | core: 2C, size: 0.5 mm2 | feature: complete with lugs, laying and termination of both ends, type: armoured, application: telephone cable |  | 86 | Mtr | SOLVENT PLANT
D ¦ SOLVENT PLANT > D5 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Power cable) | armoured cabling | core: 2C, size: 1.5 mm2 | feature: complete with lugs, laying and termination of both ends, type: power cable |  | 620 | Mtr | SOLVENT PLANT
D ¦ SOLVENT PLANT > D5 ¦ FDA SYSTEM | Supply, erection, fabrication, testing and commission of VOC detector with range of 1 – 1000 ppm isobutylene equivalent.and following accessoriesa) DigiPID internal dust filter (Pack of 5) b) Waterproof Filter Assy, RAEGuard2 PID, Pack of 5 c) DigiPID Teflon UV electrode shield pack of 10 d) DigiPID Dust Cover e) Air Drying Pre Filter Kit f) DigiPID external water trap filter (Pack of 5) | voc detector | range: 1 – 1000 ppm isobutylene equivalent | accessories: DigiPID internal dust filter (Pack of 5), Waterproof Filter Assy, RAEGuard2 PID (Pack of 5), DigiPID Teflon UV electrode shield (pack of 10), DigiPID Dust Cover, Air Drying Pre Filter Kit, DigiPID external water trap filter (Pack of 5) |  | 16 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D5 ¦ FDA SYSTEM | Supply, installation, testing and commissioning of aspiration detector with CMOS imager combined with multiple photodiode for reliable very early warning in a wide range of environments with minimal nuisance alarms. The detector should have 4 pipe inlet and min 100m pipelength support per inlet.The detector should have Smart on-board filter retains dust count and remaining filter life for predictable maintenance& coverage area of min 5000 Sq. | aspiration detector | pipe inlet: 4, pipelength support per inlet: min 100m, coverage area: min 5000 Sq. | imager: CMOS, sensor: multiple photodiode, feature: very early warning, feature: minimal nuisance alarms, feature: smart on-board filter retains dust count and remaining filter life for predictable maintenance |  | 4 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D5 ¦ FDA SYSTEM | Supply,Installation,Testing & Commissioning of UL/VDS listed CPVC Pipe 25 mm Dia & Pipe Accessories for the Aspiration detection. | cpvc pipe | diameter: 25 mm | certification: UL, certification: VDS, application: aspiration detection |  | 846 | Mtr | SOLVENT PLANT
D ¦ SOLVENT PLANT > D5 ¦ FDA SYSTEM | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable trays |  | material: gi(galvanized iron), application: laying all type of cables, feature: including all necessary structural supports |  | 894 | Mtr | SOLVENT PLANT
D ¦ SOLVENT PLANT > D6 ¦ PA SYSTEM | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | ip based networkable touch screen paging station |  | feature: selection of zones, feature: supervision of system status, feature: setting of scheduled broadcasts, feature: central exchange with stand by CPU, feature: built-in monitoring loudspeaker, feature: goose-neck microphone, feature: LCD touchscreen display, feature: audio input |  | 1 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D6 ¦ PA SYSTEM | 15 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | horn type speaker | power: 15 W | feature: high efficiency, protection: IP 65, feature: weatherproof type, application: suitable for outdoor area |  | 8 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D6 ¦ PA SYSTEM | 30 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | horn type speaker | power: 30 W | feature: high efficiency, protection: IP 65, feature: weatherproof type, application: suitable for outdoor area |  | 8 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D6 ¦ PA SYSTEM | Rack Mounted 500 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | power amplifier | power: 500 watt | mounting: rack mounted, feature: battery back up, feature: wattage shall be as per requirement |  | 1 | Nos | SOLVENT PLANT
D ¦ SOLVENT PLANT > D6 ¦ PA SYSTEM | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | xlpe cu cable | core: 2C, size: 1.5 mm2 | type: multi stranded, type: shielded, type: armoured, application: power & signal |  | 440 | Mtr | SOLVENT PLANT
E ¦ ADMIN BUILDING > E1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be of grooved with groove coupling. all escavation & back filling, pedestal support, structural support shall be of vendor's scope. 100 mm NB | ms black steel pipe | size: 100 mm NB | grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, feature: all excavation & back filling, pedestal support, structural support vendor's scope |  | 36 | Mtr | ADMIN BUILDING
E ¦ ADMIN BUILDING > E1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be of grooved with groove coupling. all escavation & back filling, pedestal support, structural support shall be of vendor's scope. 80 mm NB | ms black steel pipe | size: 80 mm NB | grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, feature: all excavation & back filling, pedestal support, structural support vendor's scope |  | 36 | Mtr | ADMIN BUILDING
E ¦ ADMIN BUILDING > E1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be of grooved with groove coupling. all escavation & back filling, pedestal support, structural support shall be of vendor's scope. 25 mm NB | ms black steel pipe | size: 25 mm NB | grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, feature: all excavation & back filling, pedestal support, structural support vendor's scope |  | 18 | Mtr | ADMIN BUILDING
E ¦ ADMIN BUILDING > E1 ¦ HYDRANT SYSTEM | Supply & installation of swinging type hose reel drum fabricated from 14 SWG CRCA sheets painted with red colour stove paint 2 coats over 1 coat of primer with 30 m long 20 mm dia rubber hose pipe with with SS self closing shut – off nozzle of 5 mm outlet fixed on wall. | hose reel drum | hose length: 30 m, hose diameter: 20 mm, nozzle outlet: 5 mm | type: swinging, material: 14 SWG CRCA sheet, painting: red colour stove paint 2 coats over 1 coat of primer, hose material: rubber, nozzle material: stainless steel, nozzle type: self closing shut-off, mounting: fixed on wall |  | 3 | Nos | ADMIN BUILDING
E ¦ ADMIN BUILDING > E1 ¦ HYDRANT SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends Size 25NB | globe valve | size: 25NB | material: bronze, standard: indian standard 778, end type: screwed |  | 3 | Nos | ADMIN BUILDING
E ¦ ADMIN BUILDING > E1 ¦ HYDRANT SYSTEM | Supply & installation of SS oblique type single headed Landing valve with 80 mm inlet and 63 mm outlet SS instantaneous male coupling with rubber cap and chain conforming to IS : 5290 including matching flanges, gasket, nuts and bolts complete. Size 80 mm NB | landing valve | inlet: 80 mm, outlet: 63 mm, size: 80 mm NB | material: stainless steel, type: oblique, head: single, coupling: stainless steel instantaneous male, cap: rubber, chain: included, standard: indian standard 5290, accessories: matching flanges, gasket, nuts and bolts |  | 3 | Nos | ADMIN BUILDING
E ¦ ADMIN BUILDING > E1 ¦ HYDRANT SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. | butterfly valve |  | standard: british standard 5155, type: wafer, accessories: matching flanges, nuts & bolts, fittings: provided by erection vendor |  | 2 |  | ADMIN BUILDING
E ¦ ADMIN BUILDING > E1 ¦ HYDRANT SYSTEM | Supply & installation of SS branch pipe with 20 mm nozzle conforming to IS : 903 complete | branch pipe | nozzle: 20 mm | material: stainless steel, standard: indian standard 903 |  | 2 | Nos | ADMIN BUILDING
E ¦ ADMIN BUILDING > E1 ¦ HYDRANT SYSTEM | Supply & installation of 63 mm dia rubberized reinforced rubber line hose pipe in 15 m length conforming to IS : 636 Type II ISI marked with gunmetal male and female instantaneous coupling conforming to IS 903 wounded with 18 SWG copper wire complete | rubber line hose pipe | diameter: 63 mm, length: 15 m | type: rubberized reinforced, standard: indian standard 636 type II, certification: ISI, coupling: gunmetal male and female instantaneous, coupling standard: indian standard 903, wire: 18 SWG copper |  | 4 | Nos | ADMIN BUILDING
E ¦ ADMIN BUILDING > E1 ¦ HYDRANT SYSTEM | Supply & installation of MS Hose Box of fabricated from 16 SWG CRCA sheet double door with lockable arrangements to accommodate 2 RRL hose of 15 m length and one branch pipe painted white inside and red outside with one key. (750X600X250 mm) | hose box | dimensions: 750X600X250 mm | material: ms, fabrication: 16 SWG CRCA sheet, doors: double, lockable: yes, capacity: 2 RRL hose of 15 m length and one branch pipe, painting: white inside and red outside, key: one |  | 2 | Nos | ADMIN BUILDING
E ¦ ADMIN BUILDING > E2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be of grooved with groove couplings. All related civil work viz as wall cutting, structural supports etc for laying of sprinkler piping shall be vendor's scope. 40 mm NB | ms black steel pipe | size: 40 mm NB | grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove couplings, civil work: wall cutting, structural supports for laying of sprinkler piping vendor's scope |  | 18 | Mtr | ADMIN BUILDING
E ¦ ADMIN BUILDING > E2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be of grooved with groove couplings. All related civil work viz as wall cutting, structural supports etc for laying of sprinkler piping shall be vendor's scope. 25 mm NB | ms black steel pipe | size: 25 mm NB | grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove couplings, civil work: wall cutting, structural supports for laying of sprinkler piping vendor's scope |  | 72 | Mtr | ADMIN BUILDING
E ¦ ADMIN BUILDING > E2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. Size100 mm NB | butterfly valve | size: 100 mm NB | standard: british standard 5155, type: wafer, fittings: matching flanges, nuts & bolts, feature: necessary fittings by erection vendor |  | 1 | Nos | ADMIN BUILDING
E ¦ ADMIN BUILDING > E2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. Size80 mm NB | butterfly valve | size: 80 mm NB | standard: british standard 5155, type: wafer, fittings: matching flanges, nuts & bolts, feature: necessary fittings by erection vendor |  | 1 | Nos | ADMIN BUILDING
E ¦ ADMIN BUILDING > E2 ¦ AUTOMATIC SPRINKLER SYSTEM | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts confirming to API 594. Size100 mm NB | non return valve | size: 100 mm NB | type: wafer, fittings: matching flanges, nuts & bolts, standard: api 594 |  | 1 | Nos | ADMIN BUILDING
E ¦ ADMIN BUILDING > E2 ¦ AUTOMATIC SPRINKLER SYSTEM | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts confirming to API 594. Size80 mm NB | non return valve | size: 80 mm NB | type: wafer, fittings: matching flanges, nuts & bolts, standard: api 594 |  | 1 | Nos | ADMIN BUILDING
E ¦ ADMIN BUILDING > E2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & fixing of paddle type Flow Switch | flow switch |  | type: paddle |  | 2 | Nos | ADMIN BUILDING
E ¦ ADMIN BUILDING > E2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Fixing of Sprinkler Head Pendent type for K factor-80. Temp rating 68 deg C. UL/FM Approved. | sprinkler head pendent type |  | k factor: 80, temperature rating: 68 deg c, certification: ul, certification: fm |  | 34 | Nos | ADMIN BUILDING
E ¦ ADMIN BUILDING > E2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, installation of automatic 25 NB Air Release Valve | air release valve | size: 25 NB | feature: automatic |  | 1 | Nos | ADMIN BUILDING
E ¦ ADMIN BUILDING > E2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends Size 40NB | globe valve | size: 40NB | material: bronze, standard: indian standard 778, end type: screwed |  | 2 | Nos | ADMIN BUILDING
E ¦ ADMIN BUILDING > E2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends Size 25NB | globe valve | size: 25NB | material: bronze, standard: indian standard 778, end type: screwed |  | 2 | Nos | ADMIN BUILDING
E ¦ ADMIN BUILDING > E2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Erection and testing of Installation Control Valve complete with trims & gong. Size 100 mm NB | installation control valve | size: 100 mm NB | feature: complete with trims & gong |  | 1 | Nos | ADMIN BUILDING
E ¦ ADMIN BUILDING > E2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, Class 150 with matching flanges complete with nuts & bolts. Size 100 mm NB | gate valve | size: 100 mm NB | material: cs(carbon steel), standard: api 600, class: 150, fittings: matching flanges, nuts & bolts |  | 1 | Nos | ADMIN BUILDING
E ¦ ADMIN BUILDING > E3 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Manual Call point | manual call point |  | type: analogue addressable |  | 4 | Nos | ADMIN BUILDING
E ¦ ADMIN BUILDING > E3 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of Hooter cum strobe | hooter cum strobe |  |  |  | 4 | Nos | ADMIN BUILDING
E ¦ ADMIN BUILDING > E3 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of Telephone jack. | telephone jack |  |  |  | 2 | Nos | ADMIN BUILDING
E ¦ ADMIN BUILDING > E3 ¦ FDA SYSTEM | Supply, erction, testing & commissioning of analogue addressable Control Module | control module |  | type: analogue addressable |  | 2 | Nos | ADMIN BUILDING
E ¦ ADMIN BUILDING > E3 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Isolator Module | isolator module |  | type: analogue addressable |  | 2 | Nos | ADMIN BUILDING
E ¦ ADMIN BUILDING > E3 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Monitor module | monitor module |  | type: analogue addressable |  | 2 | Nos | ADMIN BUILDING
E ¦ ADMIN BUILDING > E3 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. a ¦ 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cabling | configuration: 2C x 1.5 mm2 | type: loop cable, feature: complete with lugs, laying and termination of both ends |  | 170 | Mtr | ADMIN BUILDING
E ¦ ADMIN BUILDING > E3 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. a ¦ 2C x 1.5 mm2 Armoured ( Power cable) | armoured cabling | configuration: 2C x 1.5 mm2 | type: power cable, feature: complete with lugs, laying and termination of both ends |  | 104 | Mtr | ADMIN BUILDING
E ¦ ADMIN BUILDING > E3 ¦ FDA SYSTEM | Providing & fixing FRLS CABLING complete with lugs, laying and termination of both ends. a ¦ 2C x 0.5 mm2 Armoured ( Telephone cable) | frls cabling | configuration: 2C x 0.5 mm2 | type: telephone cable, feature: complete with lugs, laying and termination of both ends |  | 28 | Mtr | ADMIN BUILDING
E ¦ ADMIN BUILDING > E3 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. a ¦ 2C x 1.5 mm2 Armoured ( Speaker cable) | armoured cabling | configuration: 2C x 1.5 mm2 | type: speaker cable, feature: complete with lugs, laying and termination of both ends |  | 164 | Mtr | ADMIN BUILDING
E ¦ ADMIN BUILDING > E3 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of Repeater Panel | repeater panel |  |  |  | 1 | Nos | ADMIN BUILDING
E ¦ ADMIN BUILDING > E3 ¦ FDA SYSTEM | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | ip based networkable touch screen paging station |  | feature: selection of zones, supervision of system status, setting of scheduled broadcasts, central exchange with stand by cpu, built-in monitoring loudspeaker, goose-neck microphone, lcd touchscreen display, audio input |  | 1 | Nos | ADMIN BUILDING
E ¦ ADMIN BUILDING > E3 ¦ FDA SYSTEM | 6 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | horn type of speaker | power: 6 W | feature: high efficiency, weather protection ip 65 (weatherproof type, suitable for outdoor area) |  | 21 | Nos | ADMIN BUILDING
E ¦ ADMIN BUILDING > E3 ¦ FDA SYSTEM | Rack Mounted 200 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | power amplifier | power: 200 watt | feature: rack mounted, battery back up, wattage shall be as per requirement |  | 1 | Nos | ADMIN BUILDING
E ¦ ADMIN BUILDING > E3 ¦ FDA SYSTEM | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | xlpe cu cable | core: 2C, cross section: 1.5 mm2 | feature: multi stranded, shielded, armoured, for power & signal |  | 164 | Mtr | ADMIN BUILDING
E ¦ ADMIN BUILDING > E3 ¦ FDA SYSTEM | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | dvd player |  | feature: hook up to amplifiers of pa system for music in the common areas |  | 1 | Nos | ADMIN BUILDING
E ¦ ADMIN BUILDING > E3 ¦ FDA SYSTEM | Paging Loudspeaker | paging loudspeaker |  |  |  | 1 | Nos | ADMIN BUILDING
F ¦ R & D BUILDING > F1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be of groove with grooved coupling. All escavation, pedestal support, structural support shall be of vendor's scope. a. 100 mm NB | ms black steel pipe | size: 100 mm NB | grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: groove with grooved coupling, scope: all escavation, pedestal support, structural support of vendor's scope |  | 36 | Mtr | R&D BUILDING
F ¦ R & D BUILDING > F1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be of groove with grooved coupling. All escavation, pedestal support, structural support shall be of vendor's scope. b 80 mm NB | ms black steel pipe | size: 80 mm NB | grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: groove with grooved coupling, scope: all escavation, pedestal support, structural support of vendor's scope |  | 36 | Mtr | R&D BUILDING
F ¦ R & D BUILDING > F1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be of groove with grooved coupling. All escavation, pedestal support, structural support shall be of vendor's scope. c 25 mm NB | ms black steel pipe | size: 25 mm NB | grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: groove with grooved coupling, scope: all escavation, pedestal support, structural support of vendor's scope |  | 18 | Mtr | R&D BUILDING
F ¦ R & D BUILDING > F1 ¦ HYDRANT SYSTEM | Supply & installation of swinging type hose reel drum fabricated from 14 SWG CRCA sheets painted with red colour stove paint 2 coats over 1 coat of primer with 30 m long 20 mm dia rubber hose pipe with with SS self closing shut – off nozzle of 5 mm outlet fixed on wall. | hose reel drum | hose length: 30 m, hose diameter: 20 mm, nozzle outlet: 5 mm | type: swinging, fabrication: 14 SWG CRCA sheets, painting: red colour stove paint 2 coats over 1 coat of primer, hose material: rubber, nozzle material: ss(stainless steel), nozzle type: self closing shut-off, mounting: fixed on wall |  | 3 | Nos | R&D BUILDING
F ¦ R & D BUILDING > F1 ¦ HYDRANT SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends a Size 25NB | globe valve | size: 25NB | material: bronze, standard: indian standard 778, end connection: screwed |  | 3 | Nos | R&D BUILDING
F ¦ R & D BUILDING > F1 ¦ HYDRANT SYSTEM | Supply & installation of SS oblique type single headed Landing valve with 80 mm inlet and 63 mm outlet SS instantaneous male coupling with rubber cap and chain conforming to IS : 5290 including matching flanges, gasket, nuts and bolts complete. | landing valve | inlet: 80 mm, outlet: 63 mm | material: ss(stainless steel), type: oblique, head: single, coupling: ss(stainless steel) instantaneous male, accessories: rubber cap and chain, standard: indian standard 5290, accessories: matching flanges, gasket, nuts and bolts |  | 2 | Nos | R&D BUILDING
F ¦ R & D BUILDING > F1 ¦ HYDRANT SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. a Size 80 mm NB | butterfly valve | size: 80 mm NB | standard: british standard 5155, type: wafer, accessories: matching flanges, nuts & bolts, fittings: necessary fittings by erection vendor |  | 2 | Nos | R&D BUILDING
F ¦ R & D BUILDING > F1 ¦ HYDRANT SYSTEM | Supply & installation of SS branch pipe with 20 mm nozzle conforming to IS : 903 complete | branch pipe | nozzle: 20 mm | material: ss(stainless steel), standard: indian standard 903 |  | 2 | Nos | R&D BUILDING
F ¦ R & D BUILDING > F1 ¦ HYDRANT SYSTEM | Supply & installation of 63 mm dia rubberized reinforced rubber line hose pipe in 15 m length conforming to IS : 636 Type II ISI marked with gunmetal male and female instantaneous coupling conforming to IS 903 wounded with 18 SWG copper wire complete | rubber line hose pipe | diameter: 63 mm, length: 15 m | type: rubberized reinforced, standard: indian standard 636 type II, certification: ISI, coupling: gunmetal male and female instantaneous, coupling standard: indian standard 903, wire: 18 SWG copper |  | 4 | Nos | R&D BUILDING
F ¦ R & D BUILDING > F1 ¦ HYDRANT SYSTEM | Supply & installation of MS Hose Box of fabricated from 16 SWG CRCA sheet double door with lockable arrangements to accommodate 2 RRL hose of 15 m length and one branch pipe painted white inside and red outside with one key. (750X600X250 mm) | hose box | dimensions: 750X600X250 mm | material: ms(mild steel), fabrication: 16 SWG CRCA sheet, doors: double, lockable: yes, capacity: 2 RRL hose of 15 m length and one branch pipe, painting: white inside and red outside, accessories: one key |  | 2 | Nos | R&D BUILDING
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. e 50 mm NB | ms black steel pipe | size: 50 mm NB | grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, scope: all related civil work, supports of vendor's scope |  | 12 | Mtr | R&D BUILDING
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. f 40 mm NB | ms black steel pipe | size: 40 mm NB | grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, scope: all related civil work, supports of vendor's scope |  | 12 | Mtr | R&D BUILDING
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. g 25 mm NB | ms black steel pipe | size: 25 mm NB | grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, scope: all related civil work, supports of vendor's scope |  | 66 | Mtr | R&D BUILDING
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. a Size150 mm NB | butterfly valve | size: 150 mm NB | standard: british standard 5155, type: wafer, fittings: matching flanges, nuts & bolts, feature: necessary fittings provided by erection vendor |  | 2 | Nos | R&D BUILDING
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. b Size50 mm NB | butterfly valve | size: 50 mm NB | standard: british standard 5155, type: wafer, fittings: matching flanges, nuts & bolts, feature: necessary fittings provided by erection vendor |  | 1 | Nos | R&D BUILDING
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts confirming to API 594. a Size150 mm NB | non return valve | size: 150 mm NB | type: wafer, fittings: matching flanges, nuts & bolts, standard: api 594 |  | 2 | Nos | R&D BUILDING
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts confirming to API 594. b Size50 mm NB | non return valve | size: 50 mm NB | type: wafer, fittings: matching flanges, nuts & bolts, standard: api 594 |  | 1 | Nos | R&D BUILDING
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & fixing of Paddle type Flow Switch | paddle type flow switch |  |  |  | 2 | Nos | R&D BUILDING
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Fixing of Sprinkler Head Pendent type for K factor-80. Temp rating 68 deg C. UL/FM Approved. | sprinkler head pendent type | k factor: 80 | temperature rating: 68 deg c, certification: ul(underwriters laboratories), certification: fm(factory mutual) |  | 108 | Nos | R&D BUILDING
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, installation of automatic 25 NB Air Release Valve | air release valve | size: 25 NB | feature: automatic |  | 1 | Nos | R&D BUILDING
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends a Size 40NB | globe valve | size: 40 NB | material: bronze, standard: indian standard 778, end connection: screwed |  | 2 | Nos | R&D BUILDING
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends b Size 25NB | globe valve | size: 25 NB | material: bronze, standard: indian standard 778, end connection: screwed |  | 2 | Nos | R&D BUILDING
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Erection and testing of Installation Control Valve complete with trims & gong. a Size 100 mm NB | installation control valve | size: 100 mm NB | feature: complete with trims & gong |  | 1 | Nos | R&D BUILDING
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | multicriteria detector |  | type: analogue addressable |  | 25 | Nos | R&D BUILDING
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, testing & commissioning of analogue addressable Manual Call point | manual call point |  | type: analogue addressable |  | 4 | Nos | R&D BUILDING
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, testing & commissioning of Hooter cum strobe | hooter cum strobe |  |  |  | 4 | Nos | R&D BUILDING
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, testing & commissioning of Telephone jack. | telephone jack |  |  |  | 2 | Nos | R&D BUILDING
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erction, testing & commissioning of analogue addressable Control Module | control module |  | type: analogue addressable |  | 2 | Nos | R&D BUILDING
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, testing & commissioning of analogue addressable Isolator Module | isolator module |  | type: analogue addressable |  | 1 | Nos | R&D BUILDING
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, testing & commissioning of analogue addressable Monitor module | monitor module |  | type: analogue addressable |  | 3 | Nos | R&D BUILDING
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. a 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cabling | cable: 2C x 1.5 mm2 | feature: complete with lugs, laying and termination of both ends, type: loop cable, cable type: armoured |  | 170 | Mtr | R&D BUILDING
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. a 2C x 1.5 mm2 Armoured ( Power cable) | armoured cabling | cable: 2C x 1.5 mm2 | feature: complete with lugs, laying and termination of both ends, type: power cable, cable type: armoured |  | 104 | Mtr | R&D BUILDING
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Providing & fixing FRLS CABLING complete with lugs, laying and termination of both ends. a 2C x 0.5 mm2 Armoured ( Telephone cable) | frls cabling | cable: 2C x 0.5 mm2 | feature: complete with lugs, laying and termination of both ends, type: telephone cable, cable type: armoured |  | 28 | Mtr | R&D BUILDING
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Providing & fixing 200Watt Amplifier with necessary accessories. | amplifier | power: 200Watt | feature: with necessary accessories |  | 1 | Nos | R&D BUILDING
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, testing & commissioning of Repeater Panel | repeater panel |  |  |  | 1 | Nos | R&D BUILDING
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | ip based networkable touch screen paging station |  | feature: selection of zones, supervision of system status, setting of scheduled broadcasts, central exchange with stand by cpu, built-in monitoring loudspeaker, goose-neck microphone, lcd touchscreen display, audio input |  | 1 | Nos | R&D BUILDING
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | 6 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | horn type of speaker | power: 6 W | feature: high efficiency, weather protection ip 65, weatherproof type, suitable for outdoor area |  | 21 | Nos | R&D BUILDING
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Rack Mounted 200 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | power amplifier | power: 200 watt | feature: rack mounted, battery back up, wattage shall be as per requirement |  | 1 | Nos | R&D BUILDING
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | xlpe cu cable | core: 2C, cross section: 1.5 mm2 | feature: multi stranded, shielded, armoured, for power & signal |  | 164 | Mtr | R&D BUILDING
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | dvd player |  | feature: hook up to amplifiers of pa system for music in the common areas |  | 1 | Nos | R&D BUILDING
F ¦ R & D BUILDING > F2 ¦ AUTOMATIC SPRINKLER SYSTEM | Paging Loudspeaker | paging loudspeaker |  |  |  | 1 | Nos | R&D BUILDING
G ¦ MONOMER COLD ROOM > G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection , testing & commissioning of Deluge valve with wet pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 3/2 way Solenoid Valve, air filter regulator etc. & manual release unit. The valve shall be electro-pneumatic type. 80 mm NB | deluge valve | size: 80 mm NB | trim assembly: wet pilot, fitted with: strainer, drain valve, pressure gauge, pressure switch, solenoid valve: flame proof 3/2 way, air filter regulator: included, manual release unit: included, type: electro-pneumatic |  | 1 | Nos | MONOMER COLD ROOM
G ¦ MONOMER COLD ROOM > G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. 80 mm NB | gate valve | size: 80 mm NB | material: cs(carbon steel), standard: API 600, class: 150, flanges: matching, included: nuts & bolts |  | 3 | Nos | MONOMER COLD ROOM
G ¦ MONOMER COLD ROOM > G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, installation, testing & commissioning of Y- Stainer 80 mm NB | y stainer | size: 80 mm NB |  |  | 1 | Nos | MONOMER COLD ROOM
G ¦ MONOMER COLD ROOM > G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply,installation,testing and commissioning of HVWS NOZZLE with necessary threaded fittings as per drawing. K26, SPRAY ANGLE=100° | hvws nozzle |  | model: K26, spray angle: 100°, fittings: necessary threaded fittings as per drawing |  | 12 | Nos | MONOMER COLD ROOM
G ¦ MONOMER COLD ROOM > G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply,installation and commissioning of UL/FM approved Quartzoid Bulb Detector for K factor-80. Temp rating 68 deg C | quartzoid bulb detector |  | certification: UL(underwriters laboratories)/FM(factory mutual), k factor: 80, temperature rating: 68 deg C |  | 12 | Nos | MONOMER COLD ROOM
G ¦ MONOMER COLD ROOM > G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 80 NB | gi "c" class pipes | size: 80 NB | class: heavy class, standard: IS 1239, fittings: threaded or grooved, included: elbow, tee, reducer, welding flanges, clamps to MS brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, application: above ground pipes, as per fire authorities requirement |  | 9 | Mtr | MONOMER COLD ROOM
G ¦ MONOMER COLD ROOM > G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 65 NB | gi "c" class pipes | size: 65 NB | class: heavy class, standard: IS 1239, fittings: threaded or grooved, included: elbow, tee, reducer, welding flanges, clamps to MS brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, application: above ground pipes, as per fire authorities requirement |  | 6 | Mtr | MONOMER COLD ROOM
G ¦ MONOMER COLD ROOM > G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 50 NB | gi "c" class pipes | size: 50 NB | class: heavy class, standard: IS 1239, fittings: threaded or grooved, included: elbow, tee, reducer, welding flanges, clamps to MS brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, application: above ground pipes, as per fire authorities requirement |  | 6 | Mtr | MONOMER COLD ROOM
G ¦ MONOMER COLD ROOM > G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 40NB | gi "c" class pipes | size: 40NB | class: heavy class, standard: IS 1239, fittings: threaded or grooved, included: elbow, tee, reducer, welding flanges, clamps to MS brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, application: above ground pipes, as per fire authorities requirement |  | 17 | Mtr | MONOMER COLD ROOM
G ¦ MONOMER COLD ROOM > G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 25NB | gi "c" class pipes | size: 25NB | class: heavy class, standard: IS 1239, fittings: threaded or grooved, included: elbow, tee, reducer, welding flanges, clamps to MS brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, application: above ground pipes, as per fire authorities requirement |  | 56 | Mtr | MONOMER COLD ROOM
G ¦ MONOMER COLD ROOM > G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing & commissioning of analogue addressable ROR(Rate of Rise) type Heat Detector | heat detector |  | type: analogue addressable, detector type: ROR (Rate of Rise) |  | 4 | Nos | MONOMER COLD ROOM
G ¦ MONOMER COLD ROOM > G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing & commissioning of analogue addressable Manual Call point | manual call point |  | type: analogue addressable |  | 1 | Nos | MONOMER COLD ROOM
G ¦ MONOMER COLD ROOM > G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing & commissioning of Hooter cum strobe | hooter cum strobe |  |  |  | 1 | Nos | MONOMER COLD ROOM
G ¦ MONOMER COLD ROOM > G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erction, testing & commissioning of analogue addressable Control Module | control module |  | type: analogue addressable |  | 2 | Nos | MONOMER COLD ROOM
G ¦ MONOMER COLD ROOM > G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing & commissioning of analogue addressable Isolator Module | isolator module |  | type: analogue addressable |  | 1 | Nos | MONOMER COLD ROOM
G ¦ MONOMER COLD ROOM > G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing & commissioning of analogue addressable Monitor module | monitor module |  | type: analogue addressable |  | 1 | Nos | MONOMER COLD ROOM
G ¦ MONOMER COLD ROOM > G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cabling | configuration: 2C x 1.5 mm2 | type: armoured, cable type: loop cable, feature: complete with lugs, laying and termination of both ends |  | 32 | Mtr | MONOMER COLD ROOM
G ¦ MONOMER COLD ROOM > G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Power cable) | armoured cabling | configuration: 2C x 1.5 mm2 | type: armoured, cable type: power cable, feature: complete with lugs, laying and termination of both ends |  | 12 | Mtr | MONOMER COLD ROOM
G ¦ MONOMER COLD ROOM > G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable trays |  | feature: for laying all type of cables as indicated above, feature: including all necessary structural supports |  | 32 | Mtr | MONOMER COLD ROOM
G ¦ MONOMER COLD ROOM > G3 ¦ PA SYSTEM | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | paging station |  | type: IP based networkable, feature: touch screen, feature: selection of zones, feature: supervision of system status, feature: setting of scheduled broadcasts, feature: central exchange with stand by CPU, feature: built-in monitoring loudspeaker, feature: goose-neck microphone, feature: LCD touchscreen display, feature: audio input |  | 1 | Nos | MONOMER COLD ROOM
G ¦ MONOMER COLD ROOM > G3 ¦ PA SYSTEM | 6 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | horn type speaker | power: 6 W | efficiency: high, weather protection: IP 65, type: weatherproof, suitability: suitable for outdoor area |  | 2 | Nos | MONOMER COLD ROOM
G ¦ MONOMER COLD ROOM > G3 ¦ PA SYSTEM | Rack Mounted 125 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | power amplifier | power: 125 watt | mounting: rack mounted, feature: battery back up, feature: wattage shall be as per requirement |  | 1 | Nos | MONOMER COLD ROOM
G ¦ MONOMER COLD ROOM > G3 ¦ PA SYSTEM | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | dvd player |  | feature: features to hook up to amplifiers of PA system for music in the common areas |  | 1 | Nos | MONOMER COLD ROOM
G ¦ MONOMER COLD ROOM > G3 ¦ PA SYSTEM | Paging Loudspeaker | loudspeaker |  | feature: paging |  | 1 | Nos | MONOMER COLD ROOM
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H1 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection , testing & commissioning of Deluge valve with dry pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 3/2 way Solenoid Valve, air filter regulator etc. & manual release unit. The valve shall be electro-pneumatic double inter lock system as per scheme drawing. 80 mm NB | deluge valve | size: 80 mm NB | assembly: dry pilot trim, included: strainer, included: drain valve, included: pressure gauge, included: pressure switch, included: flame proof 3/2 way solenoid valve, included: air filter regulator, included: manual release unit, system: electro-pneumatic double inter lock |  | 3 | Nos | MONOMER, STYRENE & SOLVENT PUMP
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H1 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. 80 mm NB | gate valve | size: 80 mm NB | material: cs(carbon steel), standard: api 600, class: 150, included: matching flanges, included: nuts & bolts |  | 9 | Nos | MONOMER, STYRENE & SOLVENT PUMP
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H1 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing and commissioning of Y-Strainer.. Size 80 mm NB | y-strainer | size: 80 mm NB |  |  | 3 | Nos | MONOMER, STYRENE & SOLVENT PUMP
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H1 ¦ FOAM WATER SPRAY SYSTEM | Supply,installation,testing and commissioning of Foam Sprinkler nozzle with necessary threaded fittings as per drawing. The sprinkler shall be Open Aspiration, Pendent type, K-42 with standard spray angle.End connection 1/2" NPT/BSP.UL/FM Approved. Spray nozzle K factor -42 | foam sprinkler nozzle |  | fittings: necessary threaded, type: open aspiration, type: pendent, k-factor: 42, spray angle: standard, end connection: 1/2" NPT/BSP, certification: UL(underwriters laboratories), certification: FM(factory mutual) |  | 17 | Nos | MONOMER, STYRENE & SOLVENT PUMP
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H1 ¦ FOAM WATER SPRAY SYSTEM | Supply,installation and commissioning of UL/FM approved Quartzoid Bulb Detector for K factor-80. Temp rating 68 deg C | quartzoid bulb detector |  | certification: UL(underwriters laboratories), certification: FM(factory mutual), k-factor: 80, temperature rating: 68 deg C |  | 17 | Nos | MONOMER, STYRENE & SOLVENT PUMP
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H1 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing and commissioning of Ratio Controller. 80NB | ratio controller | size: 80NB |  |  | 3 | Nos | MONOMER, STYRENE & SOLVENT PUMP
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H1 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing and commissioning of Foam bladder tank vertical type ,manufacturing as per ASME, section-VIII part- I. The bladder material shall be BUNA-N. The Bladder Tank shall be supplied along with all necessary valves, Hydraulically Operated Foam Concentrae Control Valve ,fittingss & instruments as per Technical data sheet attached with Tender documents. Capacity of 500 ltr. | foam bladder tank | capacity: 500 ltr. | type: vertical, standard: ASME(american society of mechanical engineers) section-VIII part-I, bladder material: BUNA-N, included: all necessary valves, included: hydraulically operated foam concentrate control valve, included: fittings & instruments |  | 1 | Nos | MONOMER, STYRENE & SOLVENT PUMP
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H1 ¦ FOAM WATER SPRAY SYSTEM | Supply of AR-AFFF(3%) foam concentrate(PFOS/PFAS free) having sp. Gravity 1.0±.02 g/mlat 20⁰C , PH 7.0-8.5 & viscosity 1200 ±300 cps. | foam concentrate |  | type: AR-AFFF(3%) (aqueous film forming foam), feature: PFOS/PFAS free, specific gravity: 1.0±.02 g/ml at 20⁰C, pH: 7.0-8.5, viscosity: 1200 ±300 cps | ar-afff(3%) | 500 | Ltr | MONOMER, STYRENE & SOLVENT PUMP
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H1 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 100 mm NB | ms black steel pipe | size: 100 mm NB, thickness: 5.4mm | grade: heavy, material: ms(black steel), standard: IS 1239 Part-1(indian standard), fittings: elbows, fittings: tees, fittings: flanges, fittings: reduces clamps, supports: MS support dash fasteners, coating: two coats of approved primer, coating: two coats of approved paint, joint: grooved with groove coupling, civil work: all related civil work, supports: vendor's scope |  | 12 | Mtr | MONOMER, STYRENE & SOLVENT PUMP
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H1 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 80 mm NB | ms black steel pipe | size: 80 mm NB, thickness: 5.4mm | grade: heavy, material: ms(black steel), standard: IS 1239 Part-1(indian standard), fittings: elbows, fittings: tees, fittings: flanges, fittings: reduces clamps, supports: MS support dash fasteners, coating: two coats of approved primer, coating: two coats of approved paint, joint: grooved with groove coupling, civil work: all related civil work, supports: vendor's scope |  | 36 | Mtr | MONOMER, STYRENE & SOLVENT PUMP
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H2 ¦ FOAM GENERATOR | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 150 NB | gi pipes | size: 150 NB | class: C (heavy class), standard: IS 1239(indian standard), fittings: threaded or grooved, included: elbow, included: tee, included: reducer, included: welding flanges, fixing: clamps to MS brackets/hangers, supports: steel, coating: zinc chromate primer, coating: 2 coats red enamel paint, application: above ground pipes, as per fire authorities requirement |  | 34 | Mtr | MONOMER, STYRENE & SOLVENT PUMP
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H2 ¦ FOAM GENERATOR | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 100 NB | gi pipes | size: 100 NB | class: C (heavy class), standard: IS 1239(indian standard), fittings: threaded or grooved, included: elbow, included: tee, included: reducer, included: welding flanges, fixing: clamps to MS brackets/hangers, supports: steel, coating: zinc chromate primer, coating: 2 coats red enamel paint, application: above ground pipes, as per fire authorities requirement |  | 89 | Mtr | MONOMER, STYRENE & SOLVENT PUMP
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H2 ¦ FOAM GENERATOR | Supply, erection , testing & commissioning of Deluge valve with dry pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch,dry pilot actuator, air filter regulator etc. & manual release unit. Size 150 NB | deluge valve | size: 150 NB | trim assembly: dry pilot, included: strainer, included: drain valve, included: pressure gauge, included: pressure switch, included: dry pilot actuator, included: air filter regulator, included: manual release unit |  | 2 | Nos | MONOMER, STYRENE & SOLVENT PUMP
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H2 ¦ FOAM GENERATOR | Providing & fixing Cast Iron Y Strainer. Size 150 NB | cast iron y strainer | size: 150 NB | material: cast iron |  | 2 | Nos | MONOMER, STYRENE & SOLVENT PUMP
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H2 ¦ FOAM GENERATOR | Supply & fixing of SS-304 FOAM GENERATOR with Minimum flow 120lpm | foam generator |  | material: SS-304(stainless steel 304), minimum flow: 120 lpm |  | 4 | Nos | MONOMER, STYRENE & SOLVENT PUMP
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H2 ¦ FOAM GENERATOR | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. Size 150 NB | gate valve | size: 150 NB | material: cs(carbon steel), standard: API 600, class: 150, included: matching flanges, included: nuts & bolts |  | 6 | Nos | MONOMER, STYRENE & SOLVENT PUMP
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H2 ¦ FOAM GENERATOR | Supply, installation, testing and commissioning of Atmospheric Foam tank vertical type ,manufacturing as per ASME, section-VIII part- I. Tank shall be supplied along with all necessary valves, fittingss & instruments as per Technical data sheet attached with Tender documents. Capacity of 250 ltr. | atmospheric foam tank vertical type | tank capacity: 250 ltr. | manufacturing standard: ASME section-VIII part-I, included: all necessary valves, included: fittings, included: instruments, reference: technical data sheet attached with tender documents |  | 2 | Nos | MONOMER, STYRENE & SOLVENT PUMP
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H2 ¦ FOAM GENERATOR | Supply of AR-AFFF(3%) foam concentrate (PFOS/PFAS free) having sp. Gravity 1.0±.02 g/mlat 20⁰C , pH 7.0-8.5 & viscosity 1200 ±300 cps. | ar-afff foam concentrate |  | concentration: 3%, PFOS/PFAS free, specific gravity: 1.0±.02 g/ml at 20⁰C, pH: 7.0-8.5, viscosity: 1200 ±300 cps | ar-afff foam concentrate | 500 | Ltr | MONOMER, STYRENE & SOLVENT PUMP
H ¦ MONOMER,STYRENE & SOLVENT PUMP ROOM & TANK; H2 ¦ FOAM GENERATOR | Supply, installation, testing and commissioning of Inline Inductor 150NB | inline inductor | size: 150NB |  |  | 2 | Nos | MONOMER, STYRENE & SOLVENT PUMP
| Supply, erection, testing & commissioning of analogue addressable Monitor module | monitor module |  | type: analogue addressable |  | 4 | Nos | MONOMER, STYRENE & SOLVENT PUMP
| Supply, erection, testing & commissioning of IR Detector | ir detector |  |  |  | 4 | Nos | MONOMER, STYRENE & SOLVENT PUMP
| Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. | armoured cabling |  | feature: complete with lugs, laying and termination of both ends |  |  |  | MONOMER, STYRENE & SOLVENT PUMP
| 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cable | size: 2C x 1.5 mm2 | type: loop cable |  | 106 | Mtr | MONOMER, STYRENE & SOLVENT PUMP
| Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable trays |  | feature: for laying all type of cables as indicated above including all necessary structural supports |  | 106 | Mtr | MONOMER, STYRENE & SOLVENT PUMP
I ¦ PAINTS CONTROL LAB I1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 100 mm NB | ms black steel pipe | size: 100 mm NB | thickness: 5.4mm, material: ms(mild steel), grade: heavy, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, civil work: all related civil work and supports of vendor's scope |  | 36 | Mtr | PAINTS CONTROL LAB
I ¦ PAINTS CONTROL LAB I1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 80 mm NB | ms black steel pipe | size: 80 mm NB | thickness: 5.4mm, material: ms(mild steel), grade: heavy, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, civil work: all related civil work and supports of vendor's scope |  | 36 | Mtr | PAINTS CONTROL LAB
I ¦ PAINTS CONTROL LAB I1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 25 mm NB | ms black steel pipe | size: 25 mm NB | thickness: 5.4mm, material: ms(mild steel), grade: heavy, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, civil work: all related civil work and supports of vendor's scope |  | 18 | Mtr | PAINTS CONTROL LAB
I ¦ PAINTS CONTROL LAB I1 ¦ HYDRANT SYSTEM | Supply & installation of swinging type hose reel drum fabricated from 14 SWG CRCA sheets painted with red colour stove paint 2 coats over 1 coat of primer with 30 m long 20 mm dia rubber hose pipe with with SS self closing shut – off nozzle of 5 mm outlet fixed on wall. | hose reel drum | hose length: 30 m, hose diameter: 20 mm, nozzle outlet: 5 mm | type: swinging, fabrication: 14 SWG CRCA sheets, painting: red colour stove paint 2 coats over 1 coat of primer, hose material: rubber, nozzle material: ss(stainless steel), nozzle type: self closing shut-off, mounting: fixed on wall |  | 3 | Nos | PAINTS CONTROL LAB
I ¦ PAINTS CONTROL LAB I1 ¦ HYDRANT SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends Size 25NB | globe valve | size: 25NB | material: bronze, standard: indian standard 778, end connection: screwed |  | 3 | Nos | PAINTS CONTROL LAB
I ¦ PAINTS CONTROL LAB I1 ¦ HYDRANT SYSTEM | Supply & installation of SS oblique type single headed Landing valve with 80 mm inlet and 63 mm outlet SS instantaneous male coupling with rubber cap and chain conforming to IS : 5290 including matching flanges, gasket, nuts and bolts complete. | landing valve | inlet: 80 mm, outlet: 63 mm | material: ss(stainless steel), type: oblique, head: single, coupling: ss instantaneous male, cap: rubber, chain: included, standard: indian standard 5290, accessories: matching flanges, gasket, nuts and bolts |  | 2 | Nos | PAINTS CONTROL LAB
I ¦ PAINTS CONTROL LAB I1 ¦ HYDRANT SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. Size 80 mm NB | butterfly valve | size: 80 mm NB | standard: british standard 5155, type: wafer, accessories: matching flanges, nuts & bolts, fittings: necessary fittings by erection vendor |  | 2 | Nos | PAINTS CONTROL LAB
I ¦ PAINTS CONTROL LAB I1 ¦ HYDRANT SYSTEM | Supply & installation of SS branch pipe with 20 mm nozzle conforming to IS : 903 complete | branch pipe | nozzle: 20 mm | material: ss(stainless steel), standard: indian standard 903 |  | 2 | Nos | PAINTS CONTROL LAB
I ¦ PAINTS CONTROL LAB I1 ¦ HYDRANT SYSTEM | Supply & installation of 63 mm dia rubberized reinforced rubber line hose pipe in 15 m length conforming to IS : 636 Type II ISI marked with gunmetal male and female instantaneous coupling conforming to IS 903 wounded with 18 SWG copper wire complete | rubber line hose pipe | diameter: 63 mm, length: 15 m | type: rubberized reinforced, standard: indian standard 636 type II, certification: ISI, coupling: gunmetal male and female instantaneous, coupling standard: indian standard 903, wire: 18 SWG copper |  | 4 | Nos | PAINTS CONTROL LAB
I ¦ PAINTS CONTROL LAB I1 ¦ HYDRANT SYSTEM | Supply & installation of MS Hose Box of fabricated from 16 SWG CRCA sheet double door with lockable arrangements to accommodate 2 RRL hose of 15 m length and one branch pipe painted white inside and red outside with one key. (750X600X250 mm) | hose box | dimensions: 750X600X250 mm | material: ms(mild steel), fabrication: 16 SWG CRCA sheet, door: double, lockable: yes, capacity: accommodates 2 RRL hose of 15 m length and one branch pipe, painting: white inside and red outside, key: one included |  | 2 | Nos | PAINTS CONTROL LAB
I ¦ PAINTS CONTROL LAB I2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 40 mm NB | ms black steel pipe | size: 40 mm NB | thickness: 5.4mm, material: ms(mild steel), grade: heavy, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, civil work: all related civil work and supports of vendor's scope |  | 18 | Mtr | PAINTS CONTROL LAB
I ¦ PAINTS CONTROL LAB I2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 25 mm NB | ms black steel pipe | size: 25 mm NB | thickness: 5.4mm, material: ms(mild steel), grade: heavy, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, civil work: all related civil work and supports of vendor's scope |  | 54 | Mtr | PAINTS CONTROL LAB
I ¦ PAINTS CONTROL LAB I2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. Size80 mm NB | butterfly valve | size: 80 mm NB | standard: british standard 5155, type: wafer, fittings: matching flanges, nuts & bolts, feature: necessary fittings provided by erection vendor |  | 1 | Nos | PAINTS CONTROL LAB
I ¦ PAINTS CONTROL LAB I2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. Size40 mm NB | butterfly valve | size: 40 mm NB | standard: british standard 5155, type: wafer, fittings: matching flanges, nuts & bolts, feature: necessary fittings provided by erection vendor |  | 1 | Nos | PAINTS CONTROL LAB
I ¦ PAINTS CONTROL LAB I2 ¦ AUTOMATIC SPRINKLER SYSTEM | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts confirming IS:5312(PN16). Size80 mm NB | non return valve | size: 80 mm NB | type: wafer, fittings: matching flanges, nuts & bolts, standard: indian standard 5312(PN16) |  | 1 | Nos | PAINTS CONTROL LAB
I ¦ PAINTS CONTROL LAB I2 ¦ AUTOMATIC SPRINKLER SYSTEM | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts confirming IS:5312(PN16). Size40 mm NB | non return valve | size: 40 mm NB | type: wafer, fittings: matching flanges, nuts & bolts, standard: indian standard 5312(PN16) |  | 1 | Nos | PAINTS CONTROL LAB
I ¦ PAINTS CONTROL LAB I2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & fixing of paddle type Flow Switch | flow switch |  | type: paddle |  | 2 | Nos | PAINTS CONTROL LAB
I ¦ PAINTS CONTROL LAB I2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Fixing of Sprinkler Head Pendent type for K factor-80. Temp rating 68 deg C.UL/FM Approved. | sprinkler head pendent type | k factor: 80 | temperature rating: 68 deg C, certification: UL(underwriters laboratories)/FM(factory mutual) approved |  | 26 | Nos | PAINTS CONTROL LAB
I ¦ PAINTS CONTROL LAB I2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, installation of automatic 25 NB Air Release Valve | air release valve | size: 25 NB | feature: automatic |  | 1 | Nos | PAINTS CONTROL LAB
I ¦ PAINTS CONTROL LAB I2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends Size 40NB | globe valve | size: 40 NB | material: bronze, standard: indian standard 778, ends: screwed |  | 2 | Nos | PAINTS CONTROL LAB
I ¦ PAINTS CONTROL LAB I2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends Size 25NB | globe valve | size: 25 NB | material: bronze, standard: indian standard 778, ends: screwed |  | 2 | Nos | PAINTS CONTROL LAB
I ¦ PAINTS CONTROL LAB I2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Erection and testing of Installation Control Valve complete with trims & gong. Size 100 mm NB | installation control valve | size: 100 mm NB | feature: complete with trims & gong |  | 1 | Nos | PAINTS CONTROL LAB
I ¦ PAINTS CONTROL LAB I2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. Size 100 mm NB | gate valve | size: 100 mm NB | material: cs(carbon steel), standard: api 600, class: 150, fittings: matching flanges, nuts & bolts |  | 1 | Nos | PAINTS CONTROL LAB
I ¦ PAINTS CONTROL LAB I3 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Manual Call point | manual call point |  | type: analogue addressable |  | 3 | Nos | PAINTS CONTROL LAB
I ¦ PAINTS CONTROL LAB I3 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of Hooter cum strobe | hooter cum strobe |  |  |  | 3 | Nos | PAINTS CONTROL LAB
I ¦ PAINTS CONTROL LAB I3 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of Telephone jack. | telephone jack |  |  |  | 2 | Nos | PAINTS CONTROL LAB
I ¦ PAINTS CONTROL LAB I3 ¦ FDA SYSTEM | Supply, erction, testing & commissioning of analogue addressable Control Module | control module |  | type: analogue addressable |  | 2 | Nos | PAINTS CONTROL LAB
I ¦ PAINTS CONTROL LAB I3 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Isolator Module | isolator module |  | type: analogue addressable |  | 2 | Nos | PAINTS CONTROL LAB
I ¦ PAINTS CONTROL LAB I3 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Monitor module | monitor module |  | type: analogue addressable |  | 2 | Nos | PAINTS CONTROL LAB
I ¦ PAINTS CONTROL LAB I3 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cabling | cable size: 2C x 1.5 mm2 | feature: complete with lugs, laying and termination of both ends, cable type: loop cable |  | 125 | Mtr | PAINTS CONTROL LAB
I ¦ PAINTS CONTROL LAB I3 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Power cable) | armoured cabling | cable size: 2C x 1.5 mm2 | feature: complete with lugs, laying and termination of both ends, cable type: power cable |  | 50 | Mtr | PAINTS CONTROL LAB
I ¦ PAINTS CONTROL LAB I3 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 0.5 mm2 Armoured ( Telephone cable) | armoured cabling | cable size: 2C x 0.5 mm2 | feature: complete with lugs, laying and termination of both ends, cable type: telephone cable |  | 20 | Mtr | PAINTS CONTROL LAB
I ¦ PAINTS CONTROL LAB I3 ¦ FDA SYSTEM | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable trays |  | feature: for laying all type of cables as indicated above including all necessary structural supports |  | 131 | Mtr | PAINTS CONTROL LAB
I ¦ PAINTS CONTROL LAB I4 ¦ PA SYSTEM | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | ip based networkable touch screen paging station |  | feature: selection of zones, supervision of system status, setting of scheduled broadcasts, central exchange with stand by CPU, built-in monitoring loudspeaker, goose-neck microphone, LCD touchscreen display, audio input |  | 1 | Nos | PAINTS CONTROL LAB
I ¦ PAINTS CONTROL LAB I4 ¦ PA SYSTEM | Rack Mounted 100 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | power amplifier | power: 100 watt | mounting: rack mounted, feature: battery back up, feature: wattage shall be as per requirement |  | 1 | Nos | PAINTS CONTROL LAB
I ¦ PAINTS CONTROL LAB I4 ¦ PA SYSTEM | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | cable | core: 2C, cross section: 1.5 mm2 | type: multi stranded, shielding: shielded, armor: armoured, insulation: XLPE, conductor: Cu (copper), application: for power & signal |  | 131 | Mtr | PAINTS CONTROL LAB
I ¦ PAINTS CONTROL LAB I4 ¦ PA SYSTEM | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | dvd player |  | feature: features to hook up to amplifiers of PA system for music in the common areas |  | 1 | Nos | PAINTS CONTROL LAB
I ¦ PAINTS CONTROL LAB I4 ¦ PA SYSTEM | Paging Loudspeaker | loudspeaker |  | feature: paging |  | 1 | Nos | PAINTS CONTROL LAB
['J ¦ WATER BASED PLANT', 'J1 ¦ HYDRANT SYSTEM'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 150 mm NB | ms black steel pipe | size: 150 mm NB | material: ms(black steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part-1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, pipe joints: grooved with groove coupling, civil work: all related civil work, supports etc shall be of vendor's scope |  | 12 | Mtr | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J1 ¦ HYDRANT SYSTEM'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 80 mm NB | ms black steel pipe | size: 80 mm NB | material: ms(black steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part-1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, pipe joints: grooved with groove coupling, civil work: all related civil work, supports etc shall be of vendor's scope |  | 24 | Mtr | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J1 ¦ HYDRANT SYSTEM'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 25 mm NB | ms black steel pipe | size: 25 mm NB | material: ms(black steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part-1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, pipe joints: grooved with groove coupling, civil work: all related civil work, supports etc shall be of vendor's scope |  | 6 | Mtr | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J1 ¦ HYDRANT SYSTEM'] | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. Size 150 mm NB | gate valve | size: 150 mm NB | material: cs(carbon steel), standard: api 600, class: 150, flanges: matching, accessories: complete with nuts & bolts |  | 1 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J1 ¦ HYDRANT SYSTEM'] | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts confirming IS:5312(PN16). Size 150 mm NB | non return valve | size: 150 mm NB | type: wafer, flanges: matching, accessories: complete with nuts & bolts, standard: indian standard 5312(pn16) |  | 1 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J1 ¦ HYDRANT SYSTEM'] | Supply & installation of SS oblique type single headed Landing valve with 80 mm inlet and 63 mm outlet SS instantaneous male coupling with rubber cap and chain conforming to IS : 5290 including matching flanges, gasket, nuts and bolts complete. | landing valve | inlet: 80 mm, outlet: 63 mm | material: ss(stainless steel), type: oblique, head: single, coupling: ss instantaneous male, accessories: rubber cap and chain, standard: indian standard 5290, flanges: matching, accessories: gasket, nuts and bolts |  | 4 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J1 ¦ HYDRANT SYSTEM'] | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. Size 80 mm NB | butterfly valve | size: 80 mm NB | standard: british standard 5155, type: wafer, flanges: matching, accessories: complete with nuts & bolts, fittings: necessary fittings shall be provided by erection vendor |  | 4 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J1 ¦ HYDRANT SYSTEM'] | Supply & installation of SS branch pipe with 20 mm nozzle conforming to IS : 903 complete | branch pipe | nozzle: 20 mm | material: ss(stainless steel), standard: indian standard 903 |  | 4 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J1 ¦ HYDRANT SYSTEM'] | Supply & installation of 63 mm dia rubberized reinforced rubber line hose pipe in 15 m length conforming to IS : 636 Type II ISI marked with gunmetal male and female instantaneous coupling conforming to IS 903 wounded with 18 SWG copper wire complete | hose pipe | diameter: 63 mm, length: 15 m | type: rubberized reinforced rubber line, standard: indian standard 636 type ii isi marked, coupling: gunmetal male and female instantaneous, coupling standard: indian standard 903, wire: 18 swg copper wire |  | 8 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J1 ¦ HYDRANT SYSTEM'] | Supply & installation of MS Hose Box of fabricated from 16 SWG CRCA sheet double door with lockable arrangements to accommodate 2 RRL hose of 15 m length and one branch pipe painted white inside and red outside with one key. (750X600X250 mm) | hose box | dimensions: 750X600X250 mm | material: ms(mild steel), fabrication: 16 swg crca sheet, doors: double, lockable arrangements: to accommodate 2 rrl hose of 15 m length and one branch pipe, painting: white inside and red outside, accessories: one key |  | 4 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J1 ¦ HYDRANT SYSTEM'] | Supply & installation of swinging type hose reel drum fabricated from 14 SWG CRCA sheets painted with red colour stove paint 2 coats over 1 coat of primer with 30 m long 20 mm dia rubber hose pipe with with SS self closing shut – off nozzle of 5 mm outlet fixed on wall. | hose reel drum | hose length: 30 m, hose diameter: 20 mm, nozzle outlet: 5 mm | type: swinging, fabrication: 14 swg crca sheets, painting: red colour stove paint 2 coats over 1 coat of primer, hose: rubber, nozzle: ss(self closing shut-off), installation: fixed on wall |  | 4 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J1 ¦ HYDRANT SYSTEM'] | Supply and installation of pressure gauge, 1/2 inch bottom entry, of suitable range with ball valves and other accessories. | pressure gauge | bottom entry: 1/2 inch | range: suitable, accessories: ball valves and other accessories |  | 1 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J1 ¦ HYDRANT SYSTEM'] | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends Size 25NB | globe valve | size: 25NB | material: bronze, standard: indian standard 778, ends: screwed |  | 6 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J2 ¦ AUTOMATIC SPRINKLER SYSTEM'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 150 mm NB | ms black steel pipe | size: 150 mm NB | material: ms(black steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, etc., clamps: reduces clamps, supports: ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved with groove coupling, scope: all related civil work, supports etc of vendor's scope |  | 121 | Mtr | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J2 ¦ AUTOMATIC SPRINKLER SYSTEM'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 100 mm NB | ms black steel pipe | size: 100 mm NB | material: ms(black steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, etc., clamps: reduces clamps, supports: ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved with groove coupling, scope: all related civil work, supports etc of vendor's scope |  | 101 | Mtr | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J2 ¦ AUTOMATIC SPRINKLER SYSTEM'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 80 mm NB | ms black steel pipe | size: 80 mm NB | material: ms(black steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, etc., clamps: reduces clamps, supports: ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved with groove coupling, scope: all related civil work, supports etc of vendor's scope |  | 66 | Mtr | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J2 ¦ AUTOMATIC SPRINKLER SYSTEM'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 65 mm NB | ms black steel pipe | size: 65 mm NB | material: ms(black steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, etc., clamps: reduces clamps, supports: ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved with groove coupling, scope: all related civil work, supports etc of vendor's scope |  | 286 | Mtr | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J2 ¦ AUTOMATIC SPRINKLER SYSTEM'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 50 mm NB | ms black steel pipe | size: 50 mm NB | material: ms(black steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, etc., clamps: reduces clamps, supports: ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved with groove coupling, scope: all related civil work, supports etc of vendor's scope |  | 386 | Mtr | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J2 ¦ AUTOMATIC SPRINKLER SYSTEM'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 40 mm NB | ms black steel pipe | size: 40 mm NB | material: ms(black steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, etc., clamps: reduces clamps, supports: ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved with groove coupling, scope: all related civil work, supports etc of vendor's scope |  | 602 | Mtr | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J2 ¦ AUTOMATIC SPRINKLER SYSTEM'] | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. Size150 mm NB | butterfly valve | size: 150 mm NB | standard: british standard 5155, type: wafer, flanges: matching, fittings: necessary fittings by erection vendor |  | 7 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J2 ¦ AUTOMATIC SPRINKLER SYSTEM'] | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts confirming IS:5312(PN16). Size150 mm NB | non return valve | size: 150 mm NB | type: wafer, flanges: matching, standard: indian standard 5312(PN16) |  | 7 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J2 ¦ AUTOMATIC SPRINKLER SYSTEM'] | Supply & fixing of paddle type Flow Switch | flow switch |  | type: paddle |  | 7 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J2 ¦ AUTOMATIC SPRINKLER SYSTEM'] | Supply,Fixing of Sprinkler Head Pendent type for K factor-160. Temp rating 68 deg C.UL/FM Approved. | sprinkler head pendent type | k factor: 160 | temperature rating: 68 deg C, certification: UL(underwriters laboratories)/FM(factory mutual) approved |  | 540 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J2 ¦ AUTOMATIC SPRINKLER SYSTEM'] | Supply, installation of automatic 25 NB Air Release Valve | air release valve | size: 25 NB | type: automatic |  | 1 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J2 ¦ AUTOMATIC SPRINKLER SYSTEM'] | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends Size 40NB | globe valve | size: 40NB | material: bronze, standard: indian standard 778, ends: screwed |  | 7 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J2 ¦ AUTOMATIC SPRINKLER SYSTEM'] | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends Size 25NB | globe valve | size: 25NB | material: bronze, standard: indian standard 778, ends: screwed |  | 2 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J2 ¦ AUTOMATIC SPRINKLER SYSTEM'] | Supply,Erection and testing of Installation Control Valve complete with trims & gong. a ¦ Size 150 mm NB | installation control valve | size: 150 mm NB | feature: complete with trims & gong |  | 1 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J2 ¦ AUTOMATIC SPRINKLER SYSTEM'] | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. a ¦ Size 150 mm NB | gate valve | size: 150 mm NB | material: cs(carbon steel), standard: API 600, class: 150, feature: matching flanges complete with nuts & bolts |  | 1 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J3 ¦ WATER CURTAIN'] | Supply, erection and testing of heavy grade(class-C) pipes of thickness 5.4mm conforming to IS-1239 including all fittings viz. tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer and structural steels for pipe supports. Hanger support with anchor fasteners and clamps shall be supplied to fix the pipes on ceiling wall etc. including supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners) as per specification. Cutting of floors, walls etc and making it good after erection of pipes shall be of vendor's scope. Necessary painting with 2 coats of primer and 2 coats of synthetic enamel paints to be done and supply of paints shall be with vendor's scope. a ¦ 50 NB | heavy grade pipe | size: 50 NB | grade: class-C, thickness: 5.4mm, standard: IS-1239, fittings: tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer, structural steels for pipe supports, support: hanger support with anchor fasteners and clamps, feature: supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners), feature: cutting of floors, walls etc and making it good after erection, painting: 2 coats of primer and 2 coats of synthetic enamel paints, supply of paints: vendor's scope |  | 56 | Mtr | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J3 ¦ WATER CURTAIN'] | Supply, erection and testing of heavy grade(class-C) pipes of thickness 5.4mm conforming to IS-1239 including all fittings viz. tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer and structural steels for pipe supports. Hanger support with anchor fasteners and clamps shall be supplied to fix the pipes on ceiling wall etc. including supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners) as per specification. Cutting of floors, walls etc and making it good after erection of pipes shall be of vendor's scope. Necessary painting with 2 coats of primer and 2 coats of synthetic enamel paints to be done and supply of paints shall be with vendor's scope. b ¦ 65 NB | heavy grade pipe | size: 65 NB | grade: class-C, thickness: 5.4mm, standard: IS-1239, fittings: tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer, structural steels for pipe supports, support: hanger support with anchor fasteners and clamps, feature: supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners), feature: cutting of floors, walls etc and making it good after erection, painting: 2 coats of primer and 2 coats of synthetic enamel paints, supply of paints: vendor's scope |  | 52 | Mtr | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J3 ¦ WATER CURTAIN'] | Supply, erection and testing of heavy grade(class-C) pipes of thickness 5.4mm conforming to IS-1239 including all fittings viz. tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer and structural steels for pipe supports. Hanger support with anchor fasteners and clamps shall be supplied to fix the pipes on ceiling wall etc. including supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners) as per specification. Cutting of floors, walls etc and making it good after erection of pipes shall be of vendor's scope. Necessary painting with 2 coats of primer and 2 coats of synthetic enamel paints to be done and supply of paints shall be with vendor's scope. c ¦ 80 NB | heavy grade pipe | size: 80 NB | grade: class-C, thickness: 5.4mm, standard: IS-1239, fittings: tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer, structural steels for pipe supports, support: hanger support with anchor fasteners and clamps, feature: supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners), feature: cutting of floors, walls etc and making it good after erection, painting: 2 coats of primer and 2 coats of synthetic enamel paints, supply of paints: vendor's scope |  | 66 | Mtr | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J3 ¦ WATER CURTAIN'] | Supply, erection and testing of heavy grade(class-C) pipes of thickness 5.4mm conforming to IS-1239 including all fittings viz. tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer and structural steels for pipe supports. Hanger support with anchor fasteners and clamps shall be supplied to fix the pipes on ceiling wall etc. including supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners) as per specification. Cutting of floors, walls etc and making it good after erection of pipes shall be of vendor's scope. Necessary painting with 2 coats of primer and 2 coats of synthetic enamel paints to be done and supply of paints shall be with vendor's scope. d ¦ 100 NB | heavy grade pipe | size: 100 NB | grade: class-C, thickness: 5.4mm, standard: IS-1239, fittings: tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer, structural steels for pipe supports, support: hanger support with anchor fasteners and clamps, feature: supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners), feature: cutting of floors, walls etc and making it good after erection, painting: 2 coats of primer and 2 coats of synthetic enamel paints, supply of paints: vendor's scope |  | 36 | Mtr | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J3 ¦ WATER CURTAIN'] | Supply, erection , testing & commissioning of Deluge valve with wet pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 2 way Solenoid Valve, air filter regulator etc. & manual release unit. a ¦ Size 80 NB | deluge valve | size: 80 NB | feature: wet pilot trim assembly, strainer, drain valve, pressure gauge, pressure switch, flame proof 2 way solenoid valve, air filter regulator, manual release unit |  | 1 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J3 ¦ WATER CURTAIN'] | Supply, erection , testing & commissioning of Deluge valve with wet pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 2 way Solenoid Valve, air filter regulator etc. & manual release unit. b ¦ Size 100 NB | deluge valve | size: 100 NB | feature: wet pilot trim assembly, strainer, drain valve, pressure gauge, pressure switch, flame proof 2 way solenoid valve, air filter regulator, manual release unit |  | 3 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J3 ¦ WATER CURTAIN'] | Providing & fixing Cast Iron Y Strainer. a ¦ Size 80 NB | y strainer | size: 80 NB | material: cast iron |  | 1 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J3 ¦ WATER CURTAIN'] | Providing & fixing Cast Iron Y Strainer. b ¦ Size 100 NB | y strainer | size: 100 NB | material: cast iron |  | 3 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J3 ¦ WATER CURTAIN'] | Supply & fixing of SS Water Curtain Nozzle (K>=71)).UL/FM Approved. | water curtain nozzle |  | material: ss(stainless steel), k-factor: >=71, certification: UL(underwriters laboratories), certification: FM(factory mutual) |  | 67 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J3 ¦ WATER CURTAIN'] | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. a ¦ Size 80 NB | gate valve | size: 80 NB | material: cs(carbon steel), standard: API 600, class: 150, feature: matching flanges complete with nuts & bolts |  | 3 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J3 ¦ WATER CURTAIN'] | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. b ¦ Size 100 NB | gate valve | size: 100 NB | material: cs(carbon steel), standard: API 600, class: 150, feature: matching flanges complete with nuts & bolts |  | 9 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J3 ¦ WATER CURTAIN'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. c ¦ 80 mm NB | ms black steel pipe | size: 80 mm NB | grade: heavy, thickness: 5.4mm, standard: IS : 1239 Part -1, fittings: elbows, tees, flanges, etc. reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, pipe joints: grooved with groove coupling, civil work: all related civil work, supports etc shall be of vendor's scope |  | 12 | Mtr | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J4 ¦ FDA SYSTEM'] | Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | multicriteria detector |  | type: analogue addressable |  | 15 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J4 ¦ FDA SYSTEM'] | Supply, erection, testing & commissioning of analogue addressable Manual Call point | manual call point |  | type: analogue addressable |  | 12 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J4 ¦ FDA SYSTEM'] | Supply, erection, testing & commissioning of Hooter cum strobe | hooter cum strobe |  |  |  | 12 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J4 ¦ FDA SYSTEM'] | Supply, erection, testing & commissioning of Telephone jack. | telephone jack |  |  |  | 2 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J4 ¦ FDA SYSTEM'] | Supply, erction, testing & commissioning of analogue addressable Control Module | control module |  | type: analogue addressable |  | 4 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J4 ¦ FDA SYSTEM'] | Supply, erection, testing & commissioning of analogue addressable Isolator Module | isolator module |  | type: analogue addressable |  | 2 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J4 ¦ FDA SYSTEM'] | Supply, erection, testing & commissioning of analogue addressable Monitor module | monitor module |  | type: analogue addressable |  | 2 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J4 ¦ FDA SYSTEM'] | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. a ¦ 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cabling | size: 2C x 1.5 mm2 | type: loop cable, feature: complete with lugs, laying and termination of both ends |  | 572 | Mtr | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J4 ¦ FDA SYSTEM'] | Supply, installation, testing and commissioning of aspiration detector with CMOS imager combined with multiple photodiode for reliable very early warning in a wide range of environments with minimal nuisance alarms. The detector should have 4 pipe inlet and min 100m pipelength support per inlet.The detector should have Smart on-board filter retains dust count and remaining filter life for predictable maintenance& coverage area of min 5000 Sq. | aspiration detector | pipe inlet: 4, pipelength support per inlet: min 100m, coverage area: min 5000 Sq. | imager: CMOS, photodiode: multiple, feature: reliable very early warning in a wide range of environments with minimal nuisance alarms, filter: smart on-board filter retains dust count and remaining filter life for predictable maintenance |  | 7 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J4 ¦ FDA SYSTEM'] | Supply,Installation,Testing & Commissioning of UL/VDS listed CPVC Pipe 25 mm Dia & Pipe Accessories for the Aspiration detection. | cpvc pipe | diameter: 25 mm | standard: UL(underwriters laboratories), standard: VDS, feature: listed, accessories: pipe accessories for the aspiration detection |  | 980 | Mtr | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J4 ¦ FDA SYSTEM'] | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. a ¦ 2C x 1.5 mm2 Armoured ( Power cable) | armoured cabling | size: 2C x 1.5 mm2 | type: power cable, feature: complete with lugs, laying and termination of both ends |  | 706 | Mtr | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J4 ¦ FDA SYSTEM'] | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable trays |  | material: gi(galvanized iron), feature: for laying all type of cables as indicated above, feature: including all necessary structural supports |  | 1158 | Mtr | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J5 ¦ PA SYSTEM'] | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | ip based networkable touch screen paging station |  | feature: selection of zones, feature: supervision of system status, feature: setting of scheduled broadcasts, feature: central exchange with stand by cpu, feature: built-in monitoring loudspeaker, feature: goose-neck microphone, feature: lcd touchscreen display, feature: audio input |  | 1 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J5 ¦ PA SYSTEM'] | 9 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | horn type of speaker | power: 9 W | feature: high efficiency, feature: weather protection ip 65, feature: weatherproof type, feature: suitable for outdoor area |  | 5 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J5 ¦ PA SYSTEM'] | 30 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | horn type of speaker | power: 30 W | feature: high efficiency, feature: weather protection ip 65, feature: weatherproof type, feature: suitable for outdoor area |  | 4 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J5 ¦ PA SYSTEM'] | Rack Mounted 200 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | power amplifier | power: 200 watt | feature: rack mounted, feature: with battery back up, feature: wattage shall be as per requirement |  | 1 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J5 ¦ PA SYSTEM'] | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | xlpe cu cable | size: 2C x 1.5 mm2 | feature: multi stranded, feature: shielded, feature: armoured, feature: for power & signal |  | 350 | Mtr | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J5 ¦ PA SYSTEM'] | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | dvd player |  | feature: features to hook up to amplifiers of pa system for music in the common areas |  | 1 | Nos | WATER BASED PLANT
['J ¦ WATER BASED PLANT', 'J5 ¦ PA SYSTEM'] | Paging Loudspeaker | paging loudspeaker |  |  |  | 1 | Nos | WATER BASED PLANT
K ¦ RAW MATERIAL STORE > K1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 100 mm NB | ms black steel pipe | size: 100 mm NB | grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, scope: all related civil work, supports of vendor's scope |  | 36 | Mtr | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 80 mm NB | ms black steel pipe | size: 80 mm NB | grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, scope: all related civil work, supports of vendor's scope |  | 12 | Mtr | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 25 mm NB | ms black steel pipe | size: 25 mm NB | grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, scope: all related civil work, supports of vendor's scope |  | 6 | Mtr | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K1 ¦ HYDRANT SYSTEM | Supply & installation of SS oblique type single headed Landing valve with 80 mm inlet and 63 mm outlet SS instantaneous male coupling with rubber cap and chain conforming to IS : 5290 including matching flanges, gasket, nuts and bolts complete. | landing valve | inlet: 80 mm, outlet: 63 mm | material: stainless steel, type: oblique, head: single headed, coupling: ss instantaneous male, accessories: rubber cap and chain, standard: indian standard 5290, accessories: matching flanges, gasket, nuts and bolts |  | 4 | Nos | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K1 ¦ HYDRANT SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. Size 80 mm NB | butterfly valve | size: 80 mm NB | standard: british standard 5155, type: wafer, accessories: matching flanges, nuts & bolts, fittings: necessary fittings by erection vendor |  | 4 | Nos | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K1 ¦ HYDRANT SYSTEM | Supply & installation of SS branch pipe with 20 mm nozzle conforming to IS : 903 complete | branch pipe | nozzle: 20 mm | material: stainless steel, standard: indian standard 903 |  | 4 | Nos | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K1 ¦ HYDRANT SYSTEM | Supply & installation of 63 mm dia rubberized reinforced rubber line hose pipe in 15 m length conforming to IS : 636 Type II ISI marked with gunmetal male and female instantaneous coupling conforming to IS 903 wounded with 18 SWG copper wire complete | hose pipe | diameter: 63 mm, length: 15 m | material: rubberized reinforced rubber, standard: indian standard 636 type ii, certification: ISI, coupling: gunmetal male and female instantaneous, coupling standard: indian standard 903, wire: 18 SWG copper |  | 8 | Nos | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K1 ¦ HYDRANT SYSTEM | Supply & installation of MS Hose Box of fabricated from 16 SWG CRCA sheet double door with lockable arrangements to accommodate 2 RRL hose of 15 m length and one branch pipe painted white inside and red outside with one key. (750X600X250 mm). | hose box | sheet thickness: 16 SWG, dimensions: 750X600X250 mm | material: ms, sheet: crca, door: double, lockable: yes, capacity: 2 rrl hose of 15 m length and one branch pipe, paint: white inside and red outside, accessories: one key |  | 4 | Nos | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K1 ¦ HYDRANT SYSTEM | Supply & installation of swinging type hose reel drum fabricated from 14 SWG CRCA sheets painted with red colour stove paint 2 coats over 1 coat of primer with 30 m long 20 mm dia rubber hose pipe with with SS self closing shut – off nozzle of 5 mm outlet fixed on wall. | hose reel drum | sheet thickness: 14 SWG, hose length: 30 m, hose diameter: 20 mm, nozzle outlet: 5 mm | type: swinging, material: crca sheets, paint: red colour stove paint 2 coats over 1 coat of primer, hose: rubber, nozzle: ss self closing shut-off, installation: fixed on wall |  | 4 | Nos | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K1 ¦ HYDRANT SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends Size 25NB | globe valve | size: 25NB | material: bronze, standard: indian standard 778, ends: screwed |  | 4 | Nos | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 50 mm NB | ms black steel pipe | size: 50 mm NB | grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, scope: all related civil work, supports of vendor's scope |  | 293 | Mtr | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 40 mm NB | ms black steel pipe | size: 40 mm NB | grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, scope: all related civil work, supports of vendor's scope |  | 384 | Mtr | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. Size150 mm NB | butterfly valve | size: 150 mm NB | standard: british standard 5155, type: wafer, fittings: matching flanges, nuts & bolts, feature: necessary fittings provided by erection vendor |  | 3 | Nos | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. Size100 mm NB | butterfly valve | size: 100 mm NB | standard: british standard 5155, type: wafer, fittings: matching flanges, nuts & bolts, feature: necessary fittings provided by erection vendor |  | 1 | Nos | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts confirming IS:5312(PN16). Size150 mm NB | non return valve | size: 150 mm NB | type: wafer, fittings: matching flanges, nuts & bolts, standard: indian standard 5312 (PN16) |  | 3 | Nos | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts confirming IS:5312(PN16). Size100 mm NB | non return valve | size: 100 mm NB | type: wafer, fittings: matching flanges, nuts & bolts, standard: indian standard 5312 (PN16) |  | 1 | Nos | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & fixing of paddle type Flow Switch | flow switch |  | type: paddle |  | 4 | Nos | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Fixing of Sprinkler Head Pendent type for K factor-160 Temp rating 68 deg. CUL/FM Approved. | sprinkler head pendent type |  | k factor: 160, temperature rating: 68 deg, certification: cul, certification: fm |  | 316 | Nos | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, installation of automatic 25 NB Air Release Valve | air release valve | size: 25 NB | feature: automatic |  | 1 | Nos | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends Size 40NB | globe valve | size: 40 NB | material: bronze, standard: indian standard 778, end connection: screwed |  | 2 | Nos | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends Size 25NB | globe valve | size: 25 NB | material: bronze, standard: indian standard 778, end connection: screwed |  | 2 | Nos | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Erection and testing of Installation Control Valve complete with trims & gong. Size 150 mm NB | installation control valve | size: 150 mm NB | feature: complete with trims & gong |  | 1 | Nos | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, installation, testing & commissioning of CI Gate Valve as per IS:14846 (PN 16) with matching flanges complete with nuts & bolts. Size 150 mm NB | gate valve | size: 150 mm NB | material: cast iron, standard: indian standard 14846 (PN 16), fittings: matching flanges, nuts & bolts |  | 1 | Nos | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K3 ¦ WATER CURTAIN | Supply, erection and testing of heavy grade(class-C) pipes conforming to IS-1239 / IS-3589 including all fittings viz. tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer and structural steels for pipe supports. Hanger support with anchor fasteners and clamps shall be supplied to fix the pipes on ceiling wall etc. including supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners) as per specification. Cutting of floors, walls etc and making it good after erection of pipes shall be of vendor's scope. Necessary painting with 2 coats of primer and 2 coats of synthetic enamel paints to be done and supply of paints shall be with vendor's scope. 50 NB | pipes | size: 50 NB | grade: heavy (class-c), standard: indian standard 1239 / indian standard 3589, fittings: tees, elbows, reducers, union, flanges, rubber gaskets, gi nuts bolts, washer, structural steels for pipe supports, support: hanger support with anchor fasteners and clamps, installation: supporting/fixing on floor/wall/ceiling with clamps, hangers (using anchor fasteners), scope: cutting of floors, walls and making good after erection, painting: 2 coats of primer and 2 coats of synthetic enamel paints, supply of paints: vendor's scope |  | 18 | Mtr | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K3 ¦ WATER CURTAIN | Supply, erection and testing of heavy grade(class-C) pipes conforming to IS-1239 / IS-3589 including all fittings viz. tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer and structural steels for pipe supports. Hanger support with anchor fasteners and clamps shall be supplied to fix the pipes on ceiling wall etc. including supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners) as per specification. Cutting of floors, walls etc and making it good after erection of pipes shall be of vendor's scope. Necessary painting with 2 coats of primer and 2 coats of synthetic enamel paints to be done and supply of paints shall be with vendor's scope. 65 NB | pipes | size: 65 NB | grade: heavy (class-c), standard: indian standard 1239 / indian standard 3589, fittings: tees, elbows, reducers, union, flanges, rubber gaskets, gi nuts bolts, washer, structural steels for pipe supports, support: hanger support with anchor fasteners and clamps, installation: supporting/fixing on floor/wall/ceiling with clamps, hangers (using anchor fasteners), scope: cutting of floors, walls and making good after erection, painting: 2 coats of primer and 2 coats of synthetic enamel paints, supply of paints: vendor's scope |  | 18 | Mtr | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K3 ¦ WATER CURTAIN | Supply, erection and testing of heavy grade(class-C) pipes conforming to IS-1239 / IS-3589 including all fittings viz. tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer and structural steels for pipe supports. Hanger support with anchor fasteners and clamps shall be supplied to fix the pipes on ceiling wall etc. including supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners) as per specification. Cutting of floors, walls etc and making it good after erection of pipes shall be of vendor's scope. Necessary painting with 2 coats of primer and 2 coats of synthetic enamel paints to be done and supply of paints shall be with vendor's scope. 80 NB | pipes | size: 80 NB | grade: heavy (class-c), standard: indian standard 1239 / indian standard 3589, fittings: tees, elbows, reducers, union, flanges, rubber gaskets, gi nuts bolts, washer, structural steels for pipe supports, support: hanger support with anchor fasteners and clamps, installation: supporting/fixing on floor/wall/ceiling with clamps, hangers (using anchor fasteners), scope: cutting of floors, walls and making good after erection, painting: 2 coats of primer and 2 coats of synthetic enamel paints, supply of paints: vendor's scope |  | 16 | Mtr | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K3 ¦ WATER CURTAIN | Supply, erection , testing & commissioning of Deluge valve with wet pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 2 way Solenoid Valve, air filter regulator etc. & manual release unit. Size 80 NB | deluge valve | size: 80 NB | trim assembly: wet pilot, fittings: strainer, drain valve, pressure gauge, pressure switch, solenoid valve (flame proof, 2 way), air filter regulator, release unit: manual |  | 2 | Nos | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K3 ¦ WATER CURTAIN | Providing & fixing Cast Iron Y Strainer. Size 80 NB | y strainer | size: 80 NB | material: cast iron |  | 2 | Nos | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K3 ¦ WATER CURTAIN | Supply & fixing of SS Water Curtain Nozzle (K>=71)).UL/FM Approved. | water curtain nozzle |  | material: ss(stainless steel), approval: ul(underwriters laboratories) / fm(factory mutual), k-factor: >=71 |  | 20 | Nos | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K3 ¦ WATER CURTAIN | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. Size 80 NB | gate valve | size: 80 NB | material: cs(carbon steel), standard: api 600, class: 150, flanges: matching, fittings: nuts & bolts |  | 6 | Nos | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K3 ¦ WATER CURTAIN | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 150 mm NB | ms black steel pipe | size: 150 mm NB, thickness: 5.4mm | grade: heavy, standard: indian standard 1239 part-1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved with groove coupling, scope: all related civil work, supports vendor's scope |  | 18 | Mtr | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K3 ¦ WATER CURTAIN | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 100 mm NB | ms black steel pipe | size: 100 mm NB, thickness: 5.4mm | grade: heavy, standard: indian standard 1239 part-1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved with groove coupling, scope: all related civil work, supports vendor's scope |  | 24 | Mtr | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K3 ¦ WATER CURTAIN | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 80 mm NB | ms black steel pipe | size: 80 mm NB, thickness: 5.4mm | grade: heavy, standard: indian standard 1239 part-1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joints: grooved with groove coupling, scope: all related civil work, supports vendor's scope |  | 12 | Mtr | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K4 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | multicriteria detector |  | type: analogue addressable |  | 89 | Nos | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K4 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Manual Call point | manual call point |  | type: analogue addressable |  | 7 | Nos | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K4 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of Hooter cum strobe | hooter cum strobe |  |  |  | 7 | Nos | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K4 ¦ FDA SYSTEM | Supply, erction, testing & commissioning of analogue addressable Control Module | control module |  | type: analogue addressable |  | 3 | Nos | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K4 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Isolator Module | isolator module |  | type: analogue addressable |  | 2 | Nos | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K4 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Monitor module | monitor module |  | type: analogue addressable |  | 2 | Nos | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K4 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cabling | configuration: 2C x 1.5 mm2 | type: armoured, cable type: loop |  | 754 | Mtr | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K4 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Power cable) | armoured cabling | configuration: 2C x 1.5 mm2 | type: armoured, cable type: power |  | 297 | Mtr | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K4 ¦ FDA SYSTEM | Providing & fixing FRLS CABLING complete with lugs, laying and termination of both ends. 2C x 0.5 mm2 Armoured ( Telephone cable) | frls cabling | configuration: 2C x 0.5 mm2 | type: armoured, cable type: telephone |  | 20 | Mtr | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K4 ¦ FDA SYSTEM | Supply, installation, testing and commissioning of aspiration detector with CMOS imager combined with multiple photodiode for reliable very early warning in a wide range of environments with minimal nuisance alarms. The detector should have 4 pipe inlet and min 100m pipelength support per inlet.The detector should have Smart on-board filter retains dust count and remaining filter life for predictable maintenance& coverage area of min 5000 Sq. | aspiration detector | pipe inlet: 4, pipelength support per inlet: min 100m, coverage area: min 5000 Sq. | imager: CMOS, sensor: multiple photodiode, feature: very early warning, feature: minimal nuisance alarms, feature: smart on-board filter retains dust count and remaining filter life for predictable maintenance |  | 6 | Nos | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K4 ¦ FDA SYSTEM | Supply,Installation,Testing & Commissioning of UL/VDS listed CPVC Pipe 25 mm Dia & Pipe Accessories for the Aspiration detection. | cpvc pipe | diameter: 25 mm | certification: UL(underwriters laboratories), certification: VDS, application: aspiration detection |  | 441 | Mtr | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K4 ¦ FDA SYSTEM | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable trays |  | material: gi(galvanized iron), application: laying all type of cables, feature: including all necessary structural supports |  | 754 | Mtr | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K5 ¦ PA SYSTEM | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | paging station |  | type: IP based networkable, feature: touch screen, feature: selection of zones, feature: supervision of system status, feature: scheduled broadcasts, feature: central exchange with stand by CPU, feature: built-in monitoring loudspeaker, feature: goose-neck microphone, feature: LCD touchscreen display, feature: audio input |  | 1 | Nos | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K5 ¦ PA SYSTEM | 30 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | horn speaker | power: 30 W | efficiency: high, protection: IP 65, feature: weatherproof type, application: suitable for outdoor area |  | 8 | Nos | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K5 ¦ PA SYSTEM | 15 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | horn speaker | power: 15 W | efficiency: high, protection: IP 65, feature: weatherproof type, application: suitable for outdoor area |  | 1 | Nos | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K5 ¦ PA SYSTEM | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | cable | core: 2C, cross section: 1.5 mm2 | type: multi stranded, shielding: shielded, armor: armoured, insulation: XLPE, conductor: Cu (copper), application: power & signal |  | 250 | Mtr | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K5 ¦ PA SYSTEM | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | dvd player |  | feature: features to hook up to amplifiers of PA system for music in the common areas |  | 1 | Nos | RAW MATERIAL STORE
K ¦ RAW MATERIAL STORE > K5 ¦ PA SYSTEM | Paging Loudspeaker | loudspeaker |  | type: paging |  | 1 | Nos | RAW MATERIAL STORE
L ¦ COLORANT STORE; L1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 150 mm NB | ms black steel pipe | size: 150 mm NB | material: ms(mild steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint: grooved with groove coupling, scope: all related civil work, supports etc of vendor's scope |  | 36 | Mtr | COLORANT STORE
L ¦ COLORANT STORE; L1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 80 mm NB | ms black steel pipe | size: 80 mm NB | material: ms(mild steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint: grooved with groove coupling, scope: all related civil work, supports etc of vendor's scope |  | 12 | Mtr | COLORANT STORE
L ¦ COLORANT STORE; L1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 25 mm NB | ms black steel pipe | size: 25 mm NB | material: ms(mild steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint: grooved with groove coupling, scope: all related civil work, supports etc of vendor's scope |  | 6 | Mtr | COLORANT STORE
L ¦ COLORANT STORE; L1 ¦ HYDRANT SYSTEM | Supply & installation of SS oblique type single headed Landing valve with 80 mm inlet and 63 mm outlet SS instantaneous male coupling with rubber cap and chain conforming to IS : 5290 including matching flanges, gasket, nuts and bolts complete. | landing valve | inlet: 80 mm, outlet: 63 mm | material: ss(stainless steel), type: oblique, head: single, coupling: ss instantaneous male, accessory: rubber cap and chain, standard: indian standard 5290, accessories: matching flanges, gasket, nuts and bolts |  | 8 | Nos | COLORANT STORE
L ¦ COLORANT STORE; L1 ¦ HYDRANT SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. Size 80 mm NB | butterfly valve | size: 80 mm NB | standard: british standard 5155, type: wafer, accessories: matching flanges, nuts & bolts, fittings: necessary fittings by erection vendor |  | 8 | Nos | COLORANT STORE
L ¦ COLORANT STORE; L1 ¦ HYDRANT SYSTEM | Supply & installation of SS branch pipe with 20 mm nozzle conforming to IS : 903 complete | branch pipe | nozzle: 20 mm | material: ss(stainless steel), standard: indian standard 903 |  | 8 | Nos | COLORANT STORE
L ¦ COLORANT STORE; L1 ¦ HYDRANT SYSTEM | Supply & installation of 63 mm dia rubberized reinforced rubber line hose pipe in 15 m length conforming to IS : 636 Type II ISI marked with gunmetal male and female instantaneous coupling conforming to IS 903 wounded with 18 SWG copper wire complete | hose pipe | diameter: 63 mm, length: 15 m | material: rubberized reinforced rubber, standard: indian standard 636 type ii, certification: ISI, coupling: gunmetal male and female instantaneous, coupling standard: indian standard 903, wire: 18 SWG copper |  | 16 | Nos | COLORANT STORE
L ¦ COLORANT STORE; L1 ¦ HYDRANT SYSTEM | Supply & installation of MS Hose Box of fabricated from 16 SWG CRCA sheet double door with lockable arrangements to accommodate 2 RRL hose of 15 m length and one branch pipe painted white inside and red outside with one key. (750X600X250 mm) | hose box | dimensions: 750X600X250 mm | material: ms(mild steel), sheet: 16 SWG CRCA, door: double, lockable: yes, capacity: 2 RRL hose of 15 m length and one branch pipe, paint: white inside and red outside, accessory: one key |  | 8 | Nos | COLORANT STORE
L ¦ COLORANT STORE; L1 ¦ HYDRANT SYSTEM | Supply & installation of swinging type hose reel drum fabricated from 14 SWG CRCA sheets painted with red colour stove paint 2 coats over 1 coat of primer with 30 m long 20 mm dia rubber hose pipe with with SS self closing shut – off nozzle of 5 mm outlet fixed on wall. | hose reel drum | hose length: 30 m, hose diameter: 20 mm, nozzle outlet: 5 mm | type: swinging, material: 14 SWG CRCA sheets, paint: red colour stove paint 2 coats over 1 coat of primer, hose: rubber, nozzle: ss(stainless steel) self closing shut-off, installation: fixed on wall |  | 8 | Nos | COLORANT STORE
L ¦ COLORANT STORE; L1 ¦ HYDRANT SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends Size 25NB | globe valve | size: 25NB | material: bronze, standard: indian standard 778, ends: screwed |  | 4 | Nos | COLORANT STORE
L ¦ COLORANT STORE; L1 ¦ HYDRANT SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends Size 40NB | globe valve | size: 40NB | material: bronze, standard: indian standard 778, ends: screwed |  | 8 | Nos | COLORANT STORE
L ¦ COLORANT STORE; L2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | multicriteria detector |  | type: analogue addressable |  | 141 | Nos | COLORANT STORE
L ¦ COLORANT STORE; L2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of Hooter cum strobe | hooter cum strobe |  |  |  | 14 | Nos | COLORANT STORE
L ¦ COLORANT STORE; L2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of Telephone jack. | telephone jack |  |  |  | 8 | Nos | COLORANT STORE
L ¦ COLORANT STORE; L2 ¦ FDA SYSTEM | Supply, erction, testing & commissioning of analogue addressable Control Module | control module |  | type: analogue addressable |  | 5 | Nos | COLORANT STORE
L ¦ COLORANT STORE; L2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Isolator Module | isolator module |  | type: analogue addressable |  | 4 | Nos | COLORANT STORE
L ¦ COLORANT STORE; L2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Monitor module | monitor module |  | type: analogue addressable |  | 4 | Nos | COLORANT STORE
L ¦ COLORANT STORE; L2 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. a ¦ 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cabling | core: 2C, cross-sectional area: 1.5 mm2 | type: armoured, cable type: loop |  | 1170 | Mtr | COLORANT STORE
L ¦ COLORANT STORE; L2 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. a ¦ 2C x 1.5 mm2 Armoured ( Power cable) | armoured cabling | core: 2C, cross-sectional area: 1.5 mm2 | type: armoured, cable type: power |  | 401 | Mtr | COLORANT STORE
L ¦ COLORANT STORE; L2 ¦ FDA SYSTEM | Providing & fixing FRLS CABLING complete with lugs, laying and termination of both ends. a ¦ 2C x 0.5 mm2 Armoured ( Telephone cable) | frls cabling | core: 2C, cross-sectional area: 0.5 mm2 | type: armoured, cable type: telephone, feature: frls (flame retardant low smoke) |  | 327 | Mtr | COLORANT STORE
L ¦ COLORANT STORE; L2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of 6 Watt Ceiling mounted Speakers | ceiling mounted speakers | power: 6 Watt |  |  | 80 | Nos | COLORANT STORE
L ¦ COLORANT STORE; L2 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. a ¦ 2C x 1.5 mm2 Armoured ( Speaker cable) | armoured cabling | core: 2C, cross-sectional area: 1.5 mm2 | type: armoured, cable type: speaker |  | 1027 | Mtr | COLORANT STORE
L ¦ COLORANT STORE; L2 ¦ FDA SYSTEM | Providing & fixing 600Watt Amplifier with necessary accessories. | amplifier | power: 600 Watt | feature: with necessary accessories |  | 1 | Nos | COLORANT STORE
L ¦ COLORANT STORE; L2 ¦ FDA SYSTEM | Supply, installation, testing and commissioning of aspiration detector with CMOS imager combined with multiple photodiode for reliable very early warning in a wide range of environments with minimal nuisance alarms. The detector should have 4 pipe inlet and min 100m pipelength support per inlet.The detector should have Smart on-board filter retains dust count and remaining filter life for predictable maintenance& coverage area of min 5000 Sq. | aspiration detector | pipe inlet: 4, pipelength support per inlet: min 100m, coverage area: min 5000 Sq. | imager: CMOS, feature: combined with multiple photodiode, feature: very early warning, feature: minimal nuisance alarms, feature: smart on-board filter retains dust count and remaining filter life for predictable maintenance |  | 4 | Nos | COLORANT STORE
L ¦ COLORANT STORE; L2 ¦ FDA SYSTEM | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable trays |  | feature: for laying all type of cables, feature: including all necessary structural supports |  | 1170 | Mtr | COLORANT STORE
L ¦ COLORANT STORE; L3 ¦ PA SYSTEM | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | ip based networkable touch screen paging station |  | feature: selection of zones, feature: supervision of system status, feature: setting of scheduled broadcasts, feature: central exchange with stand by CPU, feature: built-in monitoring loudspeaker, feature: goose-neck microphone, feature: LCD touchscreen display, feature: audio input |  | 1 | Nos | COLORANT STORE
L ¦ COLORANT STORE; L3 ¦ PA SYSTEM | 30 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | horn type speaker | power: 30 W | feature: high efficiency, feature: weather protection, protection: IP 65, feature: weatherproof type, application: suitable for outdoor area |  | 8 | Nos | COLORANT STORE
L ¦ COLORANT STORE; L3 ¦ PA SYSTEM | 9 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | horn type speaker | power: 9 W | feature: high efficiency, feature: weather protection, protection: IP 65, feature: weatherproof type, application: suitable for outdoor area |  | 1 | Nos | COLORANT STORE
L ¦ COLORANT STORE; L3 ¦ PA SYSTEM | 6 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | horn type speaker | power: 6 W | feature: high efficiency, feature: weather protection, protection: IP 65, feature: weatherproof type, application: suitable for outdoor area |  | 23 | Nos | COLORANT STORE
L ¦ COLORANT STORE; L3 ¦ PA SYSTEM | Rack Mounted 400 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | power amplifier | power: 400 watt | feature: rack mounted, feature: with battery back up, feature: wattage shall be as per requirement |  | 1 | Nos | COLORANT STORE
L ¦ COLORANT STORE; L3 ¦ PA SYSTEM | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | xlpe cu cable | conductor: 2C x 1.5 mm2 | feature: multi stranded, feature: shielded, feature: armoured, application: for power & signal |  | 541 | Mtr | COLORANT STORE
L ¦ COLORANT STORE; L3 ¦ PA SYSTEM | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | dvd player |  | feature: features to hook up to amplifiers of PA system, application: for music in the common areas |  | 1 | Nos | COLORANT STORE
L ¦ COLORANT STORE; L3 ¦ PA SYSTEM | Paging Loudspeaker | paging loudspeaker |  |  |  | 1 | Nos | COLORANT STORE
['M ¦ SOFA TANK', 'M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM'] | Supply, erection , testing & commissioning of Deluge valve with wet pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 3/2 way Solenoid Valve, air filter regulator etc. & manual release unit. The valve shall be electro-pneumatic type. | deluge valve |  | trim assembly: wet pilot, included: strainer, drain valve, pressure gauge, pressure switch, solenoid valve: flame proof 3/2 way, air filter regulator: included, manual release unit: included, type: electro-pneumatic |  |  |  | SOFA TANK
['M ¦ SOFA TANK', 'M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM'] | 150 mm NB | deluge valve | size: 150 mm NB |  |  | 1 | Nos | SOFA TANK
['M ¦ SOFA TANK', 'M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM'] | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. | gate valve |  | material: cs(carbon steel), standard: API 600, class: 150, flanges: matching, included: nuts & bolts |  |  |  | SOFA TANK
['M ¦ SOFA TANK', 'M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM'] | 150 mm NB | gate valve | size: 150 mm NB |  |  | 3 | Nos | SOFA TANK
['M ¦ SOFA TANK', 'M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM'] | Supply, installation, testing of Y- Stainer. | y strainer | [5 empty] | SOFA TANK
['M ¦ SOFA TANK', 'M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM'] | 150 mm NB | y strainer | size: 150 mm NB |  |  | 1 | Nos | SOFA TANK
['M ¦ SOFA TANK', 'M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM'] | Supply,installation and commissioning of UL/FM approved Medium Velocity Water Spray Nozzle | medium velocity water spray nozzle |  | certification: UL(underwriters laboratories)/FM(factory mutual) |  |  |  | SOFA TANK
['M ¦ SOFA TANK', 'M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM'] | MVWS nozzle K factor 18, spray angle 100⁰ | medium velocity water spray nozzle | K factor: 18, spray angle: 100⁰ |  | mvws nozzle | 66 | Nos | SOFA TANK
['M ¦ SOFA TANK', 'M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM'] | Supply,installation and commissioning of UL/FM approved Quartzoid Bulb Detector for K factor-80. Temp rating 68 deg C | quartzoid bulb detector | K factor: 80, temperature rating: 68 deg C | certification: UL(underwriters laboratories)/FM(factory mutual) |  | 66 | Nos | SOFA TANK
['M ¦ SOFA TANK', 'M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM'] | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications | gi "c" class pipes |  | class: heavy, standard: IS 1239, fittings: threaded or grooved, included: elbow, tee, reducer, welding flanges, clamps, ms(mild steel) brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, application: above ground pipes, as per fire authorities requirement |  |  |  | SOFA TANK
['M ¦ SOFA TANK', 'M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM'] | 150 NB | gi "c" class pipes | size: 150 NB |  |  | 24 | Mtr | SOFA TANK
['M ¦ SOFA TANK', 'M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM'] | 100 NB | gi "c" class pipes | size: 100 NB |  |  | 24 | Mtr | SOFA TANK
['M ¦ SOFA TANK', 'M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM'] | 80 NB | gi "c" class pipes | size: 80 NB |  |  | 30 | Mtr | SOFA TANK
['M ¦ SOFA TANK', 'M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM'] | 65 NB | gi "c" class pipes | size: 65 NB |  |  | 60 | Mtr | SOFA TANK
['M ¦ SOFA TANK', 'M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM'] | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. | ms black steel pipe |  | material: ms(mild steel), finish: black, grade: heavy, thickness: 5.4mm, standard: IS 1239 Part-1, fittings: elbows, tees, flanges, reducers, clamps, ms support, dash fasteners, painting: two coats approved primer, two coats approved paint, joints: grooved with groove coupling, civil work: included |  |  |  | SOFA TANK
['M ¦ SOFA TANK', 'M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM'] | 150 NB | ms black steel pipe | size: 150 NB |  |  | 36 | Mtr | SOFA TANK
['M ¦ SOFA TANK', 'M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM'] | 25 NB | ms black steel pipe | size: 25 NB |  |  | 218 | Mtr | SOFA TANK
['M ¦ SOFA TANK', 'M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM'] | Supply, erction, testing & commissioning of analogue addressable Control Module | analogue addressable control module |  |  |  | 1 | Nos | SOFA TANK
['M ¦ SOFA TANK', 'M2 ¦ FOAM GENERATOR'] | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications; 150 NB | gi c class pipes | size: 150 NB | class: heavy class, standard: indian standard 1239, fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, fixing: clamps to ms(mild steel) brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, location: above ground, feature: complete as per specifications |  | 66 | Mtr | SOFA TANK
['M ¦ SOFA TANK', 'M2 ¦ FOAM GENERATOR'] | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications; 100 NB | gi c class pipes | size: 100 NB | class: heavy class, standard: indian standard 1239, fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, fixing: clamps to ms(mild steel) brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, location: above ground, feature: complete as per specifications |  | 140 | Mtr | SOFA TANK
['M ¦ SOFA TANK', 'M2 ¦ FOAM GENERATOR'] | Supply, erection , testing & commissioning of Deluge valve with dry pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch,dry pilot actuator, air filter regulator etc. & manual release unit.; Size 150 NB | deluge valve | size: 150 NB | trim assembly: dry pilot, fitted with: strainer, drain valve, pressure gauge, pressure switch, dry pilot actuator, air filter regulator, manual release unit: included |  | 4 | Nos | SOFA TANK
['M ¦ SOFA TANK', 'M2 ¦ FOAM GENERATOR'] | Providing & fixing Cast Iron Y Strainer.; Size 150 NB | y strainer | size: 150 NB | material: cast iron |  | 4 | Nos | SOFA TANK
['M ¦ SOFA TANK', 'M2 ¦ FOAM GENERATOR'] | Supply & fixing of SS-304 FOAM GENERATOR with Minimum flow 120lpm | foam generator |  | material: ss-304(stainless steel 304), minimum flow: 120 lpm |  | 8 | Nos | SOFA TANK
['M ¦ SOFA TANK', 'M2 ¦ FOAM GENERATOR'] | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts.; Size 150 NB | gate valve | size: 150 NB | material: cs(carbon steel), standard: api 600, class: 150, flanges: matching, included: nuts & bolts |  | 12 | Nos | SOFA TANK
['M ¦ SOFA TANK', 'M2 ¦ FOAM GENERATOR'] | Supply, installation, testing and commissioning of Atmospheric Foam tank vertical type ,manufacturing as per ASME, section-VIII part- I. Tank shall be supplied along with all necessary valves, fittingss & instruments as per Technical data sheet attached with Tender documents.; Capacity of 250 ltr. | atmospheric foam tank | capacity: 250 ltr. | type: vertical, manufacturing standard: asme section-viii part-i, included: all necessary valves, fittings & instruments, reference: technical data sheet attached with tender documents |  | 4 | Nos | SOFA TANK
['M ¦ SOFA TANK', 'M2 ¦ FOAM GENERATOR'] | Supply of AR-AFFF(3%) foam concentrate (PFOS/PFAS free) having sp. Gravity 1.0±.02 g/mlat 20⁰C , pH 7.0-8.5 & viscosity 1200 ±300 cps. | ar-afff foam concentrate |  | concentration: 3%, feature: pfos/pfas free, specific gravity: 1.0±.02 g/ml at 20⁰c, ph: 7.0-8.5, viscosity: 1200 ±300 cps | ar-afff foam concentrate | 1000 | Ltr | SOFA TANK
['M ¦ SOFA TANK', 'M2 ¦ FOAM GENERATOR'] | Supply, installation, testing and commissioning of Inline Inductor; 150NB | inline inductor | size: 150NB |  |  | 4 | Nos | SOFA TANK
['M ¦ SOFA TANK', 'M3 ¦ FDA SYSTEM'] | Supply, erection, testing & commissioning of IR Detector | ir detector |  |  |  | 5 | Nos | SOFA TANK
['M ¦ SOFA TANK', 'M3 ¦ FDA SYSTEM'] | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. a ¦ 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cabling | cable: 2C x 1.5 mm2 | feature: complete with lugs, laying and termination of both ends, type: armoured, type: loop cable |  | 120 | Mtr | SOFA TANK
['M ¦ SOFA TANK', 'M3 ¦ FDA SYSTEM'] | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable trays |  | material: gi(galvanized iron), feature: for laying all type of cables as indicated above, feature: including all necessary structural supports |  | 120 | Mtr | SOFA TANK
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, erection , testing & commissioning of Deluge valve with wet pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 3/2 way Solenoid Valve, air filter regulator etc. & manual release unit. The valve shall be electro-pneumatic type. | deluge valve |  | trim assembly: wet pilot, included: strainer, included: drain valve, included: pressure gauge, included: pressure switch, included: flame proof 3/2 way solenoid valve, included: air filter regulator, included: manual release unit, type: electro-pneumatic |  |  |  | DEG & MEG TANK
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | 150 mm NB | deluge valve | size: 150 mm NB |  |  | 1 | Nos | DEG & MEG TANK
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. | gate valve |  | material: cs(carbon steel), standard: API 600, class: 150, included: matching flanges, included: nuts & bolts |  |  |  | DEG & MEG TANK
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | 150 mm NB | gate valve | size: 150 mm NB |  |  | 3 | Nos | DEG & MEG TANK
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, installation, testing of Y- Stainer | y-stainer | [5 empty] | DEG & MEG TANK
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | 150 mm NB | y-stainer | size: 150 mm NB |  |  | 1 | Nos | DEG & MEG TANK
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply,installation and commissioning of UL/FM approved Medium Velocity Water Spray Nozzle | medium velocity water spray nozzle |  | certification: UL(underwriters laboratories), certification: FM(factory mutual) |  |  |  | DEG & MEG TANK
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | MVWS nozzle K factor 18, spray angle 100⁰ | medium velocity water spray nozzle |  | K factor: 18, spray angle: 100⁰ |  | 90 | Nos | DEG & MEG TANK
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply,installation and commissioning of UL/FM approved Quartzoid Bulb Detector for K factor-80. Temp rating 68 deg C | quartzoid bulb detector |  | certification: UL(underwriters laboratories), certification: FM(factory mutual), K factor: 80, temperature rating: 68 deg C |  | 90 | Nos | DEG & MEG TANK
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications | gi "c" class pipes |  | class: heavy, standard: IS 1239, fittings: threaded or grooved, included: elbow, included: tee, included: reducer, included: welding flanges, included: clamps, included: MS brackets/hangers, included: steel supports, primer: zinc chromate, paint: 2 coats red enamel, application: above ground pipes, as per fire authorities requirement |  |  |  | DEG & MEG TANK
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | 150 NB | gi "c" class pipes | size: 150 NB |  |  | 12 | Mtr | DEG & MEG TANK
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | 100 NB | gi "c" class pipes | size: 100 NB |  |  | 14 | Mtr | DEG & MEG TANK
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | 80 NB | gi "c" class pipes | size: 80 NB |  |  | 64 | Mtr | DEG & MEG TANK
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | 65 NB | gi "c" class pipes | size: 65 NB |  |  | 52 | Mtr | DEG & MEG TANK
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. | ms black steel pipe |  | grade: heavy, thickness: 5.4mm, standard: IS 1239 Part-1, fittings: elbows, fittings: tees, fittings: flanges, fittings: reducers, fittings: clamps, fittings: MS support dash fasteners, paint: two coats approved primer, paint: two coats approved paint, pipe joints: grooved with groove coupling, civil work: vendor's scope |  |  |  | DEG & MEG TANK
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | 150 mm NB | ms black steel pipe | size: 150 mm NB |  |  | 24 | Mtr | DEG & MEG TANK
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | 25 NB | ms black steel pipe | size: 25 NB |  |  | 146 | Mtr | DEG & MEG TANK
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, erction, testing & commissioning of analogue addressable Control Module | analogue addressable control module |  |  |  | 1 | Nos | DEG & MEG TANK
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, erction, testing & commissioning of analogue addressable Monitor Module | analogue addressable monitor module |  |  |  | 1 | Nos | DEG & MEG TANK
N ¦ DEG & MEG TANK > N1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable trays |  | feature: for laying all type of cables, feature: including all necessary structural supports |  | 24 | Mtr | DEG & MEG TANK
N ¦ DEG & MEG TANK > N2 ¦ FOAM GENERATOR | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications a ¦ 150 NB | gi pipe | size: 150 NB | class: c class (heavy class), standard: IS 1239 (indian standard 1239), fittings: threaded or grooved, fittings: elbow, tee, reducer, welding flanges, fixing: clamps to ms brackets/hangers, supports: steel, coating: zinc chromate primer, coating: 2 coats red enamel paint, requirement: as per fire authorities, application: above ground pipes |  | 12 | Mtr | DEG & MEG TANK
N ¦ DEG & MEG TANK > N2 ¦ FOAM GENERATOR | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications b ¦ 100 NB | gi pipe | size: 100 NB | class: c class (heavy class), standard: IS 1239 (indian standard 1239), fittings: threaded or grooved, fittings: elbow, tee, reducer, welding flanges, fixing: clamps to ms brackets/hangers, supports: steel, coating: zinc chromate primer, coating: 2 coats red enamel paint, requirement: as per fire authorities, application: above ground pipes |  | 42 | Mtr | DEG & MEG TANK
N ¦ DEG & MEG TANK > N2 ¦ FOAM GENERATOR | Supply, erection , testing & commissioning of Deluge valve with dry pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch,dry pilot actuator, air filter regulator etc. & manual release unit. a ¦ Size 150 NB | deluge valve | size: 150 NB | trim assembly: dry pilot, fitted with: strainer, drain valve, pressure gauge, pressure switch, dry pilot actuator, air filter regulator, manual release unit |  | 1 | Nos | DEG & MEG TANK
N ¦ DEG & MEG TANK > N2 ¦ FOAM GENERATOR | Providing & fixing Cast Iron Y Strainer. a ¦ Size 150 NB | y strainer | size: 150 NB | material: cast iron |  | 1 | Nos | DEG & MEG TANK
N ¦ DEG & MEG TANK > N2 ¦ FOAM GENERATOR | Supply & fixing of SS-304 FOAM GENERATOR with Minimum flow 120lpm | foam generator | minimum flow: 120 lpm | material: ss-304 (stainless steel 304) |  | 2 | Nos | DEG & MEG TANK
N ¦ DEG & MEG TANK > N2 ¦ FOAM GENERATOR | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. a ¦ Size 150 NB | gate valve | size: 150 NB | material: cs (carbon steel), standard: API 600, class: 150, flanges: matching, complete with: nuts & bolts |  | 3 | Nos | DEG & MEG TANK
N ¦ DEG & MEG TANK > N2 ¦ FOAM GENERATOR | Supply, installation, testing and commissioning of Atmospheric Foam tank vertical type ,manufacturing as per ASME, section-VIII part- I. Tank shall be supplied along with all necessary valves, fittingss & instruments as per Technical data sheet attached with Tender documents. a ¦ Capacity of 250 ltr. | atmospheric foam tank vertical type | capacity: 250 ltr. | manufacturing standard: ASME section-VIII part-I, supplied with: all necessary valves, fittings & instruments, reference: technical data sheet attached with tender documents |  | 1 | Nos | DEG & MEG TANK
N ¦ DEG & MEG TANK > N2 ¦ FOAM GENERATOR | Supply of AR-AFFF(3%) foam concentrate (PFOS/PFAS free) having sp. Gravity 1.0±.02 g/mlat 20⁰C , pH 7.0-8.5 & viscosity 1200 ±300 cps. | ar-afff foam concentrate |  | concentration: 3%, feature: PFOS/PFAS free, specific gravity: 1.0±.02 g/ml at 20⁰C, pH: 7.0-8.5, viscosity: 1200 ±300 cps | ar-afff foam concentrate | 250 | Ltr | DEG & MEG TANK
N ¦ DEG & MEG TANK > N2 ¦ FOAM GENERATOR | Supply, erection, testing & commissioning of analogue addressable Monitor module | monitor module |  | feature: analogue addressable |  | 4 | Nos | DEG & MEG TANK
N ¦ DEG & MEG TANK > N2 ¦ FOAM GENERATOR | Supply, erection, testing & commissioning of IR Detector | ir detector |  |  |  | 4 | Nos | DEG & MEG TANK
N ¦ DEG & MEG TANK > N2 ¦ FOAM GENERATOR | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. | armoured cabling |  | feature: complete with lugs, laying and termination of both ends |  |  |  | DEG & MEG TANK
N ¦ DEG & MEG TANK > N2 ¦ FOAM GENERATOR | 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cable | size: 2C x 1.5 mm2 | feature: loop cable |  | 56 | Mtr | DEG & MEG TANK
N ¦ DEG & MEG TANK > N2 ¦ FOAM GENERATOR | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable trays |  | feature: for laying all type of cables as indicated above including all necessary structural supports |  | 56 | Mtr | DEG & MEG TANK
O ¦ SECURITY ROOM > O1 ¦ FDA SYSTEM | Supply, installation, testing and commissioning of Microprocessor based 6 Loop expandable upto 10 loops,Networkable analogue addressable type fire alarm control panel with 640 character LCD display.Detectors can be any mix of ion, photo, laser photo,thermal, or multi-sensor detectors; modules can be addressable pull stations, normally open contact devices,two-wire smoke, notification, or relay modules. Four access levels, Printer Port,RS-485 port for repeater/mimic panel communication,240 volts AC power supply, automatic battery charger, 24 volts sealed lead acid batteries sufficient for 24 hours normal working and then be capable of operating the system for 10 Min during an emergency conditions as required. The Panel shall have compatibility with BACKNET/MODBUS CARD for integration. | fire alarm control panel | loops: 6 (expandable upto 10) | type: microprocessor based, type: networkable analogue addressable, display: 640 character LCD, detector compatibility: ion, photo, laser photo, thermal, multi-sensor, module compatibility: addressable pull stations, normally open contact devices, two-wire smoke, notification, relay modules, access levels: four, port: printer, port: RS-485 (for repeater/mimic panel communication), power supply: 240 volts AC, battery: automatic charger, battery: 24 volts sealed lead acid, battery backup: 24 hours normal + 10 min emergency, compatibility: BACKNET/MODBUS CARD (for integration) |  | 1 | Nos | SECURITY ROOM
O ¦ SECURITY ROOM > O1 ¦ FDA SYSTEM | Providing & fixing of PA console with selector zone facility with necessary accessories. | pa console |  | feature: selector zone facility, accessories: necessary accessories | pa console | 1 | Nos | SECURITY ROOM
O ¦ SECURITY ROOM > O1 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | multicriteria detector |  | type: analogue addressable |  | 6 | Nos | SECURITY ROOM
O ¦ SECURITY ROOM > O1 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Manual Call point | manual call point |  | type: analogue addressable |  | 2 | Nos | SECURITY ROOM
O ¦ SECURITY ROOM > O1 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of Hooter cum strobe | hooter cum strobe |  |  |  | 2 | Nos | SECURITY ROOM
O ¦ SECURITY ROOM > O1 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of Telephone jack. | telephone jack |  |  |  | 1 | Nos | SECURITY ROOM
O ¦ SECURITY ROOM > O1 ¦ FDA SYSTEM | Supply, erction, testing & commissioning of analogue addressable Control Module | control module |  | type: analogue addressable |  | 1 | Nos | SECURITY ROOM
O ¦ SECURITY ROOM > O1 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Isolator Module | isolator module |  | type: analogue addressable |  | 2 | Nos | SECURITY ROOM
O ¦ SECURITY ROOM > O1 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cabling | core: 2C, cross section: 1.5 mm2 | type: armoured, cable type: loop cable, accessories: lugs, laying and termination of both ends |  | 38 | Mtr | SECURITY ROOM
O ¦ SECURITY ROOM > O1 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Power cable) | armoured cabling | core: 2C, cross section: 1.5 mm2 | type: armoured, cable type: power cable, accessories: lugs, laying and termination of both ends |  | 29 | Mtr | SECURITY ROOM
O ¦ SECURITY ROOM > O1 ¦ FDA SYSTEM | Providing & fixing FRLS CABLING complete with lugs, laying and termination of both ends. 2C x 0.5 mm2 Armoured ( Telephone cable) | frls cabling | core: 2C, cross section: 0.5 mm2 | type: armoured, cable type: telephone cable, accessories: lugs, laying and termination of both ends |  | 12 | Mtr | SECURITY ROOM
O ¦ SECURITY ROOM > O2 ¦ PA SYSTEM | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | ip based networkable touch screen paging station |  | feature: selection of zones, feature: supervision of system status, feature: setting of scheduled broadcasts, feature: central exchange with stand by cpu, feature: built-in monitoring loudspeaker, feature: goose-neck microphone, feature: lcd touchscreen display, feature: audio input |  | 1 | Nos | SECURITY ROOM
O ¦ SECURITY ROOM > O2 ¦ PA SYSTEM | 6 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | horn type of speaker | power: 6 W | feature: high efficiency, feature: weather protection ip 65 (weatherproof type, suitable for outdoor area) |  | 3 | Nos | SECURITY ROOM
O ¦ SECURITY ROOM > O2 ¦ PA SYSTEM | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | xlpe cu cable | core: 2C, cross section: 1.5 mm2 | feature: multi stranded, feature: shielded, feature: armoured, feature: for power & signal |  | 19 | Mtr | SECURITY ROOM
O ¦ SECURITY ROOM > O2 ¦ PA SYSTEM | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | dvd player |  | feature: hook up to amplifiers of pa system for music in the common areas |  | 1 | Nos | SECURITY ROOM
O ¦ SECURITY ROOM > O2 ¦ PA SYSTEM | Paging Loudspeaker | paging loudspeaker |  |  |  | 1 | Nos | SECURITY ROOM
P ¦ BIOBIQUETE STORE > P1 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 80 mm NB | ms black steel pipe | size: 80 mm NB | material: ms(mild steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, pipe joints: grooved with groove coupling, scope: all related civil work, supports etc of vendor's scope |  | 12 | Mtr | BIOBRIQUETE STORE
P ¦ BIOBIQUETE STORE > P1 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 40 mm NB | ms black steel pipe | size: 40 mm NB | material: ms(mild steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, pipe joints: grooved with groove coupling, scope: all related civil work, supports etc of vendor's scope |  | 18 | Mtr | BIOBRIQUETE STORE
P ¦ BIOBIQUETE STORE > P1 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 25 mm NB | ms black steel pipe | size: 25 mm NB | material: ms(mild steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, pipe joints: grooved with groove coupling, scope: all related civil work, supports etc of vendor's scope |  | 12 | Mtr | BIOBRIQUETE STORE
P ¦ BIOBIQUETE STORE > P1 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. Size80 mm NB | butterfly valve | size: 80 mm NB | standard: british standard 5155, type: wafer, fittings: matching flanges, nuts & bolts, erection: necessary fittings by erection vendor |  | 1 | Nos | BIOBRIQUETE STORE
P ¦ BIOBIQUETE STORE > P1 ¦ AUTOMATIC SPRINKLER SYSTEM | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts. Size80 mm NB | non return valve | size: 80 mm NB | type: wafer, fittings: matching flanges, nuts & bolts |  | 1 | Nos | BIOBRIQUETE STORE
P ¦ BIOBIQUETE STORE > P1 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & fixing of paddle type Flow Switch | flow switch |  | type: paddle |  | 1 | Nos | BIOBRIQUETE STORE
P ¦ BIOBIQUETE STORE > P1 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Fixing of Sprinkler Head Pendent type for K factor-80. Temp rating 68 deg C.UL/FM Approved. | sprinkler head pendent type |  | k factor: 80, temperature rating: 68 deg C, certification: UL(underwriters laboratories), certification: FM(factory mutual) |  | 3 | Nos | BIOBRIQUETE STORE
P ¦ BIOBIQUETE STORE > P1 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, installation of automatic 25 NB Air Release Valve | air release valve | size: 25 NB | feature: automatic |  | 1 | Nos | BIOBRIQUETE STORE
P ¦ BIOBIQUETE STORE > P1 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends Size 40NB | globe valve | size: 40 NB | material: bronze, standard: indian standard 778, ends: screwed |  | 1 | Nos | BIOBRIQUETE STORE
P ¦ BIOBIQUETE STORE > P1 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends Size 25NB | globe valve | size: 25 NB | material: bronze, standard: indian standard 778, ends: screwed |  | 2 | Nos | BIOBRIQUETE STORE
P ¦ BIOBIQUETE STORE > P1 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Erection and testing of Installation Control Valve complete with trims & gong. Size 80 mm NB | installation control valve | size: 80 mm NB | feature: complete with trims & gong |  | 1 | Nos | BIOBRIQUETE STORE
P ¦ BIOBIQUETE STORE > P2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | multicriteria detector |  | type: analogue addressable |  | 3 | Nos | BIOBRIQUETE STORE
P ¦ BIOBIQUETE STORE > P2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Manual Call point | manual call point |  | type: analogue addressable |  | 1 | Nos | BIOBRIQUETE STORE
P ¦ BIOBIQUETE STORE > P2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of Hooter cum strobe | hooter cum strobe |  |  |  | 1 | Nos | BIOBRIQUETE STORE
P ¦ BIOBIQUETE STORE > P2 ¦ FDA SYSTEM | Supply, erction, testing & commissioning of analogue addressable Control Module | control module |  | type: analogue addressable |  | 1 | Nos | BIOBRIQUETE STORE
P ¦ BIOBIQUETE STORE > P2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Isolator Module | isolator module |  | type: analogue addressable |  | 2 | Nos | BIOBRIQUETE STORE
P ¦ BIOBIQUETE STORE > P2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Monitor module | monitor module |  | type: analogue addressable |  | 1 | Nos | BIOBRIQUETE STORE
P ¦ BIOBIQUETE STORE > P2 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cabling | size: 2C x 1.5 mm2 | feature: loop cable, feature: armoured, fittings: lugs, laying and termination of both ends |  | 36 | Mtr | BIOBRIQUETE STORE
P ¦ BIOBIQUETE STORE > P2 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Power cable) | armoured cabling | size: 2C x 1.5 mm2 | feature: power cable, feature: armoured, fittings: lugs, laying and termination of both ends |  | 24 | Mtr | BIOBRIQUETE STORE
P ¦ BIOBIQUETE STORE > P2 ¦ FDA SYSTEM | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable trays |  | material: gi(galvanized iron), feature: for laying all type of cables, feature: including all necessary structural supports |  | 36 | Mtr | BIOBRIQUETE STORE
P ¦ BIOBIQUETE STORE > P3 ¦ PA SYSTEM | Rack Mounted 125 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | power amplifier | power: 125 watt | feature: rack mounted, feature: battery back up, feature: wattage shall be as per requirement |  | 1 | Nos | BIOBRIQUETE STORE
P ¦ BIOBIQUETE STORE > P3 ¦ PA SYSTEM | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | dvd player |  | feature: features to hook up to amplifiers of PA system, feature: for music in the common areas |  | 1 | Nos | BIOBRIQUETE STORE
P ¦ BIOBIQUETE STORE > P3 ¦ PA SYSTEM | Paging Loudspeaker | paging loudspeaker |  |  |  | 1 | Nos | BIOBRIQUETE STORE
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection , testing & commissioning of Deluge valve with wet pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 3/2 way Solenoid Valve, air filter regulator etc. & manual release unit. The valve shall be electro-pneumatic type. 80 mm NB | deluge valve | size: 80 mm NB | assembly: wet pilot trim, fitted with: strainer, drain valve, pressure gauge, pressure switch, solenoid valve: flame proof 3/2 way, air filter regulator: included, manual release unit: included, type: electro-pneumatic |  | 2 | Nos | SUBSTATION BUILDING
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. 80 mm NB | gate valve | size: 80 mm NB | material: cs(carbon steel), standard: API 600, class: 150, flanges: matching, included: nuts & bolts |  | 6 | Nos | SUBSTATION BUILDING
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, installation, testing of Y- Stainer . 80 mm NB | y-stainer | size: 80 mm NB |  |  | 2 | Nos | SUBSTATION BUILDING
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply,installation,testing and commissioning of HVWS NOZZLE with necessary threaded fittings as per drawing. K26, SPRAY ANGLE=100° | hvws nozzle |  | model: K26, spray angle: 100°, fittings: necessary threaded, as per drawing: yes |  | 32 | Nos | SUBSTATION BUILDING
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply,installation and commissioning of UL/FM approved Quartzoid Bulb Detector for K factor-80. Temp rating 68 deg C | quartzoid bulb detector |  | certification: UL(underwriters laboratories)/FM(factory mutual), k factor: 80, temperature rating: 68 deg C |  | 32 | Nos | SUBSTATION BUILDING
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 80 NB | gi "c" class pipes | size: 80 NB | class: heavy class, standard: IS 1239, fittings: threaded or grooved, included: elbows, tees, reducers, welding flanges, clamps, ms(mild steel) brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, as per fire authorities: yes, above ground: yes |  | 36 | Mtr | SUBSTATION BUILDING
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 65 NB | gi "c" class pipes | size: 65 NB | class: heavy class, standard: IS 1239, fittings: threaded or grooved, included: elbows, tees, reducers, welding flanges, clamps, ms(mild steel) brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, as per fire authorities: yes, above ground: yes |  | 12 | Mtr | SUBSTATION BUILDING
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 50 NB | gi "c" class pipes | size: 50 NB | class: heavy class, standard: IS 1239, fittings: threaded or grooved, included: elbows, tees, reducers, welding flanges, clamps, ms(mild steel) brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, as per fire authorities: yes, above ground: yes |  | 78 | Mtr | SUBSTATION BUILDING
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 40NB | gi "c" class pipes | size: 40NB | class: heavy class, standard: IS 1239, fittings: threaded or grooved, included: elbows, tees, reducers, welding flanges, clamps, ms(mild steel) brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, as per fire authorities: yes, above ground: yes |  | 42 | Mtr | SUBSTATION BUILDING
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 25NB | gi "c" class pipes | size: 25NB | class: heavy class, standard: IS 1239, fittings: threaded or grooved, included: elbows, tees, reducers, welding flanges, clamps, ms(mild steel) brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, as per fire authorities: yes, above ground: yes |  | 78 | Mtr | SUBSTATION BUILDING
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | multicriteria detector |  | type: analogue addressable |  | 34 | Nos | SUBSTATION BUILDING
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing & commissioning of analogue addressable Manual Call point | manual call point |  | type: analogue addressable |  | 4 | Nos | SUBSTATION BUILDING
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing & commissioning of Hooter cum strobe | hooter cum strobe |  |  |  | 4 | Nos | SUBSTATION BUILDING
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erction, testing & commissioning of analogue addressable Control Module | control module |  | type: analogue addressable |  | 4 | Nos | SUBSTATION BUILDING
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing & commissioning of analogue addressable Isolator Module | isolator module |  | type: analogue addressable |  | 2 | Nos | SUBSTATION BUILDING
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing & commissioning of analogue addressable Monitor module | monitor module |  | type: analogue addressable |  | 2 | Nos | SUBSTATION BUILDING
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cabling | configuration: 2C x 1.5 mm2 | type: armoured, cable type: loop cable, feature: complete with lugs, laying and termination of both ends |  | 240 | Mtr | SUBSTATION BUILDING
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Power cable) | armoured cabling | configuration: 2C x 1.5 mm2 | type: armoured, cable type: power cable, feature: complete with lugs, laying and termination of both ends |  | 110 | Mtr | SUBSTATION BUILDING
Q ¦ SUBSTATION BUILDING > Q1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable trays |  | feature: for laying all type of cables as indicated above, feature: including all necessary structural supports |  | 240 | Mtr | SUBSTATION BUILDING
R ¦ PRE TREATMENT CHEMICAL (PTC) R1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 150 mm NB | ms black steel pipe | size: 150 mm NB | material: ms(mild steel), finish: black, grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, scope: all related civil work, supports of vendor's scope |  | 18 | Mtr | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 80 mm NB | ms black steel pipe | size: 80 mm NB | material: ms(mild steel), finish: black, grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, scope: all related civil work, supports of vendor's scope |  | 12 | Mtr | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 25 mm NB | ms black steel pipe | size: 25 mm NB | material: ms(mild steel), finish: black, grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, scope: all related civil work, supports of vendor's scope |  | 12 | Mtr | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R1 ¦ HYDRANT SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. Size 150 mm NB | gate valve | size: 150 mm NB | material: cs(carbon steel), standard: api 600, class: 150, flanges: matching, accessories: nuts & bolts |  | 2 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R1 ¦ HYDRANT SYSTEM | Supply, installation, testing and commissioning of CS Non return valve with companion flanges,nuts & bolts and gaskets. Size 150 mm NB | non return valve | size: 150 mm NB | material: cs(carbon steel), flanges: companion, accessories: nuts & bolts, gaskets |  | 1 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R1 ¦ HYDRANT SYSTEM | Supply & installation of SS oblique type single headed Landing valve with 80 mm inlet and 63 mm outlet SS instantaneous male coupling with rubber cap and chain conforming to IS : 5290 including matching flanges, gasket, nuts and bolts complete. | landing valve | inlet: 80 mm, outlet: 63 mm | material: ss(stainless steel), type: oblique, head: single, coupling: ss(stainless steel) instantaneous male, accessories: rubber cap and chain, standard: indian standard 5290, flanges: matching, accessories: gasket, nuts and bolts |  | 3 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R1 ¦ HYDRANT SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. Size 80 mm NB | butterfly valve | size: 80 mm NB | standard: bs(british standard) 5155, type: wafer, flanges: matching, accessories: nuts & bolts, fittings: necessary fittings by erection vendor |  | 3 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R1 ¦ HYDRANT SYSTEM | Supply & installation of SS branch pipe with 20 mm nozzle conforming to IS : 903 complete | branch pipe | nozzle: 20 mm | material: ss(stainless steel), standard: indian standard 903 |  | 3 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R1 ¦ HYDRANT SYSTEM | Supply & installation of 63 mm dia rubberized reinforced rubber line hose pipe in 15 m length conforming to IS : 636 Type II ISI marked with gunmetal male and female instantaneous coupling conforming to IS 903 wounded with 18 SWG copper wire complete | hose pipe | diameter: 63 mm, length: 15 m | type: rubberized reinforced rubber line, standard: indian standard 636 type ii, certification: isi, coupling: gunmetal male and female instantaneous, coupling standard: indian standard 903, wire: 18 swg copper wire |  | 6 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R1 ¦ HYDRANT SYSTEM | Supply & installation of MS Hose Box of fabricated from 16 SWG CRCA sheet double door with lockable arrangements to accommodate 2 RRL hose of 15 m length and one branch pipe painted white inside and red outside with one key. (750X600X250 mm) | hose box | dimensions: 750X600X250 mm | material: ms(mild steel), sheet: 16 swg crca, doors: double, lockable: yes, capacity: 2 rrl hose of 15 m length and one branch pipe, paint: white inside and red outside, accessories: one key |  | 3 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R1 ¦ HYDRANT SYSTEM | Supply & installation of swinging type hose reel drum fabricated from 14 SWG CRCA sheets painted with red colour stove paint 2 coats over 1 coat of primer with 30 m long 20 mm dia rubber hose pipe with with SS self closing shut – off nozzle of 5 mm outlet fixed on wall. | hose reel drum | hose length: 30 m, hose diameter: 20 mm, nozzle outlet: 5 mm | type: swinging, material: 14 swg crca sheets, paint: red colour stove paint 2 coats over 1 coat of primer, hose: rubber, nozzle: ss(stainless steel) self closing shut-off, mounting: fixed on wall |  | 3 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R1 ¦ HYDRANT SYSTEM | Supply and installation of pressure gauge, 1/2 inch bottom entry, of suitable range with ball valves and other accessories. | pressure gauge | bottom entry: 1/2 inch | range: suitable, accessories: ball valves and other accessories |  | 1 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R1 ¦ HYDRANT SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends Size 25NB | globe valve | size: 25NB | material: bronze, standard: indian standard 778, end-type: screwed |  | 5 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R1 ¦ HYDRANT SYSTEM | Supply & installation of 250ltr foam tank filled with 3% AFFF foam concentrate with foam making branch and pick up tube. | foam tank | tank capacity: 250 ltr | foam concentrate: 3% AFFF(aqueous film forming foam), feature: with foam making branch and pick up tube |  | 1 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection , testing & commissioning of Deluge valve with dry pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 3/2 way Solenoid Valve, air filter regulator etc. & manual release unit. The valve shall be electro-pneumatic double inter lock system as per scheme drawing. 150 mm NB | deluge valve | size: 150 mm NB | feature: dry pilot trim assembly, feature: fitted with strainer, feature: fitted with drain valve, feature: fitted with pressure gauge, feature: fitted with pressure switch, feature: fitted with flame proof 3/2 way solenoid valve, feature: fitted with air filter regulator, feature: manual release unit, feature: electro-pneumatic double inter lock system as per scheme drawing |  | 1 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R2 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. 150 mm NB | gate valve | size: 150 mm NB | material: cs(carbon steel), standard: API 600, class: 150, end-type: matching flanges, feature: complete with nuts & bolts |  | 3 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R2 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing of Y- Strainer. Size 150 mm NB | y-strainer | size: 150 mm NB |  |  | 1 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R2 ¦ FOAM WATER SPRAY SYSTEM | Supply,installation,testing and commissioning of Foam Sprinkler nozzle with necessary threaded fittings as per drawing. The sprinkler shall be Open Aspiration, Pendent type, K-42 with standard spray angle.End connection 1/2" NPT/BSP.UL/FM Approved. Spray nozzle K factor -42 | foam sprinkler nozzle |  | feature: open aspiration, type: pendent, k-factor: 42, spray angle: standard, end connection: 1/2" NPT/NPT(British Standard Pipe), certification: UL(underwriters laboratories), certification: FM(factory mutual), feature: with necessary threaded fittings as per drawing |  | 59 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R2 ¦ FOAM WATER SPRAY SYSTEM | Supply,installation and commissioning of UL/FM approved Quartzoid Bulb Detector for K factor-80. Temp rating 68 deg C | quartzoid bulb detector |  | certification: UL(underwriters laboratories), certification: FM(factory mutual), k-factor: 80, temperature rating: 68 deg C |  | 59 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R2 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing and commissioning of Ratio Controller. 150NB | ratio controller | size: 150NB |  |  | 1 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R2 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing and commissioning of Foam bladder tank vertical type ,manufacturing as per ASME, section-VIII part- I. The bladder material shall be BUNA-N. The Bladder Tank shall be supplied along with all necessary valves, Hydraulically Operated Foam Concentrae Control Valve ,fittingss & instruments as per Technical data sheet attached with Tender documents. Capacity of 2100 ltr. | foam bladder tank | capacity: 2100 ltr | type: vertical, manufacturing standard: ASME(american society of mechanical engineers) section-VIII part-I, bladder material: BUNA-N, feature: supplied along with all necessary valves, feature: hydraulically operated foam concentrate control valve, feature: supplied with fittings & instruments as per technical data sheet attached with tender documents |  | 1 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 150 NB | gi c class pipe | size: 150 NB | class: heavy class, standard: IS 1239 (indian standard 1239), fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, fixing: clamps to MS brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, location: above ground, specification: as per specifications |  | 12 | Mtr | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 100 NB | gi c class pipe | size: 100 NB | class: heavy class, standard: IS 1239 (indian standard 1239), fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, fixing: clamps to MS brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, location: above ground, specification: as per specifications |  | 18 | Mtr | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 80 NB | gi c class pipe | size: 80 NB | class: heavy class, standard: IS 1239 (indian standard 1239), fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, fixing: clamps to MS brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, location: above ground, specification: as per specifications |  | 24 | Mtr | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 65 NB | gi c class pipe | size: 65 NB | class: heavy class, standard: IS 1239 (indian standard 1239), fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, fixing: clamps to MS brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, location: above ground, specification: as per specifications |  | 24 | Mtr | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 50 NB | gi c class pipe | size: 50 NB | class: heavy class, standard: IS 1239 (indian standard 1239), fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, fixing: clamps to MS brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, location: above ground, specification: as per specifications |  | 18 | Mtr | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 40NB | gi c class pipe | size: 40 NB | class: heavy class, standard: IS 1239 (indian standard 1239), fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, fixing: clamps to MS brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, location: above ground, specification: as per specifications |  | 66 | Mtr | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 25NB | gi c class pipe | size: 25 NB | class: heavy class, standard: IS 1239 (indian standard 1239), fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, fixing: clamps to MS brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, location: above ground, specification: as per specifications |  | 284 | Mtr | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 80 mm NB | ms black steel pipe | size: 80 mm NB | grade: heavy, thickness: 5.4mm, standard: IS 1239 Part-1 (indian standard 1239 part-1), fittings included: elbows, tees, flanges, reduces clamps, MS support dash fasteners, paint: two coats of approved primer and two coats of approved paint, joint: grooved with groove coupling, scope: all related civil work, supports of vendor's scope |  | 24 | Mtr | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 65 mm NB | ms black steel pipe | size: 65 mm NB | grade: heavy, thickness: 5.4mm, standard: IS 1239 Part-1 (indian standard 1239 part-1), fittings included: elbows, tees, flanges, reduces clamps, MS support dash fasteners, paint: two coats of approved primer and two coats of approved paint, joint: grooved with groove coupling, scope: all related civil work, supports of vendor's scope |  | 12 | Mtr | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 50 mm NB | ms black steel pipe | size: 50 mm NB | grade: heavy, thickness: 5.4mm, standard: IS 1239 Part-1 (indian standard 1239 part-1), fittings included: elbows, tees, flanges, reduces clamps, MS support dash fasteners, paint: two coats of approved primer and two coats of approved paint, joint: grooved with groove coupling, scope: all related civil work, supports of vendor's scope |  | 18 | Mtr | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R3 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved red oxide primer and two coats of approved red enamel paint and welded joints complete with cutting and making good the complete with cutting and making good the walls, floors or any other surface 80 mm NB | ms black steel pipe | size: 80 mm NB | grade: heavy, thickness: 5.4mm, standard: IS 1239 Part-1 (indian standard 1239 part-1), fittings included: elbows, tees, flanges, reduces clamps, MS support dash fasteners, paint: two coats of approved red oxide primer and two coats of approved red enamel paint, joints: welded, installation: complete with cutting and making good the walls, floors or any other surface |  | 24 | Mtr | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R3 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved red oxide primer and two coats of approved red enamel paint and welded joints complete with cutting and making good the complete with cutting and making good the walls, floors or any other surface 65 mm NB | ms black steel pipe | size: 65 mm NB | grade: heavy, thickness: 5.4mm, standard: IS 1239 Part-1 (indian standard 1239 part-1), fittings included: elbows, tees, flanges, reduces clamps, MS support dash fasteners, paint: two coats of approved red oxide primer and two coats of approved red enamel paint, joints: welded, installation: complete with cutting and making good the walls, floors or any other surface |  | 12 | Mtr | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R3 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved red oxide primer and two coats of approved red enamel paint and welded joints complete with cutting and making good the complete with cutting and making good the walls, floors or any other surface 50 mm NB | ms black steel pipe | size: 50 mm NB | grade: heavy, thickness: 5.4mm, standard: IS 1239 Part-1 (indian standard 1239 part-1), fittings included: elbows, tees, flanges, reduces clamps, MS support dash fasteners, paint: two coats of approved red oxide primer and two coats of approved red enamel paint, joints: welded, installation: complete with cutting and making good the walls, floors or any other surface |  | 18 | Mtr | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R3 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved red oxide primer and two coats of approved red enamel paint and welded joints complete with cutting and making good the complete with cutting and making good the walls, floors or any other surface 40 mm NB | ms black steel pipe | size: 40 mm NB | grade: heavy, thickness: 5.4mm, standard: IS 1239 Part-1 (indian standard 1239 part-1), fittings included: elbows, tees, flanges, reduces clamps, MS support dash fasteners, paint: two coats of approved red oxide primer and two coats of approved red enamel paint, joints: welded, installation: complete with cutting and making good the walls, floors or any other surface |  | 12 | Mtr | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R3 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved red oxide primer and two coats of approved red enamel paint and welded joints complete with cutting and making good the complete with cutting and making good the walls, floors or any other surface 25 mm NB | ms black steel pipe | size: 25 mm NB | grade: heavy, thickness: 5.4mm, standard: IS 1239 Part-1 (indian standard 1239 part-1), fittings included: elbows, tees, flanges, reduces clamps, MS support dash fasteners, paint: two coats of approved red oxide primer and two coats of approved red enamel paint, joints: welded, installation: complete with cutting and making good the walls, floors or any other surface |  | 24 | Mtr | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R3 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. Size 80 mm NB | butterfly valve | size: 80 mm NB | standard: BS 5155 (british standard 5155), type: wafer, flanges: matching, fittings: necessary fittings by erection vendor |  | 1 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R3 ¦ AUTOMATIC SPRINKLER SYSTEM | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts. Size 80 mm NB | non return valve | size: 80 mm NB | type: wafer, flanges: matching |  | 1 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R3 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & fixing of paddle type Flow Switch | flow switch |  | type: paddle |  | 1 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R3 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Fixing of Sprinkler Head Pendent type for K factor-80. Temp rating 68 deg C. UL/FM Approved. | sprinkler head pendent type | k factor: 80 | temperature rating: 68 deg C, certification: UL(underwriters laboratories), certification: FM(factory mutual) |  | 18 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R3 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, installation of automatic 25 NB Air Release Valve | air release valve | size: 25 NB | type: automatic |  | 1 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R3 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends Size 25NB | globe valve | size: 25 NB | material: bronze, standard: IS(indian standard) 778, end connection: screwed |  | 2 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R3 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends Size 40NB | globe valve | size: 40 NB | material: bronze, standard: IS(indian standard) 778, end connection: screwed |  | 1 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R3 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Erection and testing of Installation Control Valve complete with trims & gong. Size 80 mm NB | installation control valve | size: 80 mm NB | feature: complete with trims & gong |  | 1 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R4 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | multicriteria detector |  | type: analogue addressable |  | 4 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R4 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of IR Detector | ir detector |  |  |  | 7 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R4 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Manual Call point | manual call point |  | type: analogue addressable |  | 4 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R4 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of Hooter cum strobe | hooter cum strobe |  |  |  | 4 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R4 ¦ FDA SYSTEM | Supply, erction, testing & commissioning of analogue addressable Control Module | control module |  | type: analogue addressable |  | 3 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R4 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Isolator Module | isolator module |  | type: analogue addressable |  | 2 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R4 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Monitor module | monitor module |  | type: analogue addressable |  | 9 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R4 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of 6 Watt Ceiling mounted Speakers | ceiling mounted speaker | power: 6 Watt |  |  | 9 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R4 ¦ FDA SYSTEM | Providing & fixing 100Watt Amplifier with necessary accessories. | amplifier | power: 100 Watt | feature: necessary accessories |  | 1 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R4 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cabling | configuration: 2C x 1.5 mm2 | feature: loop cable, feature: complete with lugs, laying and termination of both ends |  | 256 | Mtr | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R4 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Power cable) | armoured cabling | configuration: 2C x 1.5 mm2 | feature: power cable, feature: complete with lugs, laying and termination of both ends |  | 127 | Mtr | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R4 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Speaker cable) | armoured cabling | configuration: 2C x 1.5 mm2 | feature: speaker cable, feature: complete with lugs, laying and termination of both ends |  | 140 | Mtr | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R4 ¦ FDA SYSTEM | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable tray |  | feature: for laying all type of cables, feature: including all necessary structural supports |  | 256 | Mtr | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R5 ¦ PA SYSTEM | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | ip based networkable touch screen paging station |  | feature: selection of zones, feature: supervision of system status, feature: setting of scheduled broadcasts, feature: central exchange with stand by CPU, feature: built-in monitoring loudspeaker, feature: goose-neck microphone, feature: LCD touchscreen display, feature: audio input |  | 1 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R5 ¦ PA SYSTEM | 15 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | horn type speaker | power: 15 W | feature: high efficiency, feature: weather protection IP 65 (weatherproof type, suitable for outdoor area) |  | 3 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R5 ¦ PA SYSTEM | Rack Mounted 125 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | power amplifier | power: 125 watt | feature: rack mounted, feature: battery back up, feature: wattage shall be as per requirement |  | 1 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R5 ¦ PA SYSTEM | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | xlpe cu cable | configuration: 2C x 1.5 mm2 | feature: multi stranded, feature: shielded, feature: armoured, feature: for power & signal |  | 90 | Mtr | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R5 ¦ PA SYSTEM | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | dvd player |  | feature: hook up to amplifiers of PA system for music in the common areas |  | 1 | Nos | PRE TREATMENT CHEMICAL(PTC)
R ¦ PRE TREATMENT CHEMICAL (PTC) R5 ¦ PA SYSTEM | Paging Loudspeaker | paging loudspeaker |  |  |  | 1 | Nos | PRE TREATMENT CHEMICAL(PTC)
S ¦ FINISH GODOWN 1 > S1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 100 mm NB | ms black steel pipe | size: 100 mm NB | material: ms(mild steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, pipe joints: grooved with groove coupling, scope: all related civil work, supports etc of vendor's scope |  | 120 | Mtr | FINISHED GOOD 1
S ¦ FINISH GODOWN 1 > S1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 80 mm NB | ms black steel pipe | size: 80 mm NB | material: ms(mild steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, pipe joints: grooved with groove coupling, scope: all related civil work, supports etc of vendor's scope |  | 30 | Mtr | FINISHED GOOD 1
S ¦ FINISH GODOWN 1 > S1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 25 mm NB | ms black steel pipe | size: 25 mm NB | material: ms(mild steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, pipe joints: grooved with groove coupling, scope: all related civil work, supports etc of vendor's scope |  | 12 | Mtr | FINISHED GOOD 1
S ¦ FINISH GODOWN 1 > S1 ¦ HYDRANT SYSTEM | Supply & installation of SS oblique type single headed Landing valve with 80 mm inlet and 63 mm outlet SS instantaneous male coupling with rubber cap and chain conforming to IS : 5290 including matching flanges, gasket, nuts and bolts complete. | landing valve | inlet: 80 mm, outlet: 63 mm | material: ss(stainless steel), type: oblique, head: single headed, coupling: ss instantaneous male, accessories: rubber cap and chain, standard: indian standard 5290, accessories: matching flanges, gasket, nuts and bolts |  | 6 | Nos | FINISHED GOOD 1
S ¦ FINISH GODOWN 1 > S1 ¦ HYDRANT SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. Size 80 mm NB | butterfly valve | size: 80 mm NB | standard: british standard 5155, type: wafer, accessories: matching flanges, nuts & bolts, fittings: necessary fittings by erection vendor |  | 6 | Nos | FINISHED GOOD 1
S ¦ FINISH GODOWN 1 > S1 ¦ HYDRANT SYSTEM | Supply & installation of SS branch pipe with 20 mm nozzle conforming to IS : 903 complete | branch pipe | nozzle: 20 mm | material: ss(stainless steel), standard: indian standard 903 |  | 6 | Nos | FINISHED GOOD 1
S ¦ FINISH GODOWN 1 > S1 ¦ HYDRANT SYSTEM | Supply & installation of 63 mm dia rubberized reinforced rubber line hose pipe in 15 m length conforming to IS : 636 Type II ISI marked with gunmetal male and female instantaneous coupling conforming to IS 903 wounded with 18 SWG copper wire complete | hose pipe | diameter: 63 mm, length: 15 m | type: rubberized reinforced rubber line, standard: indian standard 636 type ii, certification: isi, coupling: gunmetal male and female instantaneous, coupling standard: indian standard 903, wire: 18 swg copper wire |  | 12 | Nos | FINISHED GOOD 1
S ¦ FINISH GODOWN 1 > S1 ¦ HYDRANT SYSTEM | Supply & installation of MS Hose Box of fabricated from 16 SWG CRCA sheet double door with lockable arrangements to accommodate 2 RRL hose of 15 m length and one branch pipe painted white inside and red outside with one key. (750X600X250 mm) | hose box | dimensions: 750X600X250 mm | material: ms(mild steel), fabrication: 16 swg crca sheet, door: double door with lockable arrangements, capacity: accommodates 2 rrl hose of 15 m length and one branch pipe, paint: white inside and red outside, accessories: one key |  | 6 | Nos | FINISHED GOOD 1
S ¦ FINISH GODOWN 1 > S1 ¦ HYDRANT SYSTEM | Supply & installation of swinging type hose reel drum fabricated from 14 SWG CRCA sheets painted with red colour stove paint 2 coats over 1 coat of primer with 30 m long 20 mm dia rubber hose pipe with with SS self closing shut – off nozzle of 5 mm outlet fixed on wall. | hose reel drum | hose length: 30 m, hose diameter: 20 mm, nozzle outlet: 5 mm | type: swinging, fabrication: 14 swg crca sheets, paint: red colour stove paint 2 coats over 1 coat of primer, hose: rubber, nozzle: ss(stainless steel) self closing shut-off, installation: fixed on wall |  | 6 | Nos | FINISHED GOOD 1
S ¦ FINISH GODOWN 1 > S1 ¦ HYDRANT SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends Size 25NB | globe valve | size: 25NB | material: bronze, standard: indian standard 778, ends: screwed |  | 6 | Nos | FINISHED GOOD 1
S ¦ FINISH GODOWN 1 > S2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Manual Call point | manual call point |  | type: analogue addressable |  | 8 | Nos | FINISHED GOOD 1
S ¦ FINISH GODOWN 1 > S2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of Hooter cum strobe | hooter cum strobe |  |  |  | 8 | Nos | FINISHED GOOD 1
S ¦ FINISH GODOWN 1 > S2 ¦ FDA SYSTEM | Supply, erction, testing & commissioning of analogue addressable Control Module | control module |  | type: analogue addressable |  | 3 | Nos | FINISHED GOOD 1
S ¦ FINISH GODOWN 1 > S2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Isolator Module | isolator module |  | type: analogue addressable |  | 3 | Nos | FINISHED GOOD 1
S ¦ FINISH GODOWN 1 > S2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Monitor module | monitor module |  | type: analogue addressable |  | 2 | Nos | FINISHED GOOD 1
S ¦ FINISH GODOWN 1 > S2 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cabling | cable: 2C x 1.5 mm2 | feature: complete with lugs, laying and termination of both ends, type: loop cable |  | 330 | Mtr | FINISHED GOOD 1
S ¦ FINISH GODOWN 1 > S2 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Power cable) | armoured cabling | cable: 2C x 1.5 mm2 | feature: complete with lugs, laying and termination of both ends, type: power cable |  | 354 | Mtr | FINISHED GOOD 1
S ¦ FINISH GODOWN 1 > S2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of 6 Watt Ceiling mounted Speakers | ceiling mounted speakers | power: 6 Watt |  |  | 77 | Nos | FINISHED GOOD 1
S ¦ FINISH GODOWN 1 > S2 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Speaker cable) | armoured cabling | cable: 2C x 1.5 mm2 | feature: complete with lugs, laying and termination of both ends, type: speaker cable |  | 640 | Mtr | FINISHED GOOD 1
S ¦ FINISH GODOWN 1 > S2 ¦ FDA SYSTEM | Supply, installation, testing and commissioning of aspiration detector with CMOS imager combined with multiple photodiode for reliable very early warning in a wide range of environments with minimal nuisance alarms. The detector should have 4 pipe inlet and min 100m pipelength support per inlet.The detector should have Smart on-board filter retains dust count and remaining filter life for predictable maintenance& coverage area of min 5000 Sq. | aspiration detector | pipe inlet: 4, pipelength support per inlet: min 100m, coverage area: min 5000 Sq. | imager: CMOS, feature: combined with multiple photodiode for reliable very early warning in a wide range of environments with minimal nuisance alarms, feature: Smart on-board filter retains dust count and remaining filter life for predictable maintenance |  | 4 | Nos | FINISHED GOOD 1
S ¦ FINISH GODOWN 1 > S2 ¦ FDA SYSTEM | Supply,Installation,Testing & Commissioning of UL/VDS listed CPVC Pipe 25 mm Dia & Pipe Accessories for the Aspiration detection. | cpvc pipe | diameter: 25 mm | certification: UL(underwriters laboratories), certification: VDS, feature: listed, feature: for the Aspiration detection |  | 840 | Mtr | FINISHED GOOD 1
S ¦ FINISH GODOWN 1 > S2 ¦ FDA SYSTEM | Providing & fixing 600Watt Amplifier with necessary accessories. | amplifier | power: 600Watt | feature: with necessary accessories |  | 1 | Nos | FINISHED GOOD 1
S ¦ FINISH GODOWN 1 > S2 ¦ FDA SYSTEM | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable trays |  | feature: for laying all type of cables as indicated above, feature: including all necessary structural supports |  | 640 | Mtr | FINISHED GOOD 1
S ¦ FINISH GODOWN 1 > S3 ¦ WATER CURTAIN | Supply, erection , testing & commissioning of Deluge valve with wet pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 2 way Solenoid Valve, air filter regulator etc. & manual release unit. Size 150 NB | deluge valve | size: 150 NB | trim assembly: wet pilot, fitted with: strainer, drain valve, pressure gauge, pressure switch, solenoid valve: flame proof 2 way, air filter regulator: included, manual release unit: included |  | 1 | Nos | FINISHED GOOD 1
S ¦ FINISH GODOWN 1 > S3 ¦ WATER CURTAIN | Providing & fixing Cast Iron Y Strainer. Size 150 NB | y strainer | size: 150 NB | material: cast iron |  | 1 | Nos | FINISHED GOOD 1
S ¦ FINISH GODOWN 1 > S3 ¦ WATER CURTAIN | Supply & fixing of SS Water Curtain Nozzle (K>=71)UL/FM Approved. | water curtain nozzle |  | material: stainless steel, k-factor: >=71, certification: UL(underwriters laboratories), certification: FM(factory mutual) |  | 125 | Nos | FINISHED GOOD 1
S ¦ FINISH GODOWN 1 > S3 ¦ WATER CURTAIN | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. Size 150 NB | gate valve | size: 150 NB | material: cs(carbon steel), standard: API 600, class: 150, flanges: matching, complete with: nuts & bolts |  | 3 | Nos | FINISHED GOOD 1
S ¦ FINISH GODOWN 1 > S4 ¦ PA SYSTEM | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | ip based networkable touch screen paging station |  | function: selection of zones, function: supervision of system status, function: setting of scheduled broadcasts, central exchange: with stand by CPU, built-in: monitoring loudspeaker, microphone: goose-neck, display: LCD touchscreen, audio input: included |  | 1 | Nos | FINISHED GOOD 1
S ¦ FINISH GODOWN 1 > S4 ¦ PA SYSTEM | 30 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | horn type speaker | power: 30 W | efficiency: high, weather protection: IP 65, type: weatherproof, suitable for: outdoor area |  | 6 | Nos | FINISHED GOOD 1
S ¦ FINISH GODOWN 1 > S4 ¦ PA SYSTEM | Rack Mounted 200 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | power amplifier | power: 200 watt | mounting: rack mounted, battery back up: included, wattage: as per requirement |  | 1 | Nos | FINISHED GOOD 1
S ¦ FINISH GODOWN 1 > S4 ¦ PA SYSTEM | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | xlpe cu cable | core: 2C, cross section: 1.5 mm2 | type: multi stranded, type: shielded, type: armoured, application: power & signal |  | 260 | Mtr | FINISHED GOOD 1
S ¦ FINISH GODOWN 1 > S4 ¦ PA SYSTEM | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | dvd player |  | feature: hook up to amplifiers of PA system, application: music in the common areas |  | 1 | Nos | FINISHED GOOD 1
S ¦ FINISH GODOWN 1 > S4 ¦ PA SYSTEM | Paging Loudspeaker | paging loudspeaker |  |  |  | 1 | Nos | FINISHED GOOD 1
T ¦ FINISH GODOWN 2 > T1 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | multicriteria detector |  | type: analogue addressable |  | 34 | Nos | FINISHED GOOD 2
T ¦ FINISH GODOWN 2 > T1 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Manual Call point | manual call point |  | type: analogue addressable |  | 4 | Nos | FINISHED GOOD 2
T ¦ FINISH GODOWN 2 > T1 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of Hooter cum strobe | hooter cum strobe |  |  |  | 4 | Nos | FINISHED GOOD 2
T ¦ FINISH GODOWN 2 > T1 ¦ FDA SYSTEM | Supply, erction, testing & commissioning of analogue addressable Control Module | control module |  | type: analogue addressable |  | 4 | Nos | FINISHED GOOD 2
T ¦ FINISH GODOWN 2 > T1 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Isolator Module | isolator module |  | type: analogue addressable |  | 1 | Nos | FINISHED GOOD 2
T ¦ FINISH GODOWN 2 > T1 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Monitor module | monitor module |  | type: analogue addressable |  | 2 | Nos | FINISHED GOOD 2
T ¦ FINISH GODOWN 2 > T1 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cabling | configuration: 2C x 1.5 mm2 | type: armoured, feature: complete with lugs, laying and termination of both ends, cable type: loop cable |  | 240 | Mtr | FINISHED GOOD 2
T ¦ FINISH GODOWN 2 > T1 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Power cable) | armoured cabling | configuration: 2C x 1.5 mm2 | type: armoured, feature: complete with lugs, laying and termination of both ends, cable type: power cable |  | 110 | Mtr | FINISHED GOOD 2
T ¦ FINISH GODOWN 2 > T1 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Speaker cable) | armoured cabling | configuration: 2C x 1.5 mm2 | type: armoured, feature: complete with lugs, laying and termination of both ends, cable type: speaker cable |  | 32 | Mtr | FINISHED GOOD 2
T ¦ FINISH GODOWN 2 > T1 ¦ FDA SYSTEM | Supply, installation, testing and commissioning of aspiration detector with CMOS imager combined with multiple photodiode for reliable very early warning in a wide range of environments with minimal nuisance alarms. The detector should have 4 pipe inlet and min 100m pipelength support per inlet.The detector should have Smart on-board filter retains dust count and remaining filter life for predictable maintenance& coverage area of min 5000 Sq. | aspiration detector | pipe inlet: 4, pipelength support per inlet: min 100m, coverage area: min 5000 Sq. | imager: CMOS, sensor: multiple photodiode, feature: very early warning, feature: minimal nuisance alarms, feature: smart on-board filter retains dust count and remaining filter life for predictable maintenance |  | 2 | Nos | FINISHED GOOD 2
T ¦ FINISH GODOWN 2 > T1 ¦ FDA SYSTEM | Supply,Installation,Testing & Commissioning of UL/VDS listed CPVC Pipe 25 mm Dia & Pipe Accessories for the Aspiration detection. | cpvc pipe | diameter: 25 mm | certification: UL(underwriters laboratories), certification: VDS, feature: pipe accessories for the aspiration detection |  | 270 | Mtr | FINISHED GOOD 2
T ¦ FINISH GODOWN 2 > T1 ¦ FDA SYSTEM | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable trays |  | material: gi(galvanized iron), feature: for laying all type of cables, feature: including all necessary structural supports |  | 240 | Mtr | FINISHED GOOD 2
T ¦ FINISH GODOWN 2 > T2 ¦ PA SYSTEM | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | ip based networkable touch screen paging station |  | feature: selection of zones, feature: supervision of system status, feature: setting of scheduled broadcasts, feature: central exchange with stand by cpu, feature: built-in monitoring loudspeaker, feature: goose-neck microphone, feature: lcd touchscreen display, feature: audio input |  | 1 | Nos | FINISHED GOOD 2
T ¦ FINISH GODOWN 2 > T2 ¦ PA SYSTEM | 15 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | horn type of speaker | power: 15 W | feature: high efficiency, feature: weather protection ip 65(international protection 65), feature: weatherproof type, feature: suitable for outdoor area |  | 6 | Nos | FINISHED GOOD 2
T ¦ FINISH GODOWN 2 > T2 ¦ PA SYSTEM | Rack Mounted 125 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | power amplifier | power: 125 watt | mounting: rack mounted, feature: with battery back up, feature: wattage shall be as per requirement |  | 1 | Nos | FINISHED GOOD 2
T ¦ FINISH GODOWN 2 > T2 ¦ PA SYSTEM | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | xlpe cu cable | core: 2C, cross section: 1.5 mm2 | feature: multi stranded, feature: shielded, feature: armoured, material: xlpe(xlpe cross-linked polyethylene), material: cu(copper), application: for power & signal |  | 140 | Mtr | FINISHED GOOD 2
T ¦ FINISH GODOWN 2 > T2 ¦ PA SYSTEM | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | dvd player |  | feature: with features to hook up to amplifiers of pa(public address) system for music in the common areas |  | 1 | Nos | FINISHED GOOD 2
T ¦ FINISH GODOWN 2 > T2 ¦ PA SYSTEM | Paging Loudspeaker | paging loudspeaker |  |  |  | 1 | Nos | FINISHED GOOD 2
U ¦ GARBAGE YARD > U1 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection , testing & commissioning of Deluge valve with dry pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 3/2 way Solenoid Valve, air filter regulator etc. & manual release unit. The valve shall be electro-pneumatic double inter lock system as per scheme drawing. | deluge valve |  | assembly: dry pilot trim, included: strainer, included: drain valve, included: pressure gauge, included: pressure switch, included: flame proof 3/2 way solenoid valve, included: air filter regulator, included: manual release unit, system: electro-pneumatic double inter lock, reference: as per scheme drawing |  |  |  | GARBAGE YARD
U ¦ GARBAGE YARD > U1 ¦ FOAM WATER SPRAY SYSTEM | 80 mm NB | deluge valve | size: 80 mm NB |  |  | 1 | Nos | GARBAGE YARD
U ¦ GARBAGE YARD > U1 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. | gate valve |  | material: cs(carbon steel), standard: API 600, class: 150, included: matching flanges, included: nuts & bolts |  |  |  | GARBAGE YARD
U ¦ GARBAGE YARD > U1 ¦ FOAM WATER SPRAY SYSTEM | 80 mm NB | gate valve | size: 80 mm NB |  |  | 3 | Nos | GARBAGE YARD
U ¦ GARBAGE YARD > U1 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing and commissioning of Y-Strainer. | y-strainer | [5 empty] | GARBAGE YARD
U ¦ GARBAGE YARD > U1 ¦ FOAM WATER SPRAY SYSTEM | 80 mm NB | y-strainer | size: 80 mm NB |  |  | 1 | Nos | GARBAGE YARD
U ¦ GARBAGE YARD > U1 ¦ FOAM WATER SPRAY SYSTEM | Supply,installation,testing and commissioning of Foam Sprinkler nozzle with necessary threaded fittings as per drawing. The sprinkler shall be Open Aspiration, Pendent type, K-42 with standard spray angle.End connection 1/2" NPT/BSP.UL/FM Approved. | foam sprinkler nozzle |  | fittings: necessary threaded, type: open aspiration, type: pendent, k-factor: 42, spray angle: standard, end connection: 1/2" NPT/BSP, certification: UL(underwriters laboratories), certification: FM(factory mutual) |  |  |  | GARBAGE YARD
U ¦ GARBAGE YARD > U1 ¦ FOAM WATER SPRAY SYSTEM | Spray nozzle K factor -42 | foam sprinkler nozzle | k-factor: 42 |  |  | 25 | Nos | GARBAGE YARD
U ¦ GARBAGE YARD > U1 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing and commissioning of Ratio Controller. | ratio controller |  |  |  |  | Nos | GARBAGE YARD
U ¦ GARBAGE YARD > U1 ¦ FOAM WATER SPRAY SYSTEM | 80 mm NB | ratio controller | size: 80 mm NB |  |  | 1 | Nos | GARBAGE YARD
U ¦ GARBAGE YARD > U1 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing and commissioning of Foam bladder tank vertical type ,manufacturing as per ASME, section-VIII part- I. The bladder material shall be BUNA-N. The Bladder Tank shall be supplied along with all necessary valves, Hydraulically Operated Foam Concentrae Control Valve ,fittingss & instruments as per Technical data sheet attached with Tender documents. | foam bladder tank |  | type: vertical, standard: ASME(american society of mechanical engineers) section-VIII part-I, bladder material: BUNA-N, included: all necessary valves, included: hydraulically operated foam concentrate control valve, included: fittings, included: instruments, reference: as per technical data sheet attached with tender documents |  |  |  | GARBAGE YARD
U ¦ GARBAGE YARD > U1 ¦ FOAM WATER SPRAY SYSTEM | Capacity of 500 ltr. | foam bladder tank | tank capacity: 500 ltr. |  |  | 1 | Nos | GARBAGE YARD
U ¦ GARBAGE YARD > U1 ¦ FOAM WATER SPRAY SYSTEM | Supply of AR-AFFF(3%) foam concentrate(PFOS/PFAS free) having sp. Gravity 1.0±.02 g/mlat 20⁰C , PH 7.0-8.5 & viscosity 1200 ±300 cps. | foam concentrate |  | type: AR-AFFF(3%), feature: PFOS/PFAS free, specific gravity: 1.0±.02 g/ml at 20⁰C, PH: 7.0-8.5, viscosity: 1200 ±300 cps | ar-afff(3%) | 500 | Ltr | GARBAGE YARD
U ¦ GARBAGE YARD > U1 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. | ms black steel pipe | thickness: 5.4mm | grade: heavy, standard: IS 1239 Part-1(indian standard 1239 part-1), fittings: elbows, fittings: tees, fittings: flanges, fittings: reducers, fittings: clamps, supports: ms support dash fasteners, coating: two coats of approved primer, coating: two coats of approved paint, joints: grooved with groove coupling, scope: all related civil work and supports of vendor's scope |  |  |  | GARBAGE YARD
U ¦ GARBAGE YARD > U1 ¦ FOAM WATER SPRAY SYSTEM | 80 mm NB | ms black steel pipe | size: 80 mm NB |  |  | 45 | Mtr | GARBAGE YARD
U ¦ GARBAGE YARD > U2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of IR Detector | ir detector |  |  |  | 2 | Nos | GARBAGE YARD
U ¦ GARBAGE YARD > U2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Manual Call point | manual call point |  | type: analogue addressable |  | 1 | Nos | GARBAGE YARD
U ¦ GARBAGE YARD > U2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of Hooter cum strobe | hooter cum strobe |  |  |  | 1 | Nos | GARBAGE YARD
U ¦ GARBAGE YARD > U2 ¦ FDA SYSTEM | Supply, erction, testing & commissioning of analogue addressable Control Module | control module |  | type: analogue addressable |  | 1 | Nos | GARBAGE YARD
U ¦ GARBAGE YARD > U2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Isolator Module | isolator module |  | type: analogue addressable |  | 2 | Nos | GARBAGE YARD
U ¦ GARBAGE YARD > U2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Monitor module | monitor module |  | type: analogue addressable |  | 3 | Nos | GARBAGE YARD
U ¦ GARBAGE YARD > U2 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. | armoured cabling |  | included: lugs, included: laying, included: termination of both ends |  |  |  | GARBAGE YARD
U ¦ GARBAGE YARD > U2 ¦ FDA SYSTEM | 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cabling | size: 2C x 1.5 mm2 | type: loop cable |  | 72 | Mtr | GARBAGE YARD
U ¦ GARBAGE YARD > U2 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. | armoured cabling |  | included: lugs, included: laying, included: termination of both ends |  |  |  | GARBAGE YARD
U ¦ GARBAGE YARD > U2 ¦ FDA SYSTEM | 2C x 1.5 mm2 Armoured ( Power cable) | armoured cabling | size: 2C x 1.5 mm2 | type: power cable |  | 26 | Mtr | GARBAGE YARD
U ¦ GARBAGE YARD > U2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of 6 Watt Ceiling mounted Speakers | ceiling mounted speakers | power: 6 Watt |  |  | 4 | Nos | GARBAGE YARD
U ¦ GARBAGE YARD > U2 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. | armoured cabling |  | included: lugs, included: laying, included: termination of both ends |  |  |  | GARBAGE YARD
U ¦ GARBAGE YARD > U2 ¦ FDA SYSTEM | 2C x 1.5 mm2 Armoured ( Speaker cable) | armoured cabling | size: 2C x 1.5 mm2 | type: speaker cable |  | 36 | Mtr | GARBAGE YARD
U ¦ GARBAGE YARD > U3 ¦ PA SYSTEM | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | ip based networkable touch screen paging station |  | function: selection of zones, function: supervision of system status, function: setting of scheduled broadcasts, feature: central exchange with stand by cpu, feature: built-in monitoring loudspeaker, feature: goose-neck microphone, feature: lcd touchscreen display, feature: audio input |  | 1 | Nos | GARBAGE YARD
U ¦ GARBAGE YARD > U3 ¦ PA SYSTEM | 6 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | horn type speaker | power: 6 W | feature: high efficiency, weather protection: ip 65 (weatherproof type, suitable for outdoor area) |  | 4 | Nos | GARBAGE YARD
U ¦ GARBAGE YARD > U3 ¦ PA SYSTEM | Rack Mounted 125 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | power amplifier | power: 125 watt | mounting: rack mounted, feature: battery back up, note: wattage shall be as per requirement |  | 1 | Nos | GARBAGE YARD
U ¦ GARBAGE YARD > U3 ¦ PA SYSTEM | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | xlpe cu cable | configuration: 2C x 1.5 mm2 | conductor: multi stranded, shielding: shielded, armor: armoured, application: for power & signal |  | 50 | Mtr | GARBAGE YARD
U ¦ GARBAGE YARD > U3 ¦ PA SYSTEM | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | dvd player |  | feature: hook up to amplifiers of pa system for music in the common areas |  | 1 | Nos | GARBAGE YARD
U ¦ GARBAGE YARD > U3 ¦ PA SYSTEM | Paging Loudspeaker | paging loudspeaker |  |  |  | 1 | Nos | GARBAGE YARD
V ¦ RESIN TANK | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications a ¦ 150 NB | gi pipe | size: 150 NB | class: c class (heavy class), standard: indian standard 1239, fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, fixing: clamps to ms brackets / hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, application: above ground pipes |  | 75 | Mtr | RESIN TANK
V ¦ RESIN TANK | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications b ¦ 100 NB | gi pipe | size: 100 NB | class: c class (heavy class), standard: indian standard 1239, fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, fixing: clamps to ms brackets / hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, application: above ground pipes |  | 106 | Mtr | RESIN TANK
V ¦ RESIN TANK | Supply, erection , testing & commissioning of Deluge valve with dry pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch,dry pilot actuator, air filter regulator etc. & manual release unit. a ¦ Size 150 NB | deluge valve | size: 150 NB | trim assembly: dry pilot, fitted with: strainer, drain valve, pressure gauge, pressure switch, dry pilot actuator, air filter regulator, manual release unit: included |  | 2 | Nos | RESIN TANK
V ¦ RESIN TANK | Supply, erection , testing & commissioning of Deluge valve with dry pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch,dry pilot actuator, air filter regulator etc. & manual release unit. b ¦ Size 100 NB | deluge valve | size: 100 NB | trim assembly: dry pilot, fitted with: strainer, drain valve, pressure gauge, pressure switch, dry pilot actuator, air filter regulator, manual release unit: included |  | 2 | Nos | RESIN TANK
V ¦ RESIN TANK | Providing & fixing Cast Iron Y Strainer. a ¦ Size 150 NB | y strainer | size: 150 NB | material: cast iron |  | 2 | Nos | RESIN TANK
V ¦ RESIN TANK | Providing & fixing Cast Iron Y Strainer. b ¦ Size 100 NB | y strainer | size: 100 NB | material: cast iron |  | 2 | Nos | RESIN TANK
V ¦ RESIN TANK | Supply & fixing of SS-304 FOAM GENERATOR with Minimum flow 120lpm | foam generator |  | material: ss-304, minimum flow: 120 lpm |  | 6 | Nos | RESIN TANK
V ¦ RESIN TANK | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. a ¦ Size 150 NB | gate valve | size: 150 NB | material: cs(carbon steel), standard: api 600, class: 150, flanges: matching, accessories: nuts & bolts |  | 6 | Nos | RESIN TANK
V ¦ RESIN TANK | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. b ¦ Size 100 NB | gate valve | size: 100 NB | material: cs(carbon steel), standard: api 600, class: 150, flanges: matching, accessories: nuts & bolts |  | 6 | Nos | RESIN TANK
V ¦ RESIN TANK | Supply, installation, testing and commissioning of Atmospheric Foam tank vertical type ,manufacturing as per ASME, section-VIII part- I. Tank shall be supplied along with all necessary valves, fittingss & instruments as per Technical data sheet attached with Tender documents. a ¦ Capacity of 250 ltr. | atmospheric foam tank | capacity: 250 ltr. | type: vertical, standard: asme section-viii part-i, supplied with: all necessary valves, fittings & instruments, reference: technical data sheet attached with tender documents |  | 2 | Nos | RESIN TANK
V ¦ RESIN TANK | Supply, installation, testing and commissioning of Atmospheric Foam tank vertical type ,manufacturing as per ASME, section-VIII part- I. Tank shall be supplied along with all necessary valves, fittingss & instruments as per Technical data sheet attached with Tender documents. b ¦ Capacity of 150 ltr. | atmospheric foam tank | capacity: 150 ltr. | type: vertical, standard: asme section-viii part-i, supplied with: all necessary valves, fittings & instruments, reference: technical data sheet attached with tender documents |  | 2 | Nos | RESIN TANK
V ¦ RESIN TANK | Supply of AR-AFFF(3%) foam concentrate (PFOS/PFAS free) having sp. Gravity 1.0±.02 g/mlat 20⁰C , pH 7.0-8.5 & viscosity 1200 ±300 cps. | foam concentrate |  | type: ar-afff(3%), pfos/pfas: free, specific gravity: 1.0±.02 g/ml at 20⁰c, ph: 7.0-8.5, viscosity: 1200 ±300 cps |  | 800 | Ltr | RESIN TANK
V ¦ RESIN TANK | Supply, installation, testing and commissioning of Inline Inductor a ¦ 150NB | inline inductor | size: 150NB |  |  | 2 | Nos | RESIN TANK
V ¦ RESIN TANK | b ¦ 100 NB | inline inductor | size: 100 NB |  |  | 2 | Nos | RESIN TANK
V2 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, erection , testing & commissioning of Deluge valve with wet pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 3/2 way Solenoid Valve, air filter regulator etc. & manual release unit. The valve shall be electro-pneumatic type. a ¦ 100 NB | deluge valve | size: 100 NB | trim assembly: wet pilot, included: strainer, drain valve, pressure gauge, pressure switch, solenoid valve: flame proof 3/2 way, air filter regulator: included, manual release unit: included, type: electro-pneumatic |  | 1 | Mtr | RESIN TANK
V2 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, erection , testing & commissioning of Deluge valve with wet pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 3/2 way Solenoid Valve, air filter regulator etc. & manual release unit. The valve shall be electro-pneumatic type. b ¦ 80 NB | deluge valve | size: 80 NB | trim assembly: wet pilot, included: strainer, drain valve, pressure gauge, pressure switch, solenoid valve: flame proof 3/2 way, air filter regulator: included, manual release unit: included, type: electro-pneumatic |  | 3 | Mtr | RESIN TANK
V2 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. a ¦ 100 NB | gate valve | size: 100 NB | material: cs(carbon steel), standard: API 600, class: 150, flanges: matching, included: nuts & bolts |  | 3 | Mtr | RESIN TANK
V2 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. b ¦ 80 NB | gate valve | size: 80 NB | material: cs(carbon steel), standard: API 600, class: 150, flanges: matching, included: nuts & bolts |  | 9 | Mtr | RESIN TANK
V2 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Y- Strainer a ¦ 100 NB | y-strainer | size: 100 NB |  |  | 1 | Mtr | RESIN TANK
V2 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Y- Strainer b ¦ 80 NB | y-strainer | size: 80 NB |  |  | 3 | Mtr | RESIN TANK
V2 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply,installation and commissioning of UL/FM approved Medium Velocity Water Spray Nozzle. UL/FM Approved. a ¦ MVWS nozzle K factor 18, spray angle 100⁰ | medium velocity water spray nozzle |  | approval: UL(underwriters laboratories)/FM(factory mutual), k factor: 18, spray angle: 100⁰ |  | 91 | Nos | RESIN TANK
V2 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply,installation and commissioning of UL/FM approved Quartzoid Bulb Detector for K factor-80. Temp rating 68 deg C | quartzoid bulb detector |  | approval: UL(underwriters laboratories)/FM(factory mutual), k factor: 80, temperature rating: 68 deg C |  | 91 | Nos | RESIN TANK
V2 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications a ¦ 100 NB | gi "c" class pipes | size: 100 NB | class: heavy, standard: IS 1239, fittings: threaded or grooved, included: elbow, tee, reducer, welding flanges, clamps, ms brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, application: above ground pipes |  | 14 | Mtr | RESIN TANK
V2 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications b ¦ 80 NB | gi "c" class pipes | size: 80 NB | class: heavy, standard: IS 1239, fittings: threaded or grooved, included: elbow, tee, reducer, welding flanges, clamps, ms brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, application: above ground pipes |  | 60 | Mtr | RESIN TANK
V2 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications c ¦ 65 NB | gi "c" class pipes | size: 65 NB | class: heavy, standard: IS 1239, fittings: threaded or grooved, included: elbow, tee, reducer, welding flanges, clamps, ms brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, application: above ground pipes |  | 210 | Mtr | RESIN TANK
V2 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, erction, testing & commissioning of analogue addressable Control Module | analogue addressable control module |  |  |  | 4 | Nos | RESIN TANK
V2 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, erction, testing & commissioning of analogue addressable Monitor Module | analogue addressable monitor module |  |  |  | 4 | Nos | RESIN TANK
V3 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Monitor module | analogue addressable monitor module |  |  |  | 9 | Nos | RESIN TANK
V3 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of IR Detector | ir detector |  |  |  | 9 | Nos | RESIN TANK
V3 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. a ¦ 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cabling | cable: 2C x 1.5 mm2 | feature: complete with lugs, laying and termination of both ends, type: armoured, cable type: loop cable |  | 60 | Mtr | RESIN TANK
V3 ¦ FDA SYSTEM | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable trays |  | feature: for laying all type of cables as indicated above, feature: including all necessary structural supports |  | 62 | Mtr | RESIN TANK
W ¦ EMULSION PLANT W1 ¦ FDA SYSTEM | Supply, installation, testing and commissioning of aspiration detector with CMOS imager combined with multiple photodiode for reliable very early warning in a wide range of environments with minimal nuisance alarms. The detector should have 4 pipe inlet and min 100m pipelength support per inlet.The detector should have Smart on-board filter retains dust count and remaining filter life for predictable maintenance& coverage area of min 5000 Sq. | aspiration detector | pipe inlet: 4, pipelength support per inlet: min 100m, coverage area: min 5000 Sq. | imager: CMOS, sensor: multiple photodiode, feature: very early warning, feature: minimal nuisance alarms, filter: smart on-board filter, filter feature: retains dust count and remaining filter life for predictable maintenance |  | 2 | Nos | EMULSION PLANT
W ¦ EMULSION PLANT W1 ¦ FDA SYSTEM | Supply,Installation,Testing & Commissioning of UL/VDS listed CPVC Pipe 25 mm Dia & Pipe Accessories for the Aspiration detection. | cpvc pipe | diameter: 25 mm | certification: UL, certification: VDS, application: aspiration detection, accessories: pipe accessories |  | 212 | Mtr | EMULSION PLANT
W ¦ EMULSION PLANT W1 ¦ FDA SYSTEM | Supply, erection, fabrication, testing and commission of VOC detector with range of 1 – 1000 ppm isobutylene equivalent.and following accessoriesa) DigiPID internal dust filter (Pack of 5) b) Waterproof Filter Assy, RAEGuard2 PID, Pack of 5 c) DigiPID Teflon UV electrode shield pack of 10 d) DigiPID Dust Cover e) Air Drying Pre Filter Kit f) DigiPID external water trap filter (Pack of 5) | voc detector | range: 1 – 1000 ppm isobutylene equivalent | accessories: DigiPID internal dust filter (Pack of 5), accessories: Waterproof Filter Assy, RAEGuard2 PID, Pack of 5, accessories: DigiPID Teflon UV electrode shield pack of 10, accessories: DigiPID Dust Cover, accessories: Air Drying Pre Filter Kit, accessories: DigiPID external water trap filter (Pack of 5) |  | 3 | Nos | EMULSION PLANT
W ¦ EMULSION PLANT W1 ¦ FDA SYSTEM | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable trays |  | material: GI (galvanized iron), application: laying all type of cables, feature: including all necessary structural supports |  | 18 | Mtr | EMULSION PLANT
W ¦ EMULSION PLANT W2 ¦ PA SYSTEM | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | ip based networkable touch screen paging station |  | feature: selection of zones, feature: supervision of system status, feature: setting of scheduled broadcasts, feature: central exchange with stand by CPU, feature: built-in monitoring loudspeaker, feature: goose-neck microphone, feature: LCD touchscreen display, feature: audio input |  | 1 | Nos | EMULSION PLANT
W ¦ EMULSION PLANT W2 ¦ PA SYSTEM | 30 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | horn type speaker | power: 30 W | feature: high efficiency, weather protection: IP 65, feature: weatherproof type, application: suitable for outdoor area |  | 4 | Nos | EMULSION PLANT
W ¦ EMULSION PLANT W2 ¦ PA SYSTEM | Rack Mounted 125 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | power amplifier | power: 125 watt | mounting: rack mounted, feature: battery back up, feature: wattage shall be as per requirement |  | 1 | Nos | EMULSION PLANT
W ¦ EMULSION PLANT W2 ¦ PA SYSTEM | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | xlpe cu cable | core: 2C, cross section: 1.5 mm2 | feature: multi stranded, feature: shielded, feature: armoured, application: power & signal |  | 150 | Mtr | EMULSION PLANT
W ¦ EMULSION PLANT W2 ¦ PA SYSTEM | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | dvd player |  | feature: hook up to amplifiers of PA system, application: music in the common areas |  | 1 | Nos | EMULSION PLANT
W ¦ EMULSION PLANT W2 ¦ PA SYSTEM | Paging Loudspeaker | paging loudspeaker |  |  |  | 1 | Nos | EMULSION PLANT
['PLC AUTOMATION'] | SUPPLY & INSTALLATION OF PLC BASED DV CONTROL PANEL FOR FOAM SPRINKLER SYSTEM AND FIRE WATER PUMPING SYSTEM INTERGRATION PANEL WITH PLC. Supply,Installation,Termination of cable,Testing and Commissioning of PLC Based Deluge Valve Control Panel with accessories. The panel should have local push botton switched for emergency operation from panel.Panel and associated accessories shall be designed to withstand environmental conditions at site.Panel in open areas shall be weatherproof to IP-65 as per IS/ IEC-60529. Canopy/Shed of adequate sizes shall be provided for each panel to protect from weather, the cost of the same shall be included in the panel cost.No extra payment shall be made for providing fixture , fittings & accessories. PLC Based DELUGE VALVE CONTROL PANEL should contain the following:- 1. Programmable Logic Controller. 2.Solid State type or microprocessor based programmable type Alarm Annunciator with sounder. 3.UPS. 4.Cables (Power & Control) Specification of Programmable Logic Controller (PLC) : 1.Input Power: 24vdc,Redundant Supply. 2.Application capabilities with up to 7 expansion I/O modules for a maximum of 256 discrete I/O. 3.Up to 6 embedded 100 kHz highspeed counters (on controllers with dc inputs) 4.2 Serial ports with DF1/ DH485/Modbus RTU/DNP3/ASCII protocol support. 5.Ethernet port provides you with EtherNet/IP, DNP3 over IP and Modbus TCP/IP protocol support as well as web server and email capabilities. 6.Built-in LCD with backlight allows you to view controller and I/O status, and provides a simple interface for messages, bit / integer monitoring and manipulation. 9.Memory:non-volatile battery backed RAM. 10.online editing:yes. 11.Operating Temp.:-20°C...+60°C. 12.Storage Temp:-40°C (or -30°C)...+85°C. Specification of Solid State type or microprocessor based programmable type Alarm Annunciator with sounder: Window display shall be back lighted incandescent lamps or cluster LED type integral power supply. Specification of UPS: 1.Alarm Condition: 1 hours. 2.Standalone Condition: 4 Hours. For 22 nos. Deluge Valve IO point 3 nos (22 W + 3 S)-SOLVENT PLANT | plc based deluge valve control panel | deluge valve io point: 22 nos, panel: 3 nos (22 W + 3 S) | system: foam sprinkler system and fire water pumping system integration, operation: local push button switches for emergency, weatherproof: IP-65 as per IS/ IEC-60529, canopy: included, accessories: included, controller: programmable logic controller, alarm annunciator: solid state or microprocessor based programmable type with sounder, ups: included, cables: power & control, plc input power: 24vdc, redundant supply, expansion: up to 7 expansion I/O modules, max discrete I/O: 256, highspeed counters: up to 6 embedded 100 kHz, serial ports: 2 with DF1/ DH485/Modbus RTU/DNP3/ASCII protocol support, ethernet: EtherNet/IP, DNP3 over IP, Modbus TCP/IP, web server, email, lcd: built-in with backlight, memory: non-volatile battery backed RAM, online editing: yes, operating temperature: -20°C...+60°C, storage temperature: -40°C (or -30°C)...+85°C, annunciator window display: back lighted incandescent lamps or cluster LED type integral power supply, ups alarm condition: 1 hour, ups standalone condition: 4 hours |  | 2 | Set | PLC AUTOMATION
['PLC AUTOMATION'] | For 3 nos. Deluge Valve IO point 1 nos (3 W + 1 S)-RESIN PLANT | plc based deluge valve control panel | deluge valve io point: 3 nos, panel: 1 nos (3 W + 1 S) | location: resin plant |  | 1 | Set | PLC AUTOMATION
['PLC AUTOMATION'] | For 2 nos. Deluge Valve IO point 1 nos (2 W + 1 S) -,MONOMER & STYRENE | plc based deluge valve control panel | deluge valve io point: 2 nos, panel: 1 nos (2 W + 1 S) | location: monomer & styrene |  | 1 | Set | PLC AUTOMATION
['PLC AUTOMATION'] | For 4 nos. Deluge Valve IO point 1 nos(4 W + 1 S) -WATER BASED PLANT | plc based deluge valve control panel | deluge valve io point: 4 nos, panel: 1 nos (4 W + 1 S) | location: water based plant |  | 2 | Sets | PLC AUTOMATION
['PLC AUTOMATION'] | For 2 nos. Deluge Valve IO point 1 nos (2 W + 1 S)-SUBSTATION BUILDING | plc based deluge valve control panel | deluge valve io point: 2 nos, panel: 1 nos (2 W + 1 S) | location: substation building |  | 1 | Set | PLC AUTOMATION
['PLC AUTOMATION'] | For 1 nos. Deluge Valve IO point 1 nos (1 W + 1 S) -,SOFA AREA | plc based deluge valve control panel | deluge valve io point: 1 nos, panel: 1 nos (1 W + 1 S) | location: sofa area |  | 1 | Set | PLC AUTOMATION
['PLC AUTOMATION'] | For 1 nos. Deluge Valve IO point 1 nos (1 W + 1 S)-PTC | plc based deluge valve control panel | deluge valve io point: 1 nos, panel: 1 nos (1 W + 1 S) | location: ptc |  | 1 | Set | PLC AUTOMATION
['PLC AUTOMATION'] | For 1 nos. Deluge Valve IO point 1 nos (1 W + 1 S) -,FG-1 | plc based deluge valve control panel | deluge valve io point: 1 nos, panel: 1 nos (1 W + 1 S) | location: fg-1 |  | 1 | Set | PLC AUTOMATION
['PLC AUTOMATION'] | For 1 nos. Deluge Valve IO point 1 nos(1 W + 1 S) -,MONOMER COLD ROOM | plc based deluge valve control panel | deluge valve io point: 1 nos, panel: 1 nos (1 W + 1 S) | location: monomer cold room |  | 1 | Set | PLC AUTOMATION
['PLC AUTOMATION'] | For 2 nos. Deluge Valve IO point 1 nos (2 W + 1 S) - DEG & MEG TANK FIRM | plc based deluge valve control panel | deluge valve io point: 2 nos, panel: 1 nos (2 W + 1 S) | location: deg & meg tank firm |  | 1 | Set | PLC AUTOMATION
['PLC AUTOMATION'] | For 8 nos. Deluge Valve IO point 1 nos (8 W + 1 S) - resin TANK FIRM foam generator & MVWS. | plc based deluge valve control panel | deluge valve io point: 8 nos, panel: 1 nos (8 W + 1 S) | location: resin tank firm foam generator & mvws |  | 1 | Set | PLC AUTOMATION
['PLC AUTOMATION'] | For 4 nos. Deluge Valve IO point 1 nos(4 W + 1 S) - SOFA TANK area foam generator. | plc based deluge valve control panel | deluge valve io point: 4 nos, panel: 1 nos (4 W + 1 S) | location: sofa tank area foam generator |  | 1 | Set | PLC AUTOMATION
['PLC AUTOMATION'] | For 2 nos. Deluge Valve IO point 1 nos(2 W + 1 S) - styrene & monomer tank area foam generator. | plc based deluge valve control panel | deluge valve io point: 2 nos, panel: 1 nos (2 W + 1 S) | location: styrene & monomer tank area foam generator |  | 1 | Set | PLC AUTOMATION
['PLC AUTOMATION'] | For 2 nos. Deluge Valve IO point 1 nos (2 W + 1 S) - raw material curtain. | plc based deluge valve control panel | deluge valve io point: 2 nos, panel: 1 nos (2 W + 1 S) | location: raw material curtain |  | 1 | Set | PLC AUTOMATION
['PLC AUTOMATION'] | For 2 Nos. Electric Motor driven Pump,2 Nos. of Diesel Engine driven Pump,2 nos. of Jockey Pumps, Air Compressor running-"ON" & "OFF" Condition. | plc based deluge valve control panel | electric motor driven pump: 2 nos, diesel engine driven pump: 2 nos, jockey pumps: 2 nos | air compressor: running "ON" & "OFF" condition |  | 1 | Set | PLC AUTOMATION
['PLC AUTOMATION'] | SUPPLY & ERECTION OF HMI PC Supply,Installation and Commissioning of HMI PC with all accessories complete in all respect and UPS of suitable capacity capable supply power for atleast 1 hour in Alarm Condition & 4 hours in Standalone Condition. (Two Sets of HMI PC shall be provided in two different Locations, one at Control Room/Security Cabin and another at Admin Block) Specification of HMI PC: 1.Site specific HMI software and provision for stimulation DV System. 2.HMI Software for one user with paper licence. 3.Harddisk:1TB. 4.RAM: 8 GB. 5.Display:21" LED. 6.OS: windows lateset professional version. 7.DVD drive ± R/RW 16X. 8.Processor 32 bit Intel Xeon Quad Core Processor with 2.8 GHz. 9.Graphics NVIDIA Quadro 600 with 1GB video memory. 10.event history:min 1 month. | hmi pc | harddisk: 1TB, ram: 8 GB, display: 21" | ups: suitable capacity for 1 hour alarm, 4 hours standalone, hmi software: site specific, provision for stimulation dv system, licence: paper, os: windows latest professional version, dvd drive: ± R/RW 16X, processor: 32 bit intel xeon quad core 2.8 GHz, graphics: nvidia quadro 600 with 1GB video memory, event history: min 1 month, location: control room/security cabin and admin block |  | 2 | Sets | PLC AUTOMATION
Y ¦ PANEL SUPPRESSION SYSTEM | FIRETRACE Direct Low Pressure (DLP) Novec 1230 4 Kgs. System, supplied complete with differential pressure valve, Novec 1230, Pressure Gauage,with panel mounting bracket. (CE Approved) | firetrace direct low pressure novec 1230 system | system capacity: 4 kgs | type: direct low pressure (DLP), extinguishing agent: novec 1230, included: differential pressure valve, pressure gauge, panel mounting bracket, certification: CE approved | dlp novec 1230 system | 32 | Nos | PANEL SUPPRESSION SYSTEM
Y ¦ PANEL SUPPRESSION SYSTEM | FIRETRACE Direct Low Pressure (DLP) Novec 1230 2 Kgs. System, supplied complete with differential pressure valve, Novec 1230, Pressure Gauage,with panel mounting bracket. (CE Approved) | firetrace direct low pressure novec 1230 system | system capacity: 2 kgs | type: direct low pressure (DLP), extinguishing agent: novec 1230, included: differential pressure valve, pressure gauge, panel mounting bracket, certification: CE approved | dlp novec 1230 system | 7 | Nos | PANEL SUPPRESSION SYSTEM
Y ¦ PANEL SUPPRESSION SYSTEM | FIRETRACE Direct Low Pressure (DLP) Novec 1230 1 Kgs. System, supplied complete with differential pressure valve, Novec 1230, Pressure Gauage,with panel mounting bracket. (CE Approved) | firetrace direct low pressure novec 1230 system | system capacity: 1 kgs | type: direct low pressure (DLP), extinguishing agent: novec 1230, included: differential pressure valve, pressure gauge, panel mounting bracket, certification: CE approved | dlp novec 1230 system | 3 | Nos | PANEL SUPPRESSION SYSTEM
Y ¦ PANEL SUPPRESSION SYSTEM | Pressure Switch | pressure switch |  |  |  | 42 | Nos | PANEL SUPPRESSION SYSTEM
Y ¦ PANEL SUPPRESSION SYSTEM | End of line Adaptor with pressure Gauge | end of line adaptor |  | included: pressure gauge |  | 42 | Nos | PANEL SUPPRESSION SYSTEM
Y ¦ PANEL SUPPRESSION SYSTEM | Firetrace 4/6 Linear Pneumatic Heat detection tube kit, (Standard) | firetrace linear pneumatic heat detection tube kit |  | type: 4/6 linear, standard: standard |  | 610 | Mtr | PANEL SUPPRESSION SYSTEM
Y ¦ PANEL SUPPRESSION SYSTEM | 6mm End Plug | end plug | size: 6mm |  |  | 84 | Nos | PANEL SUPPRESSION SYSTEM
Y ¦ PANEL SUPPRESSION SYSTEM | 6mm Equal TEE | equal tee | size: 6mm |  |  | 84 | Nos | PANEL SUPPRESSION SYSTEM
Y ¦ PANEL SUPPRESSION SYSTEM | Master Control Unit | master control unit |  |  |  | 42 | Nos | PANEL SUPPRESSION SYSTEM
Y ¦ PANEL SUPPRESSION SYSTEM | Supply, erection, testing & commissioning of analogue addressable Monitor module | analogue addressable monitor module |  | feature: supply, erection, testing & commissioning |  | 42 | Nos | PANEL SUPPRESSION SYSTEM
Y ¦ PANEL SUPPRESSION SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. | armoured cabling |  | included: lugs, laying and termination of both ends |  |  |  | PANEL SUPPRESSION SYSTEM
Y ¦ PANEL SUPPRESSION SYSTEM | 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cable | configuration: 2C x 1.5 mm2 | type: loop cable |  | 3200 | Mtr | PANEL SUPPRESSION SYSTEM
Z ¦ GAS LEAK DETECTION | Supply, erection, fabrication, testing and commission of VOC detector with range of 1 – 1000 ppm isobutylene equivalent.and following accessoriesa) DigiPID internal dust filter (Pack of 5) b) Waterproof Filter Assy, RAEGuard2 PID, Pack of 5 c) DigiPID Teflon UV electrode shield pack of 10 d) DigiPID Dust Cover e) Air Drying Pre Filter Kit f) DigiPID external water trap filter (Pack of 5) | voc detector | range: 1 – 1000 ppm isobutylene equivalent | accessories: DigiPID internal dust filter (Pack of 5), Waterproof Filter Assy, RAEGuard2 PID (Pack of 5), DigiPID Teflon UV electrode shield (pack of 10), DigiPID Dust Cover, Air Drying Pre Filter Kit, DigiPID external water trap filter (Pack of 5) |  | 5 | Nos | GAS LEAK DETECTION
Z ¦ GAS LEAK DETECTION | Supply, erection, fabrication, testing and commission of IR based LEL Detector, includes nylon weather protection. | lel detector |  | type: IR based, feature: nylon weather protection |  | 4 | Nos | GAS LEAK DETECTION
Z ¦ GAS LEAK DETECTION | Supply, erection, fabrication, testing and commission of Ex proof Hooter & Beacon. | hooter and beacon |  | feature: explosion proof |  | 5 | Nos | GAS LEAK DETECTION
Z ¦ GAS LEAK DETECTION | Supply, erection, fabrication, testing and commission of Local Display (VOC monitoring) unit. | local display unit |  | feature: VOC monitoring |  | 1 | Nos | GAS LEAK DETECTION
Z ¦ GAS LEAK DETECTION | Supply, erection, fabrication, testing and commission of Micro-controller based, multi-channel monitoring and control of Gas Sensors 39 channel. | monitoring and control unit | channels: 39 | feature: micro-controller based, feature: multi-channel monitoring and control of gas sensors |  | 1 | Nos | GAS LEAK DETECTION
Z ¦ GAS LEAK DETECTION | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. a ¦ 3C x 2.5 mm2 Armoured | armoured cabling | configuration: 3C x 2.5 mm2 | feature: complete with lugs, laying and termination of both ends |  | 1600 | Mtr | GAS LEAK DETECTION