## Sheet1
section_context_for_this_product_block | full_product_description | core_product_name | size | feature_or_specifications | acronymed_core_product_name | quantity | unit
E ¦ ADMIN BUILDING; E1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be of grooved with groove coupling. all escavation & back filling, pedestal support, structural support shall be of vendor's scope. 100 mm NB | ms black steel pipe | size: 100 mm NB | grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, scope: all excavation & back filling, pedestal support, structural support by vendor |  | 36.0 | Mtr
E ¦ ADMIN BUILDING; E1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be of grooved with groove coupling. all escavation & back filling, pedestal support, structural support shall be of vendor's scope. 80 mm NB | ms black steel pipe | size: 80 mm NB | grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, scope: all excavation & back filling, pedestal support, structural support by vendor |  | 36.0 | Mtr
E ¦ ADMIN BUILDING; E1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be of grooved with groove coupling. all escavation & back filling, pedestal support, structural support shall be of vendor's scope. 25 mm NB | ms black steel pipe | size: 25 mm NB | grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, scope: all excavation & back filling, pedestal support, structural support by vendor |  | 18.0 | Mtr
E ¦ ADMIN BUILDING; E1 ¦ HYDRANT SYSTEM | Supply & installation of swinging type hose reel drum fabricated from 14 SWG CRCA sheets painted with red colour stove paint 2 coats over 1 coat of primer with 30 m long 20 mm dia rubber hose pipe with with SS self closing shut – off nozzle of 5 mm outlet fixed on wall. | hose reel drum | hose length: 30 m, hose diameter: 20 mm, nozzle outlet: 5 mm | type: swinging, material: 14 SWG CRCA sheets, painting: red colour stove paint 2 coats over 1 coat of primer, nozzle: ss(stainless steel) self closing shut-off, mounting: fixed on wall |  | 3.0 | Nos
E ¦ ADMIN BUILDING; E1 ¦ HYDRANT SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends Size 25NB | globe valve | size: 25NB | material: bronze, standard: indian standard 778, ends: screwed |  | 3.0 | Nos
E ¦ ADMIN BUILDING; E1 ¦ HYDRANT SYSTEM | Supply & installation of SS oblique type single headed Landing valve with 80 mm inlet and 63 mm outlet SS instantaneous male coupling with rubber cap and chain conforming to IS : 5290 including matching flanges, gasket, nuts and bolts complete. Size 80 mm NB | landing valve | inlet: 80 mm, outlet: 63 mm, size: 80 mm NB | material: ss(stainless steel), type: oblique, head: single, coupling: ss(stainless steel) instantaneous male, accessories: rubber cap and chain, standard: indian standard 5290, includes: matching flanges, gasket, nuts and bolts |  | 3.0 | Nos
E ¦ ADMIN BUILDING; E1 ¦ HYDRANT SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. | butterfly valve |  | standard: british standard 5155, type: wafer, includes: matching flanges, nuts & bolts, fittings: provided by erection vendor |  | 2.0
E ¦ ADMIN BUILDING; E1 ¦ HYDRANT SYSTEM | Supply & installation of SS branch pipe with 20 mm nozzle conforming to IS : 903 complete | branch pipe | nozzle: 20 mm | material: ss(stainless steel), standard: indian standard 903 |  | 2.0 | Nos
E ¦ ADMIN BUILDING; E1 ¦ HYDRANT SYSTEM | Supply & installation of 63 mm dia rubberized reinforced rubber line hose pipe in 15 m length conforming to IS : 636 Type II ISI marked with gunmetal male and female instantaneous coupling conforming to IS 903 wounded with 18 SWG copper wire complete | rubber line hose pipe | diameter: 63 mm, length: 15 m | type: rubberized reinforced, standard: indian standard 636 type ii, certification: ISI, coupling: gunmetal male and female instantaneous, coupling standard: indian standard 903, wire: 18 SWG copper |  | 4.0 | Nos
E ¦ ADMIN BUILDING; E1 ¦ HYDRANT SYSTEM | Supply & installation of MS Hose Box of fabricated from 16 SWG CRCA sheet double door with lockable arrangements to accommodate 2 RRL hose of 15 m length and one branch pipe painted white inside and red outside with one key. (750X600X250 mm) | hose box | dimensions: 750X600X250 mm | material: ms(mild steel), sheet: 16 SWG CRCA, doors: double, lockable: yes, accommodates: 2 RRL hose of 15 m length and one branch pipe, painting: white inside and red outside, includes: one key |  | 2.0 | Nos
E ¦ ADMIN BUILDING; E2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be of grooved with groove couplings. All related civil work viz as wall cutting, structural supports etc for laying of sprinkler piping shall be vendor's scope. 40 mm NB | ms black steel pipe | size: 40 mm NB | grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove couplings, civil work: wall cutting, structural supports for laying of sprinkler piping by vendor |  | 18.0 | Mtr
E ¦ ADMIN BUILDING; E2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be of grooved with groove couplings. All related civil work viz as wall cutting, structural supports etc for laying of sprinkler piping shall be vendor's scope. 25 mm NB | ms black steel pipe | size: 25 mm NB | grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove couplings, civil work: wall cutting, structural supports for laying of sprinkler piping by vendor |  | 72.0 | Mtr
E ¦ ADMIN BUILDING; E2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. Size100 mm NB | butterfly valve | size: 100 mm NB | standard: british standard 5155, type: wafer, fittings: matching flanges, nuts & bolts, feature: necessary fittings by erection vendor |  | 1.0 | Nos
E ¦ ADMIN BUILDING; E2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. Size80 mm NB | butterfly valve | size: 80 mm NB | standard: british standard 5155, type: wafer, fittings: matching flanges, nuts & bolts, feature: necessary fittings by erection vendor |  | 1.0 | Nos
E ¦ ADMIN BUILDING; E2 ¦ AUTOMATIC SPRINKLER SYSTEM | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts confirming to API 594. Size100 mm NB | non return valve | size: 100 mm NB | type: wafer, fittings: matching flanges, nuts & bolts, standard: api 594 |  | 1.0 | Nos
E ¦ ADMIN BUILDING; E2 ¦ AUTOMATIC SPRINKLER SYSTEM | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts confirming to API 594. Size80 mm NB | non return valve | size: 80 mm NB | type: wafer, fittings: matching flanges, nuts & bolts, standard: api 594 |  | 1.0 | Nos
E ¦ ADMIN BUILDING; E2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & fixing of paddle type Flow Switch | flow switch |  | type: paddle |  | 2.0 | Nos
E ¦ ADMIN BUILDING; E2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Fixing of Sprinkler Head Pendent type for K factor-80. Temp rating 68 deg C. UL/FM Approved. | sprinkler head pendent type | k factor: 80 | temperature rating: 68 deg c, certification: ul, certification: fm |  | 34.0 | Nos
E ¦ ADMIN BUILDING; E2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, installation of automatic 25 NB Air Release Valve | air release valve | size: 25 NB | feature: automatic |  | 1.0 | Nos
E ¦ ADMIN BUILDING; E2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends Size 40NB | globe valve | size: 40 NB | material: bronze, standard: indian standard 778, ends: screwed |  | 2.0 | Nos
E ¦ ADMIN BUILDING; E2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends Size 25NB | globe valve | size: 25 NB | material: bronze, standard: indian standard 778, ends: screwed |  | 2.0 | Nos
E ¦ ADMIN BUILDING; E2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Erection and testing of Installation Control Valve complete with trims & gong. Size 100 mm NB | installation control valve | size: 100 mm NB | feature: complete with trims & gong |  | 1.0 | Nos
E ¦ ADMIN BUILDING; E2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, Class 150 with matching flanges complete with nuts & bolts. Size 100 mm NB | gate valve | size: 100 mm NB | material: cs(carbon steel), standard: api 600, class: 150, fittings: matching flanges, nuts & bolts |  | 1.0 | Nos
E ¦ ADMIN BUILDING; E3 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Manual Call point | manual call point |  | type: analogue addressable |  | 4.0 | Nos
E ¦ ADMIN BUILDING; E3 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of Hooter cum strobe | hooter cum strobe |  |  |  | 4.0 | Nos
E ¦ ADMIN BUILDING; E3 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of Telephone jack. | telephone jack |  |  |  | 2.0 | Nos
E ¦ ADMIN BUILDING; E3 ¦ FDA SYSTEM | Supply, erction, testing & commissioning of analogue addressable Control Module | control module |  | type: analogue addressable |  | 2.0 | Nos
E ¦ ADMIN BUILDING; E3 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Isolator Module | isolator module |  | type: analogue addressable |  | 2.0 | Nos
E ¦ ADMIN BUILDING; E3 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Monitor module | monitor module |  | type: analogue addressable |  | 2.0 | Nos
E ¦ ADMIN BUILDING; E3 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. a ¦ 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cabling | cable: 2C x 1.5 mm2 | feature: loop cable, feature: armoured, feature: complete with lugs, laying and termination of both ends |  | 170.0 | Mtr
E ¦ ADMIN BUILDING; E3 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. a ¦ 2C x 1.5 mm2 Armoured ( Power cable) | armoured cabling | cable: 2C x 1.5 mm2 | feature: power cable, feature: armoured, feature: complete with lugs, laying and termination of both ends |  | 104.0 | Mtr
E ¦ ADMIN BUILDING; E3 ¦ FDA SYSTEM | Providing & fixing FRLS CABLING complete with lugs, laying and termination of both ends. a ¦ 2C x 0.5 mm2 Armoured ( Telephone cable) | frls cabling | cable: 2C x 0.5 mm2 | feature: telephone cable, feature: armoured, feature: complete with lugs, laying and termination of both ends |  | 28.0 | Mtr
E ¦ ADMIN BUILDING; E3 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. a ¦ 2C x 1.5 mm2 Armoured ( Speaker cable) | armoured cabling | cable: 2C x 1.5 mm2 | feature: speaker cable, feature: armoured, feature: complete with lugs, laying and termination of both ends |  | 164.0 | Mtr
E ¦ ADMIN BUILDING; E3 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of Repeater Panel | repeater panel |  |  |  | 1.0 | Nos
E ¦ ADMIN BUILDING; E3 ¦ FDA SYSTEM | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | ip based networkable touch screen paging station |  | feature: selection of zones, supervision of system status, setting of scheduled broadcasts, central exchange with stand by CPU, built-in monitoring loudspeaker, goose-neck microphone, LCD touchscreen display, audio input |  | 1.0 | Nos
E ¦ ADMIN BUILDING; E3 ¦ FDA SYSTEM | 6 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | horn type of speaker | power: 6 W | feature: high efficiency, weather protection IP 65 (weatherproof type, suitable for outdoor area) |  | 21.0 | Nos
E ¦ ADMIN BUILDING; E3 ¦ FDA SYSTEM | Rack Mounted 200 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | power amplifier | power: 200 watt | feature: rack mounted, battery back up, wattage shall be as per requirement |  | 1.0 | Nos
E ¦ ADMIN BUILDING; E3 ¦ FDA SYSTEM | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | xlpe cu cable | core: 2C, cross section: 1.5 mm2 | feature: multi stranded, shielded, armoured, for power & signal |  | 164.0 | Mtr
E ¦ ADMIN BUILDING; E3 ¦ FDA SYSTEM | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | dvd player |  | feature: hook up to amplifiers of PA system for music in the common areas |  | 1.0 | Nos
E ¦ ADMIN BUILDING; E3 ¦ FDA SYSTEM | Paging Loudspeaker | paging loudspeaker |  |  |  | 1.0 | Nos