## Sheet1
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
L | COLORANT STORE
L1 | HYDRANT SYSTEM
1 | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope.
a | 150 mm NB | Mtr | 36
b | 80 mm NB | Mtr | 12
c | 25 mm NB | Mtr | 6
2 | Supply & installation of SS oblique type single headed Landing valve with 80 mm inlet and 63 mm outlet SS instantaneous male coupling with rubber cap and chain conforming to IS : 5290 including matching flanges, gasket, nuts and bolts complete. | Nos | 8
3 | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor.
a | Size 80 mm NB | Nos | 8
4 | Supply & installation of SS branch pipe with 20 mm nozzle conforming to IS : 903 complete | Nos | 8
5 | Supply & installation of 63 mm dia rubberized reinforced rubber line hose pipe in 15 m length conforming to IS : 636 Type II ISI marked with gunmetal male and female instantaneous coupling conforming to IS 903 wounded with 18 SWG copper wire complete | Nos | 16
6 | Supply & installation of MS Hose Box of fabricated from 16 SWG CRCA sheet double door with lockable arrangements to accommodate 2 RRL hose of 15 m length and one branch pipe painted white inside and red outside with one key. (750X600X250 mm) | Nos | 8
7 | Supply & installation of swinging type hose reel drum fabricated from 14 SWG CRCA sheets painted with red colour stove paint 2 coats over 1 coat of primer with 30 m long 20 mm dia rubber hose pipe with with SS self closing shut – off nozzle of 5 mm outlet fixed on wall. | Nos | 8
8 | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends
a | Size 25NB | Nos | 4
b | Size 40NB | Nos | 8
L2 | FDA SYSTEM
1 | Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | Nos | 141
2 | Supply, erection, testing & commissioning of analogue addressable Manual Call point | Nos | 15
3 | Supply, erection, testing & commissioning of Hooter cum strobe | Nos | 14
4 | Supply, erection, testing & commissioning of Telephone jack. | Nos | 8
5 | Supply, erction, testing & commissioning of analogue addressable Control Module | Nos | 5
6 | Supply, erection, testing & commissioning of analogue addressable Isolator Module | Nos | 4
7 | Supply, erection, testing & commissioning of analogue addressable Monitor module | Nos | 4
8 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Loop cable) | Mtr | 1170
9 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Power cable) | Mtr | 401
10 | Providing & fixing FRLS CABLING complete with lugs, laying and termination of both ends.
a | 2C x 0.5 mm2 Armoured ( Telephone cable) | Mtr | 327
11 | Supply, erection, testing & commissioning of 6 Watt Ceiling mounted Speakers | Nos | 80
12 | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends.
a | 2C x 1.5 mm2 Armoured ( Speaker cable) | Mtr | 1027
13 | Providing & fixing 600Watt Amplifier with necessary accessories. | Nos | 1
14 | Supply, installation, testing and commissioning of aspiration detector with CMOS imager combined with multiple photodiode for reliable very early warning in a wide range of environments with minimal nuisance alarms. The detector should have 4 pipe inlet and min 100m pipelength support per inlet.The detector should have Smart on-board filter retains dust count and remaining filter life for predictable maintenance& coverage area of min 5000 Sq. | Nos | 4
15 | Supply,Installation,Testing & Commissioning of UL/VDS listed CPVC Pipe 25 mm Dia & Pipe Accessories for the Aspiration detection. | Mtr | 744
16 | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | Mtr | 1170
L3 | PA SYSTEM
1 | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | Nos | 1
2 | 30 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | Nos | 8
3 | 9 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | Nos | 1
4 | 6 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | Nos | 23
5 | Rack Mounted 400 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | Nos | 1
6 | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | Mtr | 541
7 | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | Nos | 1
8 | Paging Loudspeaker | Nos | 1
TOTAL