## Sheet1
section_context_for_this_product_block | full_product_description | core_product_name | size | feature_or_specifications | acronymed_core_product_name | quantity | unit
B. ¦ EXTERNAL HYDRANT, SPRINKLER LINE & FDA | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cabling | core: 2C, cross section: 1.5 mm2 | type: loop cable, feature: complete with lugs, laying and termination of both ends |  | 1820 | Mtr
B. ¦ EXTERNAL HYDRANT, SPRINKLER LINE & FDA | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 1.5 mm2 Armoured ( Power cable) | armoured cabling | core: 2C, cross section: 1.5 mm2 | type: power cable, feature: complete with lugs, laying and termination of both ends |  | 1320 | Mtr
B. ¦ EXTERNAL HYDRANT, SPRINKLER LINE & FDA | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. 2C x 0.5 mm2 Armoured ( Telephone cable) | armoured cabling | core: 2C, cross section: 0.5 mm2 | type: telephone cable, feature: complete with lugs, laying and termination of both ends |  | 1200 | Mtr
B. ¦ EXTERNAL HYDRANT, SPRINKLER LINE & FDA | Supply, erection, fabrication, testing of MS black steel pipe of 7 mm Heavy grade conforming to IS : 3589 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipes shall be erected with grooved joints only. All sorts of escavation, pedestal support and structural support shall be of vendor's scope. 200 NB(FOR REVAMPING OF HYDRANT LINE) | ms black steel pipe | nominal bore: 200 NB, thickness: 7 mm | material: ms(black steel), grade: heavy, standard: indian standard 3589 part-1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, coating: two coats of approved primer and two coats of approved paint, joint type: grooved, feature: all sorts of excavation, pedestal support and structural support shall be of vendor's scope |  | 250 | Mtr
B. ¦ EXTERNAL HYDRANT, SPRINKLER LINE & FDA | Supply, erection, fabrication, testing of MS black steel pipe of 7 mm Heavy grade conforming to IS : 3589 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipes shall be erected with grooved joints only. All sorts of escavation, pedestal support and structural support shall be of vendor's scope. 200 NB(FOR EXTERNAL SPRINKLER LINE) | ms black steel pipe | nominal bore: 200 NB, thickness: 7 mm | material: ms(black steel), grade: heavy, standard: indian standard 3589 part-1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, coating: two coats of approved primer and two coats of approved paint, joint type: grooved, feature: all sorts of excavation, pedestal support and structural support shall be of vendor's scope |  | 1040 | Mtr
B. ¦ EXTERNAL HYDRANT, SPRINKLER LINE & FDA | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, Class 150, with matching flanges complete with nuts & bolts. (IN SPRINKLER LINE) 200 mm NB | gate valve | nominal bore: 200 mm | material: cs(carbon steel), standard: api 600, class: 150, feature: with matching flanges complete with nuts & bolts, application: in sprinkler line |  | 3 | Nos
B. ¦ EXTERNAL HYDRANT, SPRINKLER LINE & FDA | Supply, fabrication and erection of MS Structural material for various kind of supports consistes of angle, channels, I sections, plates etc including nuts, bolts and washers. | ms structural material |  | material: ms(mild steel), feature: for various kind of supports consists of angle, channels, I sections, plates etc including nuts, bolts and washers |  | 35000 | kg
B. ¦ EXTERNAL HYDRANT, SPRINKLER LINE & FDA | Supply, erection, testing & commissioning of analogue addressable outdoor type Manual Call point explosion proof complete with fittings and accessories. | manual call point |  | type: analogue addressable, application: outdoor, feature: explosion proof, feature: complete with fittings and accessories |  | 52 | Nos
B. ¦ EXTERNAL HYDRANT, SPRINKLER LINE & FDA | Supply, erection, testing & commissioning of External Hooter cum strobe(IP 67 rating) complete with fittings and accessories. | external hooter cum strobe |  | ip rating: 67, feature: complete with fittings and accessories |  | 52 | Nos
B. ¦ EXTERNAL HYDRANT, SPRINKLER LINE & FDA | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable trays |  | material: gi(galvanized iron), application: for laying all type of cables as indicated above, feature: including all necessary structural supports |  | 1820 | Mtr
B. ¦ EXTERNAL HYDRANT, SPRINKLER LINE & FDA | Supply & installation of portable foam tank of 250 ltr. | portable foam tank | tank capacity: 250 ltr |  |  | R/O | Nos
B. ¦ EXTERNAL HYDRANT, SPRINKLER LINE & FDA | Supply & installation of FOAM WATER MONITOR 65NB water passage with 32nb Nozzle bore having 1750 lpm flow and 360 degree rotation with compaitable accessories. | foam water monitor | water passage: 65NB, nozzle bore: 32nb, flow: 1750 lpm | feature: 360 degree rotation, feature: with compatible accessories |  | R/O | Nos
B. ¦ EXTERNAL HYDRANT, SPRINKLER LINE & FDA | Supply, erection, testing & commissioning of Air Compressor with motor,mounted on a common base frame with air receiver tank. The set shall be fitted with dry suction filter, diaphragm,automatic venting device, safety valve, pressure gauge cooler, motor starter etc. The compressor shall be of capacity 25 M³/Hr( FAD), discharge pressure 10 bar, single stage, reciprocating type | air compressor | capacity: 25 M³/Hr (FAD), discharge pressure: 10 bar | mounting: common base frame with air receiver tank, feature: dry suction filter, feature: diaphragm, feature: automatic venting device, feature: safety valve, feature: pressure gauge cooler, feature: motor starter, type: single stage, type: reciprocating |  | 2 | Nos
B. ¦ EXTERNAL HYDRANT, SPRINKLER LINE & FDA | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications ¦ 50 NB | gi c class pipe | diameter: 50 NB | class: c class (heavy class), standard: indian standard 1239, fitting: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, fixing: clamps to ms brackets / hangers, steel supports, coating: zinc chromate primer, coating: 2 coats red enamel paint, requirement: as per fire authorities, application: above ground pipes |  | 1800 | Mtr
B. ¦ PA SYSTEM | Main IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | ip based networkable touch screen paging station |  | feature: selection of zones, feature: supervision of system status, feature: scheduled broadcasts, feature: central exchange with stand by cpu, feature: built-in monitoring loudspeaker, feature: goose-neck microphone, feature: lcd touchscreen display, feature: audio input |  | 2 | Nos
B. ¦ PA SYSTEM | High Efficiency SIREN with weather protection IP 21C (Weatherproof Type, Suitable for Outdoor Area), 3km range. | siren | range: 3km | efficiency: high, weather protection: IP 21C (weatherproof type), application: suitable for outdoor area |  | 2 | Nos
B. ¦ PA SYSTEM | Supply, erection, testing & commissioning of 3 tone controller for high frequency siren. | 3 tone controller |  | application: for high frequency siren |  | 1 | Nos
B. ¦ PA SYSTEM | Rack Mounted 125 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | power amplifier | power: 125 watt | mounting: rack mounted, feature: battery back up, feature: wattage as per requirement |  | 1 | Nos
B. ¦ PA SYSTEM | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | xlpe cu cable | core: 2C, area: 1.5 mm2 | type: multi stranded, type: shielded, type: armoured, application: for power & signal |  | 2 | Mtr
B. ¦ PA SYSTEM | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | dvd player |  | feature: hook up to amplifiers of pa system, application: music in the common areas |  | 2 | Nos
B. ¦ PA SYSTEM | Paging Loudspeaker | paging loudspeaker |  |  |  | 2 | Nos
B. ¦ PA SYSTEM | Optical Fibre Cable (Armoured) with all accessories. | optical fibre cable |  | type: armoured, accessories: with all accessories |  | 1700 | Nos