## Sheet1
section_context_for_this_product_block | full_product_description | core_product_name | size | feature_or_specifications | acronymed_core_product_name | quantity | unit
S ¦ FINISH GODOWN 1 > S1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 100 mm NB | ms black steel pipe | size: 100 mm NB | material: ms(mild steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, scope: all related civil work, supports etc of vendor's scope |  | 120.0 | Mtr
S ¦ FINISH GODOWN 1 > S1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 80 mm NB | ms black steel pipe | size: 80 mm NB | material: ms(mild steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, scope: all related civil work, supports etc of vendor's scope |  | 30.0 | Mtr
S ¦ FINISH GODOWN 1 > S1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. 25 mm NB | ms black steel pipe | size: 25 mm NB | material: ms(mild steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, scope: all related civil work, supports etc of vendor's scope |  | 12.0 | Mtr
S ¦ FINISH GODOWN 1 > S1 ¦ HYDRANT SYSTEM | Supply & installation of SS oblique type single headed Landing valve with 80 mm inlet and 63 mm outlet SS instantaneous male coupling with rubber cap and chain conforming to IS : 5290 including matching flanges, gasket, nuts and bolts complete. | landing valve | inlet: 80 mm, outlet: 63 mm | material: ss(stainless steel), type: oblique, head: single headed, coupling: ss(stainless steel) instantaneous male, accessory: rubber cap and chain, standard: indian standard 5290, accessories: matching flanges, gasket, nuts and bolts |  | 6.0 | Nos
S ¦ FINISH GODOWN 1 > S1 ¦ HYDRANT SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. Size 80 mm NB | butterfly valve | size: 80 mm NB | standard: british standard 5155, type: wafer, accessories: matching flanges, nuts & bolts, fittings: necessary fittings by erection vendor |  | 6.0 | Nos
S ¦ FINISH GODOWN 1 > S1 ¦ HYDRANT SYSTEM | Supply & installation of SS branch pipe with 20 mm nozzle conforming to IS : 903 complete | branch pipe | nozzle: 20 mm | material: ss(stainless steel), standard: indian standard 903 |  | 6.0 | Nos
S ¦ FINISH GODOWN 1 > S1 ¦ HYDRANT SYSTEM | Supply & installation of 63 mm dia rubberized reinforced rubber line hose pipe in 15 m length conforming to IS : 636 Type II ISI marked with gunmetal male and female instantaneous coupling conforming to IS 903 wounded with 18 SWG copper wire complete | hose pipe | diameter: 63 mm, length: 15 m | material: rubberized reinforced rubber, standard: indian standard 636 type II, certification: ISI, coupling: gunmetal male and female instantaneous, coupling standard: indian standard 903, wire: 18 SWG copper |  | 12.0 | Nos
S ¦ FINISH GODOWN 1 > S1 ¦ HYDRANT SYSTEM | Supply & installation of MS Hose Box of fabricated from 16 SWG CRCA sheet double door with lockable arrangements to accommodate 2 RRL hose of 15 m length and one branch pipe painted white inside and red outside with one key. (750X600X250 mm) | hose box | dimensions: 750X600X250 mm | material: ms(mild steel), fabrication: 16 SWG CRCA sheet, door: double door with lockable arrangements, capacity: accommodates 2 RRL hose of 15 m length and one branch pipe, paint: white inside and red outside, accessory: one key |  | 6.0 | Nos
S ¦ FINISH GODOWN 1 > S1 ¦ HYDRANT SYSTEM | Supply & installation of swinging type hose reel drum fabricated from 14 SWG CRCA sheets painted with red colour stove paint 2 coats over 1 coat of primer with 30 m long 20 mm dia rubber hose pipe with with SS self closing shut – off nozzle of 5 mm outlet fixed on wall. | hose reel drum | hose length: 30 m, hose diameter: 20 mm, nozzle outlet: 5 mm | type: swinging, fabrication: 14 SWG CRCA sheets, paint: red colour stove paint 2 coats over 1 coat of primer, hose material: rubber, nozzle: ss(stainless steel) self closing shut-off, installation: fixed on wall |  | 6.0 | Nos
S ¦ FINISH GODOWN 1 > S1 ¦ HYDRANT SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends Size 25NB | globe valve | size: 25NB | material: bronze, standard: indian standard 778, ends: screwed |  | 6.0 | Nos
S ¦ FINISH GODOWN 1 > S2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Manual Call point | manual call point |  | type: analogue addressable |  | 8.0 | Nos
S ¦ FINISH GODOWN 1 > S2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of Hooter cum strobe | hooter cum strobe |  |  |  | 8.0 | Nos
S ¦ FINISH GODOWN 1 > S2 ¦ FDA SYSTEM | Supply, erction, testing & commissioning of analogue addressable Control Module | control module |  | type: analogue addressable |  | 3.0 | Nos
S ¦ FINISH GODOWN 1 > S2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Isolator Module | isolator module |  | type: analogue addressable |  | 3.0 | Nos
S ¦ FINISH GODOWN 1 > S2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Monitor module | monitor module |  | type: analogue addressable |  | 2.0 | Nos
S ¦ FINISH GODOWN 1 > S2 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. a ¦ 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cabling | cable size: 2C x 1.5 mm2 | feature: complete with lugs, laying and termination of both ends, cable type: loop cable |  | 330.0 | Mtr
S ¦ FINISH GODOWN 1 > S2 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. a ¦ 2C x 1.5 mm2 Armoured ( Power cable) | armoured cabling | cable size: 2C x 1.5 mm2 | feature: complete with lugs, laying and termination of both ends, cable type: power cable |  | 354.0 | Mtr
S ¦ FINISH GODOWN 1 > S2 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of 6 Watt Ceiling mounted Speakers | ceiling mounted speakers | power: 6 Watt |  |  | 77.0 | Nos
S ¦ FINISH GODOWN 1 > S2 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. a ¦ 2C x 1.5 mm2 Armoured ( Speaker cable) | armoured cabling | cable size: 2C x 1.5 mm2 | feature: complete with lugs, laying and termination of both ends, cable type: speaker cable |  | 640.0 | Mtr
S ¦ FINISH GODOWN 1 > S2 ¦ FDA SYSTEM | Supply, installation, testing and commissioning of aspiration detector with CMOS imager combined with multiple photodiode for reliable very early warning in a wide range of environments with minimal nuisance alarms. The detector should have 4 pipe inlet and min 100m pipelength support per inlet.The detector should have Smart on-board filter retains dust count and remaining filter life for predictable maintenance& coverage area of min 5000 Sq. | aspiration detector | pipe inlet: 4, pipelength support per inlet: min 100m, coverage area: min 5000 Sq. | imager: CMOS(complementary metal–oxide–semiconductor), feature: combined with multiple photodiode, feature: very early warning, feature: minimal nuisance alarms, feature: smart on-board filter retains dust count and remaining filter life for predictable maintenance |  | 4.0 | Nos
S ¦ FINISH GODOWN 1 > S2 ¦ FDA SYSTEM | Supply,Installation,Testing & Commissioning of UL/VDS listed CPVC Pipe 25 mm Dia & Pipe Accessories for the Aspiration detection. | cpvc pipe | diameter: 25 mm | certification: UL(underwriters laboratories), certification: VDS, feature: for the aspiration detection |  | 840.0 | Mtr
S ¦ FINISH GODOWN 1 > S2 ¦ FDA SYSTEM | Providing & fixing 600Watt Amplifier with necessary accessories. | amplifier | power: 600Watt | feature: with necessary accessories |  | 1.0 | Nos
S ¦ FINISH GODOWN 1 > S2 ¦ FDA SYSTEM | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable trays |  | feature: for laying all type of cables, feature: including all necessary structural supports |  | 640.0 | Mtr
S ¦ FINISH GODOWN 1 > S3 ¦ WATER CURTAIN | Supply, erection , testing & commissioning of Deluge valve with wet pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 2 way Solenoid Valve, air filter regulator etc. & manual release unit. a ¦ Size 150 NB | deluge valve | size: 150 NB | trim assembly: wet pilot, fitted with: strainer, drain valve, pressure gauge, pressure switch, solenoid valve: flame proof 2 way, air filter regulator: included, manual release unit: included |  | 1.0 | Nos
S ¦ FINISH GODOWN 1 > S3 ¦ WATER CURTAIN | Providing & fixing Cast Iron Y Strainer. a ¦ Size 150 NB | y strainer | size: 150 NB | material: cast iron |  | 1.0 | Nos
S ¦ FINISH GODOWN 1 > S3 ¦ WATER CURTAIN | Supply & fixing of SS Water Curtain Nozzle (K>=71)UL/FM Approved. | water curtain nozzle |  | material: ss(stainless steel), k-factor: >=71, certification: UL(underwriters laboratories), certification: FM(factory mutual) |  | 125.0 | Nos
S ¦ FINISH GODOWN 1 > S3 ¦ WATER CURTAIN | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. a ¦ Size 150 NB | gate valve | size: 150 NB | material: cs(carbon steel), standard: API 600, class: 150, flanges: matching, complete with: nuts & bolts |  | 3.0 | Nos
S ¦ FINISH GODOWN 1 > S4 ¦ PA SYSTEM | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | paging station |  | type: IP based networkable, feature: touch screen, feature: selection of zones, feature: supervision of system status, feature: scheduled broadcasts, central exchange: with stand by CPU, built-in: monitoring loudspeaker, microphone: goose-neck, display: LCD touchscreen, audio input: included |  | 1.0 | Nos
S ¦ FINISH GODOWN 1 > S4 ¦ PA SYSTEM | 30 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | horn type speaker | power: 30 W | efficiency: high, weather protection: IP 65, type: weatherproof, suitable for: outdoor area |  | 6.0 | Nos
S ¦ FINISH GODOWN 1 > S4 ¦ PA SYSTEM | Rack Mounted 200 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | power amplifier | power: 200 watt | mounting: rack mounted, battery back up: included, wattage: as per requirement |  | 1.0 | Nos
S ¦ FINISH GODOWN 1 > S4 ¦ PA SYSTEM | 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | xlpe cu cable | core: 2C, cross section: 1.5 mm2 | type: multi stranded, shielding: shielded, armouring: armoured, material: XLPE, material: Cu(copper), application: power & signal |  | 260.0 | Mtr
S ¦ FINISH GODOWN 1 > S4 ¦ PA SYSTEM | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | dvd player |  | feature: hook up to amplifiers of PA system, application: music in common areas |  | 1.0 | Nos
S ¦ FINISH GODOWN 1 > S4 ¦ PA SYSTEM | Paging Loudspeaker | paging loudspeaker |  |  |  | 1.0 | Nos