## Sheet1
section_context_for_this_product_block | full_product_description | core_product_name | size | feature_or_specifications | acronymed_core_product_name | quantity | unit
| Without box - 1 set of 1 X 6/16 A Socket Controlled by 1 x16 A switch | socket | socket: 1 x 6/16 A, switch: 1 x 16 A | set: 1 set, control: controlled by 1 x 16 A switch |  | 122.0 | Set
| Without box - 2 X 6/16A Socket Controlled by 1 x16 A switch | socket | socket: 2 x 6/16 A, switch: 1 x 16 A | control: controlled by 1 x 16 A switch |  | 1166.0 | Set
| Without box - 3 X 6/16A Socket Controlled by 1 x16 A switch | socket | socket: 3 x 6/16 A, switch: 1 x 16 A | control: controlled by 1 x 16 A switch |  | 120.0 | Set
| Without box - 1 set of 1 X 6A Socket Controlled by 6 A switch | socket | socket: 1 x 6 A, switch: 1 x 6 A | set: 1 set, control: controlled by 6 A switch |  | 231.0 | Set
| Metal back box - 3 Model | metal back box | model: 3 |  |  | 320.0 | no.
| Metal back box - 6 Model | metal back box | model: 6 |  |  | 130.0 | no.
| Metal back box - 8 Model | metal back box | model: 8 |  |  | 20.0 | no.
| PVC BACK BOX FOR IT- PROVISION - 2 M PVC box | pvc back box | model: 2 M |  |  | 320.0 | no.
| POWER CIRCUIT - 3 Core - 2.5 sq.mm flexible FRSL copper cables for WORKSTATION UPS Power | copper cable | core: 3, area: 2.5 sq.mm | type: flexible, type: FRSL, application: workstation UPS power, material: copper |  | 16000.0 | m
| POWER CIRCUIT - 3 Core - 4 sq.mm flexible FRLS copper cables for PANTRY SOCKETS | copper cable | core: 3, area: 4 sq.mm | type: flexible, type: FRLS, application: pantry sockets, material: copper |  | 300.0 | m
| POWER CIRCUIT - 3 Core - 6 sq.mm flexible FRSL copper cables for HUB ROOM | copper cable | core: 3, area: 6 sq.mm | type: flexible, type: FRSL, application: hub room, material: copper |  | 200.0 | m
| POWER CIRCUIT - 3 Core - 2.5 sq.mm flexible FRSL copper cables for 25mm MS conduit. _RAW POWER & UTLITY & HVAC | copper cable | core: 3, area: 2.5 sq.mm, conduit: 25 mm | type: flexible, type: FRSL, application: raw power & utility & HVAC, material: copper, conduit material: ms(mild steel) |  | 7000.0 | m
| LIGHTING CIRCUIT - 3 Core - 2.5 sq.mm flexible FRSL copper cables for 25mm MS conduit. _LIGHTING | copper cable | core: 3, area: 2.5 sq.mm, conduit: 25 mm | type: flexible, type: FRSL, application: lighting, material: copper, conduit material: ms(mild steel) |  | 4000.0 | m
| LIGHTING CIRCUIT - 3 Core -1.5 sq.mm flexible FRSL copper cables for 25mm MS conduit. (For single Emergency lighting circuits) | copper cable | core: 3, area: 1.5 sq.mm, conduit: 25 mm | type: flexible, type: FRSL, application: single emergency lighting circuits, material: copper, conduit material: ms(mild steel) |  | 3000.0 | m
| LIGHTING CIRCUIT - 2 Core - 1.5 sq.mm flexible FRSL copper cables for 25mm MS conduit.1 MS conduit. | copper cable | core: 2, area: 1.5 sq.mm, conduit: 25 mm, conduit: 1 ms(mild steel) | type: flexible, type: FRSL, application: lighting, material: copper, conduit material: ms(mild steel) |  | 7000.0 | m
| 4C x 35Sqmm XLPE Al. Cable | aluminium cable | core: 4, area: 35 sq.mm | insulation: XLPE, material: aluminium |  | 20.0 | m
| 4C x 25Sqmm XLPE Al. Cable | aluminium cable | core: 4, area: 25 sq.mm | insulation: XLPE, material: aluminium |  | 0.0 | m
| 4C x 16Sqmm XLPE Al. Cable | aluminium cable | core: 4, area: 16 sq.mm | insulation: XLPE, material: aluminium |  | 2106.0 | m
| 4C X 10 sq mm XLPE Al. Cable | aluminium cable | core: 4, area: 10 sq.mm | insulation: XLPE, material: aluminium |  | 480.0 | m
| 4C X 4 sq mm XLPE Al. Cable | aluminium cable | core: 4, area: 4 sq.mm | insulation: XLPE, material: aluminium |  | 0.0 | m
| 4C X 6 sq mm XLPE Al. Cable | aluminium cable | core: 4, area: 6 sq.mm | insulation: XLPE, material: aluminium |  | 120.0 | m
Copper conductor cables-YFY | 4C X 16 sq mm Cu Armoured Cable | copper armoured cable | core: 4, area: 16 sq.mm | material: copper, type: armoured |  | 530.0 | m
Copper conductor cables-YFY | 4C X 10 sq mm Cu Armoured Cable | copper armoured cable | core: 4, area: 10 sq.mm | material: copper, type: armoured |  | 0.0 | m
Copper conductor cables-YFY | 4C X 6 sq mm Cu Armoured Cable | copper armoured cable | core: 4, area: 6 sq.mm | material: copper, type: armoured |  | 15.0 | m
Copper conductor cables-YFY | 4C X 4 sq mm Cu Armoured Cable | copper armoured cable | core: 4, area: 4 sq.mm | material: copper, type: armoured |  | 0.0 | m
Copper conductor cables-YFY | 4C X 2.5 sq mm Cu Armoured Cable | copper armoured cable | core: 4, area: 2.5 sq.mm | material: copper, type: armoured |  | 0.0 | m
Copper conductor cables-YFY | 3C X 16 sq mm Cu Armoured Cable | copper armoured cable | core: 3, area: 16 sq.mm | material: copper, type: armoured |  | 0.0 | m
Copper conductor cables-YFY | 3C X 10 sq mm Cu Armoured Cable | copper armoured cable | core: 3, area: 10 sq.mm | material: copper, type: armoured |  | 60.0 | m
Copper conductor cables-YFY | 3C X 6 sq mm Cu Armoured Cable | copper armoured cable | core: 3, area: 6 sq.mm | material: copper, type: armoured |  | 0.0 | m
Copper conductor cables-YFY | 3C X 4 sq mm Cu Armoured Cable | copper armoured cable | core: 3, area: 4 sq.mm | material: copper, type: armoured |  | 600.0 | m
Copper conductor cables-YFY | 3C X 2.5 sq mm Cu Armoured Cable | copper armoured cable | core: 3, area: 2.5 sq.mm | material: copper, type: armoured |  | 0.0 | m
Copper conductor cables-YFY | 3C X 2.5 sq mm Cu Armoured Cable | copper armoured cable | core: 3, area: 2.5 sq.mm | material: copper, type: armoured |  | 0.0 | m
Copper conductor cables-YFY | 2C X16 sq mm Cu Armoured Cable | copper armoured cable | core: 2, area: 16 sq.mm | material: copper, type: armoured |  | 0.0 | m
Copper conductor cables-YFY | 1C X10 sq mm Cu Armoured Cable | copper armoured cable | core: 1, area: 10 sq.mm | material: copper, type: armoured |  | 0.0 | m
Copper conductor cables-YFY | 1C X16 sq mm Cu Armoured Cable | copper armoured cable | core: 1, area: 16 sq.mm | material: copper, type: armoured |  | 0.0 | m
Copper conductor cables-YY | 1C X 25 sq mm Cu unarmoured Cable | copper unarmoured cable | core: 1, area: 25 sq.mm | material: copper, type: unarmoured |  | 0.0 | m
Copper conductor cables-YY | 1C X 6 sq mm Cu unarmoured Cable | copper unarmoured cable | core: 1, area: 6 sq.mm | material: copper, type: unarmoured |  | 100.0 | m
Aluminium conductor cables | 4C x 95Sqmm XLPE Al. Cable | aluminium cable | core: 4, area: 95 sq.mm | insulation: XLPE, material: aluminium |  |  | no.
Aluminium conductor cables | 4C x 120Sqmm XLPE Al. Cable | aluminium cable | core: 4, area: 120 sq.mm | insulation: XLPE, material: aluminium |  |  | no.
Aluminium conductor cables | 4C x 70Sqmm XLPE Al. Cable | aluminium cable | core: 4, area: 70 sq.mm | insulation: XLPE, material: aluminium |  | 4.0 | no.
Aluminium conductor cables | 4C x 50 Sqmm XLPE Al. Cable | aluminium cable | core: 4, area: 50 sq.mm | insulation: XLPE, material: aluminium |  | 0.0 | no.
Aluminium conductor cables | 4C x 35Sqmm XLPE Al. Cable | aluminium cable | core: 4, area: 35 sq.mm | insulation: XLPE, material: aluminium |  |  | no.
Aluminium conductor cables | 4C x 25Sqmm XLPE Al. Cable | aluminium cable | core: 4, area: 25 sq.mm | insulation: XLPE, material: aluminium |  |  | no.
Aluminium conductor cables | 4C x 16Sqmm XLPE Al. Cable | aluminium cable | core: 4, area: 16 sq.mm | insulation: XLPE, material: aluminium |  | 76.0 | no.
Aluminium conductor cables | 4C X 10 sq mm XLPE Al. Cable | aluminium cable | core: 4, area: 10 sq.mm | insulation: XLPE, material: aluminium |  | 4.0 | no.
Copper conductor cables-YFY | 4C X 16 sq mm Cu Armoured Cable | copper armoured cable | core: 4, area: 16 sq.mm | material: copper, type: armoured |  | 16.0 | no.
Copper conductor cables-YFY | 4C X 10 sq mm Cu Armoured Cable | copper armoured cable | core: 4, area: 10 sq.mm | material: copper, type: armoured |  | 0.0 | no.
Copper conductor cables-YFY | 4C X 6 sq mm Cu Armoured Cable | copper armoured cable | core: 4, area: 6 sq.mm | material: copper, type: armoured |  | 0.0 | no.
Copper conductor cables-YFY | 4C X 4 sq mm Cu Armoured Cable | copper armoured cable | core: 4, area: 4 sq.mm | material: copper, type: armoured |  | 0.0 | no.
Copper conductor cables-YFY | 4C X 2.5 sq mm Cu Armoured Cable | copper armoured cable | core: 4, area: 2.5 sq.mm | material: copper, type: armoured |  | 0.0 | no.
Copper conductor cables-YFY | 3C X 16 sq mm Cu Armoured Cable | copper armoured cable | core: 3, area: 16 sq.mm | material: copper, type: armoured |  | 0.0 | no.
Copper conductor cables-YFY | 3C X 10 sq mm Cu Armoured Cable | copper armoured cable | core: 3, area: 10 sq.mm | material: copper, type: armoured |  | 0.0 | no.
Copper conductor cables-YFY | 3C X 6 sq mm Cu Armoured Cable | copper armoured cable | core: 3, area: 6 sq.mm | material: copper, type: armoured |  | 0.0 | no.
Copper conductor cables-YFY | 3C X 4 sq mm Cu Armoured Cable | copper armoured cable | core: 3, area: 4 sq.mm | material: copper, type: armoured |  | 16.0 | no.
Copper conductor cables-YFY | 3C X 2.5 sq mm Cu Armoured Cable | copper armoured cable | core: 3, area: 2.5 sq.mm | material: copper, type: armoured |  | 0.0 | no.
Copper conductor cables-YFY | 2C X16 sq mm Cu Armoured Cable | copper armoured cable | core: 2, area: 16 sq.mm | material: copper, type: armoured |  | 0.0 | no.
Copper conductor cables-YFY | 1C X10sq mm Cu Armoured Cable | copper armoured cable | core: 1, area: 10 sq.mm | material: copper, type: armoured |  | 0.0 | no.
Copper conductor cables-YFY | 1C X16 sq mm Cu Armoured Cable | copper armoured cable | core: 1, area: 16 sq.mm | material: copper, type: armoured |  | 0.0 | no.
Copper conductor cables-YY | 1C X 25 sq mm Cu unarmoured Cable | copper unarmoured cable | core: 1, area: 25 sq.mm | material: copper, type: unarmoured |  | 0.0 | no.
Copper conductor cables-YY | 1C X 6 sq mm Cu unarmoured Cable | copper unarmoured cable | core: 1, area: 6 sq.mm | material: copper, type: unarmoured |  | 12.0 | no.
Copper conductor cables-YY | ( DB Control lightting circuit to be measure separte from DB to First Light) |  |  |  |  | 0.0
Copper conductor cables-YY | Primary light point with 6A switch | primary light point |  | switch: 6A |  | 212.0 | no.
Copper conductor cables-YY | Primary light point directly controlled from the DB without switch | primary light point |  | control: directly from DB, switch: without switch |  | 159.0 | no.
Copper conductor cables-YY | Emergency light point directly controlled from the DB without switch | emergency light point |  | control: directly from DB, switch: without switch |  | 66.0 | no.
Copper conductor cables-YY | Secondary looping light point for normal circuits with 3cx1.5 sq.mm PVC insulated FRLS copper cable | secondary looping light point | cable size: 3cx1.5 sq.mm | cable insulation: PVC, cable type: FRLS(fire retardant low smoke), conductor material: copper, circuit type: normal |  | 1134.0 | no.
Copper conductor cables-YY | Secondary looping light point for emg With 3cx1.5 sq.mm PVC insulated FRLS copper cable | secondary looping light point | cable size: 3cx1.5 sq.mm | cable insulation: PVC, cable type: FRLS(fire retardant low smoke), conductor material: copper, circuit type: emg |  | 240.0 | no.
EARTHING | With 100mm dia 3M long CI Pipe electrode | ci pipe electrode | diameter: 100mm, length: 3M |  |  | 0.0 | no
EARTHING | Providing and fixing of earth electrode earth station complete with brick masonary chamber, GI cover, GI frame, GI watering funnel etc. The GI frame / chamber shall be of 300 x 300 mm. The rate shall also include necessary back filling componds for each earth pit as per manufacturer's guidelines. The unit shall be similar to T39 of Ashlok earthpit of height 3000mm and outer dia of 80mm . | earth electrode earth station | frame/chamber size: 300 x 300 mm, height: 3000mm, outer diameter: 80mm | chamber material: brick masonary, cover material: gi(galvanized iron), frame material: gi(galvanized iron), watering funnel: gi(galvanized iron), feature: back filling compounds as per manufacturer's guidelines, reference: similar to T39 of Ashlok earthpit |  | 0.0 | no
Earthing Conductors | Lead connection means to do proper bracing between joints wherever applicable. No joints to be connected with nut & bolt | lead connection |  | feature: proper bracing between joints, feature: no joints to be connected with nut & bolt |  | 0.0
Earthing Conductors | All GI & CU strips to be mounted on insulator at a regular distance & inside MS powder coated box. | gi and cu strips |  | mounting: on insulator at regular distance, enclosure: ms(mild steel) powder coated box |  | 0.0
Earthing Conductors | PVC sleeves needs to provided for all Cu strips. | cu strips |  | sleeves: pvc(polyvinyl chloride) |  | 0.0
Earthing Conductors | Vendor to provide bimetallic strip for required size wherever required | bimetallic strip |  |  |  | 0.0
GI conductors | 50 x 10 mm GI earth strip. | gi earth strip | size: 50 x 10 mm | material: gi(galvanized iron) |  | 0.0 | m
GI conductors | 50 x 6 mm GI earth strip. | gi earth strip | size: 50 x 6 mm | material: gi(galvanized iron) |  | 120.0 | m
GI conductors | 25 x 3 mm GI earth strip. | gi earth strip | size: 25 x 3 mm | material: gi(galvanized iron) |  | 630.0 | m
GI conductors | 8 SWG GI WIRE | gi wire | size: 8 SWG(standard wire gauge) | material: gi(galvanized iron) |  | 1000.0 | m
GI conductors | 8 SWG CU WIRE | cu wire | size: 8 SWG(standard wire gauge) | material: cu(copper) |  | 0.0 | m
CU conductors | 25 x 3 mm Cu earth strip with PVC sleeves. | cu earth strip | size: 25 x 3 mm | material: cu(copper), sleeves: pvc(polyvinyl chloride) |  | 0.0 | m
CU conductors | 1C x 6sqmm for rack body, third pin earthing, MCB DB body earthing and Other equipements | cu conductor | size: 1C x 6sqmm | application: rack body, third pin earthing, MCB DB body earthing and other equipments |  | 0.0 | m
CU conductors | 1C x 16sqmm for rack body body earthing | cu conductor | size: 1C x 16sqmm | application: rack body body earthing |  | 0.0 | m
CU conductors | 300mm long, 50 x 3 GI Earth bus suitable for terminating 8 SWG copper wire with holes at regular intervals connected to main bus. The same need to be mounted in MS powder coated box with transperent cover. | gi earth bus | length: 300mm, size: 50 x 3 | material: gi(galvanized iron), suitable for: terminating 8 SWG copper wire, feature: holes at regular intervals, connection: connected to main bus, mounting: ms(mild steel) powder coated box with transparent cover |  | 4.0 | no.
CU conductors | 300mm long, 25 x 3 Copper Earth bus suitable for terminating 6sqmm copper wire with holes at regular intervals connected to main bus. The same need to be mounted in MS powder coated box with transperent cover. | copper earth bus | length: 300mm, size: 25 x 3 | material: copper, suitable for: terminating 6sqmm copper wire, feature: holes at regular intervals, connection: connected to main bus, mounting: ms(mild steel) powder coated box with transparent cover |  | 8.0 | no.
FLOOR/ CEILING RACEWAYS | Supply, installation of raceways of following sizes made out of 1.6 mm thick Pregalvanised sheet complete with Push type for ceiling & screwed type cover for floor & wall drops of below specified thickness with counter sunk type screws. | raceways | sheet thickness: 1.6 mm | material: pregalvanised sheet, cover type: push type for ceiling, cover type: screwed type for floor & wall drops, screws: counter sunk type |  | 0.0
FLOOR/ CEILING RACEWAYS | Note : The rate quoted shall include providing earthing for the Wireway trunking with support hardware. (Usage of jumper wire at joining is acceptable) | wireway trunking |  | feature: earthing included, support hardware included, usage of jumper wire at joining is acceptable |  | 0.0
FLOOR/ CEILING RACEWAYS | Suitable size of Threaded rod to be used for respective raceways at distance of 1500mm each. | threaded rod | distance between rods: 1500mm | application: for respective raceways |  | 0.0
FLOOR/ CEILING RACEWAYS | 100 x 40mm raceway shall be with 6mm threaded rod. 150 x 40mm to 250 x 40mm raceway shall be with 8mm threaded rod. 300 x 40mm to 450 x 40mm raceway shall be with 12mm threaded rod. | raceway | size: 100 x 40mm, threaded rod: 6mm; size: 150 x 40mm to 250 x 40mm, threaded rod: 8mm; size: 300 x 40mm to 450 x 40mm, threaded rod: 12mm |  |  | 0.0
Ceiling raceway | 100mm x 50mm GI raceway with 1mm thick cover- | gi raceway | size: 100mm x 50mm, cover thickness: 1mm | material: gi(galvanized iron) |  | 350.0 | m
Ceiling raceway | 150mm x 50mm GI raceway with 1mm thick cover- | gi raceway | size: 150mm x 50mm, cover thickness: 1mm | material: gi(galvanized iron) |  | 0.0 | m
Ceiling raceway | 200mm x 50mm GI raceway with 1mm thick cover_ | gi raceway | size: 200mm x 50mm, cover thickness: 1mm | material: gi(galvanized iron) |  | 130.0 | m
Ceiling raceway | 250mm x 50mm GI raceway with 1 thick cover_ | gi raceway | size: 250mm x 50mm, cover thickness: 1 | material: gi(galvanized iron) |  |  | m
Ceiling raceway | 300mm x 50mm GI raceway with 1mm thick cover | gi raceway | size: 300mm x 50mm, cover thickness: 1mm | material: gi(galvanized iron) |  |  | m
Ceiling raceway | 450mm x 70mm GI raceway with 1mm thick cover | gi raceway | size: 450mm x 70mm, cover thickness: 1mm | material: gi(galvanized iron) |  |  | m
Ceiling raceway | 300 x 50 mm ladder type cable tray with 1 mm thick cover | ladder type cable tray | size: 300 x 50 mm, cover thickness: 1 mm |  |  | 0.0 | m
Ceiling raceway | 50mm x 40mm GI raceway with 1mm thick cover Black colour | gi raceway | size: 50mm x 40mm, cover thickness: 1mm | material: gi(galvanized iron), colour: black |  | 0.0 | m
Floor raceway | 100mm x 40mm Al raceway | al raceway | size: 100mm x 40mm | material: al(aluminium) |  | 3120.0 | m
Floor raceway | 100mm x 28mm AL. raceway | al raceway | size: 100mm x 28mm | material: al(aluminium) |  | 700.0 | m
Floor raceway | 25mm dia, MS Conduit | ms conduit | diameter: 25mm | material: ms(mild steel) |  | 600.0 | m
POWDER COATED TRUNKING FOR HUB ROOM/ SERVER ROOM | Providing and Fixing of 2mm thick steel sheet factory fabricated post galvanized raceways to be laid in ceiling/floor for Server room/HUB area with necessary knockouts & cutouts for installation of Industrial socket outlets. The rate to include 2 mm thick Powder coated cover with fixing accessories, Earthing with 6sqmm copper wire, complete with necessary supports, bends, access boxes and cross over junction boxes as per specification and site requirement. | raceways | sheet thickness: 2mm, cover thickness: 2 mm, earthing wire size: 6sqmm | material: steel, finish: post galvanized, finish: powder coated, feature: factory fabricated, feature: with necessary knockouts & cutouts for installation of industrial socket outlets, feature: with fixing accessories, feature: with earthing, feature: with supports, bends, access boxes and cross over junction boxes |  | 0.0
POWDER COATED TRUNKING FOR HUB ROOM/ SERVER ROOM | 1) Power raceways should have different colour for each source. i.e source-1 should have Blue colour & source-2 should have Red. 2) Date raceway should have seimens grey colour. | power raceways |  | colour: blue (source-1), colour: red (source-2), colour: seimens grey (data raceway) |  | 0.0
POWDER COATED TRUNKING FOR HUB ROOM/ SERVER ROOM | 100 mm Wide x 75 mm Deep Raceways with 2 mm thick cover-POWER RACEWAYS IN FLOOR | raceways | width: 100 mm, depth: 75 mm, cover thickness: 2 mm | feature: power raceways in floor |  | 60.0 | m
POWDER COATED TRUNKING FOR HUB ROOM/ SERVER ROOM | 450 mm Wide x 75 mm Deep Raceways with 2 mm thick cover-DATA RACEWAYS IN FLOOR. | raceways | width: 450 mm, depth: 75 mm, cover thickness: 2 mm | feature: data raceways in floor |  | 60.0 | m
POWDER COATED TRUNKING FOR HUB ROOM/ SERVER ROOM | 450 mm Wide x 40 mm Deep Raceways with 2 mm thick cover-DATA RACEWAYS IN CEILING. | raceways | width: 450 mm, depth: 40 mm, cover thickness: 2 mm | feature: data raceways in ceiling |  | 0.0 | m
POWDER COATED TRUNKING FOR HUB ROOM/ SERVER ROOM | 450 x 75 mm ladder type cable tray with 2 mm thick cover-FOR SERVER ROOM NETWORK CABLE DROP IN WALL. | ladder type cable tray | size: 450 x 75 mm, cover thickness: 2 mm | feature: for server room network cable drop in wall |  | 0.0 | m
JUNCTION BOXES | Electrogalvanised junction boxes with 2mm cover with counter sunk type screws for floor raceways of the following sizes.The dimension of the same shall be as follows. Open side of the juction box needs to be closed with GI cover | junction boxes | cover thickness: 2mm | material: electrogalvanised, screw type: counter sunk, application: for floor raceways, feature: open side to be closed with gi(galvanized iron) cover |  | 0.0
JUNCTION BOXES | 110 x 110 x 55mm GI floor junction box with 1.6 mm thick cover. | gi floor junction box | size: 110 x 110 x 55mm, cover thickness: 1.6 mm | material: gi(galvanized iron) |  | 0.0 | no.
JUNCTION BOXES | 160 x 160 x 55mm GI floor junction box with 1.6 mm thick cover. | gi floor junction box | size: 160 x 160 x 55mm, cover thickness: 1.6 mm | material: gi(galvanized iron) |  | 487.0 | no.
JUNCTION BOXES | 210 x 210 x 55mm GI floor junction box with 1.6 mm thick cover. | gi floor junction box | size: 210 x 210 x 55mm, cover thickness: 1.6 mm | material: gi(galvanized iron) |  | 0.0 | no.
JUNCTION BOXES | 260 x2600x 55mm GI floor junction box with 1.6 mm thick cover. | gi floor junction box | size: 260 x 2600 x 55mm, cover thickness: 1.6 mm | material: gi(galvanized iron) |  | 87.0 | no.
JUNCTION BOXES | 360 x 360 x 55mm GI floor junction box with 1.6 mm thick cover. | gi floor junction box | size: 360 x 360 x 55mm, cover thickness: 1.6 mm | material: gi(galvanized iron) |  | 15.0 | no.
JUNCTION BOXES | 460 x 460 x 55mm GI floor junction box with 1.6 mm thick cover. | gi floor junction box | size: 460 x 460 x 55mm, cover thickness: 1.6 mm | material: gi(galvanized iron) |  | 64.0 | no.
FLOOR/WALL CHIPPING FOR REACEWAYS/CONDUIT | 415V enameled type danger boards 150 x 150mm. Size | danger boards | size: 150 x 150mm | voltage: 415V, type: enameled |  | 3.0 | no.
FLOOR/WALL CHIPPING FOR REACEWAYS/CONDUIT | 10 mm thick ISI mark 1100V grade rubber mat of standard length of 2m x 1m | rubber mat | thickness: 10 mm, length: 2m, width: 1m | standard: ISI(indian standards), voltage: 1100V grade |  | 6.0 | no.
FLOOR/WALL CHIPPING FOR REACEWAYS/CONDUIT | Shock treatment chart duly framed and laminated | shock treatment chart |  | feature: duly framed and laminated |  | 3.0 | no.
EMPTY CONDUITS | Supply and installation of 2 mm thick conduits of following sizes for open / enclosed wiring complete with all necessary accessories | conduits | thickness: 2 mm | feature: for open or enclosed wiring, feature: complete with all necessary accessories |  | 0.0
EMPTY CONDUITS | Color coding for MS conduits shall be as below | ms conduit |  | feature: color coding as specified below |  | 0.0
EMPTY CONDUITS | Raw power and lighting- Black UPS power - Blue Data and voice- Grey | ms conduit |  | color coding: raw power and lighting - black, ups power - blue, data and voice - grey |  | 0.0
EMPTY CONDUITS | 19 mm dia, 2mm thick, MS conduit | ms conduit | diameter: 19 mm, thickness: 2mm | material: ms(mild steel) |  | 800.0 | m
EMPTY CONDUITS | 25 mm dia, 2mm thick, MS conduit | ms conduit | diameter: 25 mm, thickness: 2mm | material: ms(mild steel) |  | 0.0 | m
CABLE TRAYS | Supply and installing of following size of fabricated galvanised 2mm thick ladder type cable tray made of suitable type of angles / sheets, including horizontal and vertical bends, reducers, tees, cross members and other accessories as required and suspended from the ceiling. | ladder type cable tray | thickness: 2mm | material: fabricated galvanised, feature: made of suitable type of angles or sheets, feature: including horizontal and vertical bends, reducers, tees, cross members and other accessories, feature: suspended from the ceiling |  | 0.0
CABLE TRAYS | Note: The rate shall include all necessary supporting structure / supports as required. | ladder type cable tray |  | feature: rate includes all necessary supporting structure or supports |  | 0.0
CABLE TRAYS | 150 x 50mm cable tray shall be with 6mm threaded rod. 300 x 50mm cable tray shall be with 8 mm threaded rod. 300 x 70mm to 450 x 70mm cable tray shall be with 12mm threaded rod. 450 x 70mm to 750 x 70mm cable tray shall be with 75 x 75mm MS angle | cable tray |  | feature: 150 x 50mm cable tray with 6mm threaded rod, feature: 300 x 50mm cable tray with 8mm threaded rod, feature: 300 x 70mm to 450 x 70mm cable tray with 12mm threaded rod, feature: 450 x 70mm to 750 x 70mm cable tray with 75 x 75mm ms(mild steel) angle |  | 0.0
CABLE TRAYS > Perforated type cable tray | 150 x 50 mm wide cable tray | cable tray | width: 150 mm, height: 50 mm | type: perforated |  | 295.0 | m
CABLE TRAYS > Perforated type cable tray | 300 x 50 mm wide cable tray | cable tray | width: 300 mm, height: 50 mm | type: perforated |  | 305.0 | m
CABLE TRAYS > Perforated type cable tray | 450 x 70mm wide cable tray | cable tray | width: 450 mm, height: 70 mm | type: perforated |  | 40.0 | m
CABLE TRAYS > Perforated type cable tray | 600 x 70 mm wide cable tray | cable tray | width: 600 mm, height: 70 mm | type: perforated |  | 0.0 | m