## Sheet1
0 | 1 | 2 | 3
1 | Without box
| 1 set of 1 X 6/16 A Socket Controlled by 1 x16 A switch | Set | 122
| 2 X 6/16A Socket Controlled by 1 x16 A switch | Set | 1166
| 3 X 6/16A Socket Controlled by 1 x16 A switch | Set | 120
| 1 set of 1 X 6A Socket Controlled by 6 A switch | Set | 231
2 | Metal back box |  | 0
| 3 Model | no. | 320
| 6 Model | no. | 130
| 8 Model | no. | 20
3 | PVC BACK BOX FOR IT- PROVISION |  | 0
| 2 M PVC box | no. | 320
4 | POWER CIRCUIT |  | 0
| 3 Core - 2.5 sq.mm flexible FRSL copper cables for WORKSTATION UPS Power | m | 16000
| 3 Core - 4 sq.mm flexible FRLS copper cables for PANTRY SOCKETS | m | 300
| 3 Core - 6 sq.mm flexible FRSL copper cables for HUB ROOM | m | 200
| 3 Core - 2.5 sq.mm flexible FRSL copper cables for 25mm MS conduit. _RAW POWER & UTLITY & HVAC | m | 7000
5 | LIGHTING CIRCUIT |  | 0
| 3 Core - 2.5 sq.mm flexible FRSL copper cables for 25mm MS conduit. _LIGHTING | m | 4000
| 3 Core -1.5 sq.mm flexible FRSL copper cables for 25mm MS conduit. (For single Emergency lighting circuits) | m | 3000
| 2 Core - 1.5 sq.mm flexible FRSL copper cables for 25mm MS conduit.1 MS conduit. | m | 7000
6 | Aluminium conductor cables-A2XFY |  | 0
| 3.5C x 400Sqmm XLPE Al. Cable | m | 0
| 4C x 300Sqmm XLPE Al. Cable | m | 20
| 3.5C x 300Sqmm XLPE Al. Cable | m | 315
| 3.5C x 240Sqmm XLPE Al. Cable | m | 0
| 4Cx150 SQ. MM XLPE AL. CABLE | m | 20
| 4C x 95Sqmm XLPE Al. Cable | m | 20
| 4C x 120Sqmm XLPE Al. Cable | m
| 4C x 70Sqmm XLPE Al. Cable | m | 100
| 4C x 50 Sqmm XLPE Al. Cable | m | 0
| 4C x 35Sqmm XLPE Al. Cable | m | 20
| 4C x 25Sqmm XLPE Al. Cable | m | 0
| 4C x 16Sqmm XLPE Al. Cable | m | 2106
| 4C X 10 sq mm XLPE Al. Cable | m | 480
| 4C X 4 sq mm XLPE Al. Cable | m | 0
| 4C X 6 sq mm XLPE Al. Cable | m | 120
7 | Copper conductor cables-YFY
| 4C X 16 sq mm Cu Armoured Cable | m | 530
| 4C X 10 sq mm Cu Armoured Cable | m | 0
| 4C X 6 sq mm Cu Armoured Cable | m | 15
| 4C X 4 sq mm Cu Armoured Cable | m | 0
| 4C X 2.5 sq mm Cu Armoured Cable | m | 0
| 3C X 16 sq mm Cu Armoured Cable | m | 0
| 3C X 10 sq mm Cu Armoured Cable | M | 60
| 3C X 6 sq mm Cu Armoured Cable | M | 0
| 3C X 4 sq mm Cu Armoured Cable | m | 600
| 3C X 2.5 sq mm Cu Armoured Cable | m | 0
| 3C X 2.5 sq mm Cu Armoured Cable | m | 0
| 2C X16 sq mm Cu Armoured Cable | m | 0
| 1C X10 sq mm Cu Armoured Cable | m | 0
| 1C X16 sq mm Cu Armoured Cable | m | 0
8 | Copper conductor cables-YY
| 1C X 25 sq mm Cu unarmoured Cable | m | 0
| 1C X 6 sq mm Cu unarmoured Cable | m | 100
9 | Aluminium conductor cables
| 3.5C x 400Sqmm XLPE Al. Cable | no. | 0
| 4C x 300Sqmm XLPE Al. Cable | no.
| 3.5C x 300Sqmm XLPE Al. Cable | no. | 6
| 3.5C x 240Sqmm XLPE Al. Cable | no. | 0
| 4Cx150 SQ. MM XLPE AL. CABLE | no. | 0
| 4C x 95Sqmm XLPE Al. Cable | no.
| 4C x 120Sqmm XLPE Al. Cable | no.
| 4C x 70Sqmm XLPE Al. Cable | no. | 4
| 4C x 50 Sqmm XLPE Al. Cable | no. | 0
| 4C x 35Sqmm XLPE Al. Cable | no.
| 4C x 25Sqmm XLPE Al. Cable | no.
| 4C x 16Sqmm XLPE Al. Cable | no. | 76
| 4C X 10 sq mm XLPE Al. Cable | no. | 4
10 | Copper conductor cables-YFY
| 4C X 16 sq mm Cu Armoured Cable | no. | 16
| 4C X 10 sq mm Cu Armoured Cable | no. | 0
| 4C X 6 sq mm Cu Armoured Cable | no. | 0
| 4C X 4 sq mm Cu Armoured Cable | no. | 0
| 4C X 2.5 sq mm Cu Armoured Cable | no. | 0
| 3C X 16 sq mm Cu Armoured Cable | no. | 0
| 3C X 10 sq mm Cu Armoured Cable | no. | 0
| 3C X 6 sq mm Cu Armoured Cable | no. | 0
| 3C X 4 sq mm Cu Armoured Cable | no. | 16
| 3C X 2.5 sq mm Cu Armoured Cable | no. | 0
| 2C X16 sq mm Cu Armoured Cable | no. | 0
| 1C X10sq mm Cu Armoured Cable | no. | 0
| 1C X16 sq mm Cu Armoured Cable | no. | 0
11 | Copper conductor cables-YY
| 1C X 25 sq mm Cu unarmoured Cable | no. | 0
| 1C X 6 sq mm Cu unarmoured Cable | no. | 12
| ( DB Control lightting circuit to be measure separte from DB to First Light) |  | 0
| Primary light point with 6A switch | no. | 212
| Primary light point directly controlled from the DB without switch | no. | 159
| Emergency light point directly controlled from the DB without switch | no. | 66
| Secondary light point with 6A switch control | no. | 480
| Secondary looping light point for normal circuits with 3cx1.5 sq.mm PVC insulated FRLS copper cable | no. | 1134
| Secondary looping light point for emg With 3cx1.5 sq.mm PVC insulated FRLS copper cable | no. | 240
12 | EARTHING
| With 100mm dia 3M long CI Pipe electrode | no | 0
| Providing and fixing of earth electrode earth station complete with brick masonary chamber, GI cover, GI frame, GI watering funnel etc. The GI frame / chamber shall be of 300 x 300 mm. The rate shall also include necessary back filling componds for each earth pit as per manufacturer's guidelines. The unit shall be similar to T39 of Ashlok earthpit of height 3000mm and outer dia of 80mm . | no | 0
13 | Earthing Conductors |  | 0
| Lead connection means to do proper bracing between joints wherever applicable. No joints to be connected with nut & bolt |  | 0
| All GI & CU strips to be mounted on insulator at a regular distance & inside MS powder coated box. |  | 0
| PVC sleeves needs to provided for all Cu strips. |  | 0
| Vendor to provide bimetallic strip for required size wherever required |  | 0
14 | GI conductors |  | 0
| 50 x 10 mm GI earth strip. | m | 0
| 50 x 6 mm GI earth strip. | m | 120
| 25 x 3 mm GI earth strip. | m | 630
| 8 SWG GI WIRE | m | 1000
| 8 SWG CU WIRE | m | 0
15 | CU conductors |  | 0
| 25 x 3 mm Cu earth strip with PVC sleeves. | m | 0
| 1C x 6sqmm for rack body, third pin earthing, MCB DB body earthing and Other equipements | m | 0
| 1C x 16sqmm for rack body body earthing | m | 0
| 300mm long, 50 x 3 GI Earth bus suitable for terminating 8 SWG copper wire with holes at regular intervals connected to main bus. The same need to be mounted in MS powder coated box with transperent cover. | no. | 4
| 300mm long, 25 x 3 Copper Earth bus suitable for terminating 6sqmm copper wire with holes at regular intervals connected to main bus. The same need to be mounted in MS powder coated box with transperent cover. | no. | 8
16 | FLOOR/ CEILING RACEWAYS |  | 0
| Supply, installation of raceways of following sizes made out of 1.6 mm thick Pregalvanised sheet complete with Push type for ceiling & screwed type cover for floor & wall drops of below specified thickness with counter sunk type screws. |  | 0
| Note : The rate quoted shall include providing earthing for the Wireway trunking with support hardware. (Usage of jumper wire at joining is acceptable) |  | 0
| Suitable size of Threaded rod to be used for respective raceways at distance of 1500mm each. |  | 0
| 100 x 40mm raceway shall be with 6mm threaded rod. 150 x 40mm to 250 x 40mm raceway shall be with 8mm threaded rod. 300 x 40mm to 450 x 40mm raceway shall be with 12mm threaded rod. |  | 0
17 | Ceiling raceway |  | 0
| 100mm x 50mm GI raceway with 1mm thick cover- | m | 350
| 150mm x 50mm GI raceway with 1mm thick cover- | m | 0
| 200mm x 50mm GI raceway with 1mm thick cover_ | m | 130
| 250mm x 50mm GI raceway with 1 thick cover_ | m
| 300mm x 50mm GI raceway with 1mm thick cover | m
| 450mm x 70mm GI raceway with 1mm thick cover | m
| 300 x 50 mm ladder type cable tray with 1 mm thick cover | m | 0
| 50mm x 40mm GI raceway with 1mm thick cover Black colour | m | 0
18 | Floor raceway |  | 0
| 100mm x 40mm Al raceway | m | 3120
| 100mm x 28mm AL. raceway | m | 700
| 25mm dia, MS Conduit | m | 600
19 | POWDER COATED TRUNKING FOR HUB ROOM/ SERVER ROOM |  | 0
| Providing and Fixing of 2mm thick steel sheet factory fabricated post galvanized raceways to be laid in ceiling/floor for Server room/HUB area with necessary knockouts & cutouts for installation of Industrial socket outlets. The rate to include 2 mm thick Powder coated cover with fixing accessories, Earthing with 6sqmm copper wire, complete with necessary supports, bends, access boxes and cross over junction boxes as per specification and site requirement. |  | 0
| 1) Power raceways should have different colour for each source. i.e source-1 should have Blue colour & source-2 should have Red. 2) Date raceway should have seimens grey colour. |  | 0
| 100 mm Wide x 75 mm Deep Raceways with 2 mm thick cover-POWER RACEWAYS IN FLOOR | m | 60
| 450 mm Wide x 75 mm Deep Raceways with 2 mm thick cover-DATA RACEWAYS IN FLOOR. | m | 60
| 450 mm Wide x 40 mm Deep Raceways with 2 mm thick cover-DATA RACEWAYS IN CEILING. | m | 0
| 450 x 75 mm ladder type cable tray with 2 mm thick cover-FOR SERVER ROOM NETWORK CABLE DROP IN WALL. | m | 0
20 | JUNCTION BOXES |  | 0
| Electrogalvanised junction boxes with 2mm cover with counter sunk type screws for floor raceways of the following sizes.The dimension of the same shall be as follows. Open side of the juction box needs to be closed with GI cover |  | 0
| 110 x 110 x 55mm GI floor junction box with 1.6 mm thick cover. | no. | 0
| 160 x 160 x 55mm GI floor junction box with 1.6 mm thick cover. | no. | 487
| 210 x 210 x 55mm GI floor junction box with 1.6 mm thick cover. | no. | 0
| 260 x2600x 55mm GI floor junction box with 1.6 mm thick cover. | no. | 87
| 360 x 360 x 55mm GI floor junction box with 1.6 mm thick cover. | no. | 15
| 460 x 460 x 55mm GI floor junction box with 1.6 mm thick cover. | no. | 64
21 | FLOOR/WALL CHIPPING FOR REACEWAYS/CONDUIT |  | 0
| Cutting of floor screeding for accomadating the floor raceways / conduits for the below mentioned size of raceways / conduits. The rate shall include closing of extra gap with cement morter, cutting and dabries removing ( Final Finishing will be done by civil contractor ) |  | 0
| 100mm x 40mm /100mm x 25mm AL raceway | m | 3120
| 25mm dia, 2mm thick, FRLS type MS conduit | m | 650
22 | MISCELLANIOUS ITEMS |  | 0
| 415V enameled type danger boards 150 x 150mm. Size | no. | 3
| 10 mm thick ISI mark 1100V grade rubber mat of standard length of 2m x 1m | no. | 6
| Shock treatment chart duly framed and laminated | no. | 3
23 | EMPTY CONDUITS |  | 0
| Supply and installation of 2 mm thick conduits of following sizes for open / enclosed wiring complete with all necessary accessories |  | 0
| Color coding for MS conduits shall be as below |  | 0
| Raw power and lighting- Black UPS power - Blue Data and voice- Grey |  | 0
| 19 mm dia, 2mm thick, MS conduit | m | 800
| 25 mm dia, 2mm thick, MS conduit | m | 0
24 | CABLE TRAYS |  | 0
| Supply and installing of following size of fabricated galvanised 2mm thick ladder type cable tray made of suitable type of angles / sheets, including horizontal and vertical bends, reducers, tees, cross members and other accessories as required and suspended from the ceiling. |  | 0
| Note: The rate shall include all necessary supporting structure / supports as required. |  | 0
| 150 x 50mm cable tray shall be with 6mm threaded rod. 300 x 50mm cable tray shall be with 8 mm threaded rod. 300 x 70mm to 450 x 70mm cable tray shall be with 12mm threaded rod. 450 x 70mm to 750 x 70mm cable tray shall be with 75 x 75mm MS angle |  | 0
25 | Perforated type cable tray |  | 0
| 150 x 50 mm wide cable tray | m | 295
| 300 x 50 mm wide cable tray | m | 305
| 450 x 70mm wide cable tray | m | 40
| 600 x 70 mm wide cable tray | m | 0