## Sheet1
section_context_for_this_product_block | full_product_description | core_product_name | size | feature_or_specifications | acronymed_core_product_name | quantity | unit
G ¦ MONOMER COLD ROOM G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection , testing & commissioning of Deluge valve with wet pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 3/2 way Solenoid Valve, air filter regulator etc. & manual release unit. The valve shall be electro-pneumatic type. a ¦ 80 mm NB | deluge valve | size: 80 mm NB | trim assembly: wet pilot, fitted with: strainer, fitted with: drain valve, fitted with: pressure gauge, fitted with: pressure switch, fitted with: flame proof 3/2 way solenoid valve, fitted with: air filter regulator, fitted with: manual release unit, type: electro-pneumatic |  | 1.0 | Nos
G ¦ MONOMER COLD ROOM G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. a ¦ 80 mm NB | gate valve | size: 80 mm NB | material: cs(carbon steel), standard: API 600, class: 150, ends: matching flanges, complete with: nuts & bolts |  | 3.0 | Nos
G ¦ MONOMER COLD ROOM G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, installation, testing & commissioning of Y- Stainer a ¦ 80 mm NB | y strainer | size: 80 mm NB |  |  | 1.0 | Nos
G ¦ MONOMER COLD ROOM G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply,installation,testing and commissioning of HVWS NOZZLE with necessary threaded fittings as per drawing. a ¦ K26, SPRAY ANGLE=100° | hvws nozzle | model: K26, spray angle: 100° | fittings: necessary threaded fittings as per drawing |  | 12.0 | Nos
G ¦ MONOMER COLD ROOM G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply,installation and commissioning of UL/FM approved Quartzoid Bulb Detector for K factor-80. Temp rating 68 deg C | quartzoid bulb detector | k factor: 80, temp rating: 68 deg C | certification: UL(underwriters laboratories), certification: FM(factory mutual), feature: approved |  | 12.0 | Nos
G ¦ MONOMER COLD ROOM G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications a ¦ 80 NB | gi pipe | size: 80 NB | class: c class (heavy class), standard: IS 1239(indian standard 1239), fittings: threaded or grooved, fittings: elbow, fittings: tee, fittings: reducer, fittings: welding flanges, fixing: clamps to MS brackets/hangers, supports: steel, coating: zinc chromate primer, coating: 2 coats red enamel paint, requirement: fire authorities, application: above ground pipes |  | 9.0 | Mtr
G ¦ MONOMER COLD ROOM G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications b ¦ 65 NB | gi pipe | size: 65 NB | class: c class (heavy class), standard: IS 1239(indian standard 1239), fittings: threaded or grooved, fittings: elbow, fittings: tee, fittings: reducer, fittings: welding flanges, fixing: clamps to MS brackets/hangers, supports: steel, coating: zinc chromate primer, coating: 2 coats red enamel paint, requirement: fire authorities, application: above ground pipes |  | 6.0 | Mtr
G ¦ MONOMER COLD ROOM G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications c ¦ 50 NB | gi pipe | size: 50 NB | class: c class (heavy class), standard: IS 1239(indian standard 1239), fittings: threaded or grooved, fittings: elbow, fittings: tee, fittings: reducer, fittings: welding flanges, fixing: clamps to MS brackets/hangers, supports: steel, coating: zinc chromate primer, coating: 2 coats red enamel paint, requirement: fire authorities, application: above ground pipes |  | 6.0 | Mtr
G ¦ MONOMER COLD ROOM G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications d ¦ 40NB | gi pipe | size: 40 NB | class: c class (heavy class), standard: IS 1239(indian standard 1239), fittings: threaded or grooved, fittings: elbow, fittings: tee, fittings: reducer, fittings: welding flanges, fixing: clamps to MS brackets/hangers, supports: steel, coating: zinc chromate primer, coating: 2 coats red enamel paint, requirement: fire authorities, application: above ground pipes |  | 17.0 | Mtr
G ¦ MONOMER COLD ROOM G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications e ¦ 25NB | gi pipe | size: 25 NB | class: c class (heavy class), standard: IS 1239(indian standard 1239), fittings: threaded or grooved, fittings: elbow, fittings: tee, fittings: reducer, fittings: welding flanges, fixing: clamps to MS brackets/hangers, supports: steel, coating: zinc chromate primer, coating: 2 coats red enamel paint, requirement: fire authorities, application: above ground pipes |  | 56.0 | Mtr
G ¦ MONOMER COLD ROOM G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing & commissioning of analogue addressable ROR(Rate of Rise) type Heat Detector | analogue addressable rate of rise type heat detector |  | type: analogue addressable, type: rate of rise (ROR) | ror type heat detector | 4.0 | Nos
G ¦ MONOMER COLD ROOM G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing & commissioning of analogue addressable Manual Call point | analogue addressable manual call point |  | type: analogue addressable |  | 1.0 | Nos
G ¦ MONOMER COLD ROOM G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing & commissioning of Hooter cum strobe | hooter cum strobe |  |  |  | 1.0 | Nos
G ¦ MONOMER COLD ROOM G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erction, testing & commissioning of analogue addressable Control Module | analogue addressable control module |  | type: analogue addressable |  | 2.0 | Nos
G ¦ MONOMER COLD ROOM G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing & commissioning of analogue addressable Isolator Module | analogue addressable isolator module |  | type: analogue addressable |  | 1.0 | Nos
G ¦ MONOMER COLD ROOM G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing & commissioning of analogue addressable Monitor module | analogue addressable monitor module |  | type: analogue addressable |  | 1.0 | Nos
G ¦ MONOMER COLD ROOM G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. a ¦ 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cabling | configuration: 2C x 1.5 mm2 | feature: complete with lugs, laying and termination of both ends, type: armoured, type: loop cable |  | 32.0 | Mtr
G ¦ MONOMER COLD ROOM G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. a ¦ 2C x 1.5 mm2 Armoured ( Power cable) | armoured cabling | configuration: 2C x 1.5 mm2 | feature: complete with lugs, laying and termination of both ends, type: armoured, type: power cable |  | 12.0 | Mtr
G ¦ MONOMER COLD ROOM G1 ¦ HIGH VELOCITY WATER SPRAY SYSTEM | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable trays |  | feature: for laying all type of cables as indicated above, feature: including all necessary structural supports |  | 32.0 | Mtr
G ¦ MONOMER COLD ROOM G3 ¦ PA SYSTEM | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | ip based networkable touch screen paging station |  | feature: selection of zones, feature: supervision of system status, feature: setting of scheduled broadcasts, feature: central exchange with stand by CPU, feature: built-in monitoring loudspeaker, feature: goose-neck microphone, feature: LCD touchscreen display, feature: audio input |  | 1.0 | Nos
G ¦ MONOMER COLD ROOM G3 ¦ PA SYSTEM | 6 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | horn type speaker | power: 6 W | feature: high efficiency, protection: IP 65, feature: weatherproof type, feature: suitable for outdoor area |  | 2.0 | Nos
G ¦ MONOMER COLD ROOM G3 ¦ PA SYSTEM | Rack Mounted 125 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | rack mounted power amplifier | power: 125 watt | feature: battery back up, feature: wattage shall be as per requirement |  | 1.0 | Nos
G ¦ MONOMER COLD ROOM G3 ¦ PA SYSTEM | DVD player with features to hook up to amplifiers of PA system for music in the common areas. | dvd player |  | feature: features to hook up to amplifiers of pa system for music in the common areas |  | 1.0 | Nos
G ¦ MONOMER COLD ROOM G3 ¦ PA SYSTEM | Paging Loudspeaker | paging loudspeaker |  |  |  | 1.0 | Nos