## Sheet1
section_context_for_this_product_block | full_product_description | core_product_name | size | feature_or_specifications | acronymed_core_product_name | quantity | unit
I ¦ PAINTS CONTROL LAB I1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. a ¦ 100 mm NB | ms black steel pipe | size: 100 mm NB | material: ms(mild steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 Part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, scope: all related civil work, supports etc of vendor's scope |  | 36.0 | Mtr
I ¦ PAINTS CONTROL LAB I1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. b ¦ 80 mm NB | ms black steel pipe | size: 80 mm NB | material: ms(mild steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 Part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, scope: all related civil work, supports etc of vendor's scope |  | 36.0 | Mtr
I ¦ PAINTS CONTROL LAB I1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. c ¦ 25 mm NB | ms black steel pipe | size: 25 mm NB | material: ms(mild steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 Part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, scope: all related civil work, supports etc of vendor's scope |  | 18.0 | Mtr
I ¦ PAINTS CONTROL LAB I1 ¦ HYDRANT SYSTEM | Supply & installation of swinging type hose reel drum fabricated from 14 SWG CRCA sheets painted with red colour stove paint 2 coats over 1 coat of primer with 30 m long 20 mm dia rubber hose pipe with with SS self closing shut – off nozzle of 5 mm outlet fixed on wall. | hose reel drum | hose length: 30 m, hose diameter: 20 mm, nozzle outlet: 5 mm | type: swinging, fabrication: 14 SWG CRCA sheets, painting: red colour stove paint 2 coats over 1 coat of primer, hose material: rubber, nozzle: ss(stainless steel) self closing shut-off, mounting: fixed on wall |  | 3.0 | Nos
I ¦ PAINTS CONTROL LAB I1 ¦ HYDRANT SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends a ¦ Size 25NB | globe valve | size: 25NB | material: bronze, standard: indian standard 778, end connection: screwed |  | 3.0 | Nos
I ¦ PAINTS CONTROL LAB I1 ¦ HYDRANT SYSTEM | Supply & installation of SS oblique type single headed Landing valve with 80 mm inlet and 63 mm outlet SS instantaneous male coupling with rubber cap and chain conforming to IS : 5290 including matching flanges, gasket, nuts and bolts complete. | landing valve | inlet: 80 mm, outlet: 63 mm | material: ss(stainless steel), type: oblique, head: single, coupling: ss(stainless steel) instantaneous male, accessories: rubber cap and chain, standard: indian standard 5290, accessories: matching flanges, gasket, nuts and bolts |  | 2.0 | Nos
I ¦ PAINTS CONTROL LAB I1 ¦ HYDRANT SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. a ¦ Size 80 mm NB | butterfly valve | size: 80 mm NB | standard: british standard 5155, type: wafer, accessories: matching flanges, nuts & bolts, fittings: necessary fittings by erection vendor |  | 2.0 | Nos
I ¦ PAINTS CONTROL LAB I1 ¦ HYDRANT SYSTEM | Supply & installation of SS branch pipe with 20 mm nozzle conforming to IS : 903 complete | branch pipe | nozzle: 20 mm | material: ss(stainless steel), standard: indian standard 903 |  | 2.0 | Nos
I ¦ PAINTS CONTROL LAB I1 ¦ HYDRANT SYSTEM | Supply & installation of 63 mm dia rubberized reinforced rubber line hose pipe in 15 m length conforming to IS : 636 Type II ISI marked with gunmetal male and female instantaneous coupling conforming to IS 903 wounded with 18 SWG copper wire complete | rubber line hose pipe | diameter: 63 mm, length: 15 m | material: rubberized reinforced rubber, standard: indian standard 636 Type II, certification: ISI, coupling: gunmetal male and female instantaneous, coupling standard: indian standard 903, reinforcement: 18 SWG copper wire |  | 4.0 | Nos
I ¦ PAINTS CONTROL LAB I1 ¦ HYDRANT SYSTEM | Supply & installation of MS Hose Box of fabricated from 16 SWG CRCA sheet double door with lockable arrangements to accommodate 2 RRL hose of 15 m length and one branch pipe painted white inside and red outside with one key. (750X600X250 mm) | hose box | box size: 750X600X250 mm, accommodates: 2 RRL hose of 15 m length and one branch pipe | material: ms(mild steel), fabrication: 16 SWG CRCA sheet, door: double, lockable: yes, painting: white inside and red outside, accessories: one key |  | 2.0 | Nos
I ¦ PAINTS CONTROL LAB I2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. e ¦ 40 mm NB | ms black steel pipe | size: 40 mm NB | material: ms(mild steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 Part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, scope: all related civil work, supports etc of vendor's scope |  | 18.0 | Mtr
I ¦ PAINTS CONTROL LAB I2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. f ¦ 25 mm NB | ms black steel pipe | size: 25 mm NB | material: ms(mild steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 Part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint type: grooved with groove coupling, scope: all related civil work, supports etc of vendor's scope |  | 54.0 | Mtr
I ¦ PAINTS CONTROL LAB I2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. a ¦ Size80 mm NB | butterfly valve | size: 80 mm NB | standard: british standard 5155, type: wafer, fittings: matching flanges, nuts & bolts, feature: necessary fittings provided by erection vendor |  | 1.0 | Nos
I ¦ PAINTS CONTROL LAB I2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. b ¦ Size40 mm NB | butterfly valve | size: 40 mm NB | standard: british standard 5155, type: wafer, fittings: matching flanges, nuts & bolts, feature: necessary fittings provided by erection vendor |  | 1.0 | Nos
I ¦ PAINTS CONTROL LAB I2 ¦ AUTOMATIC SPRINKLER SYSTEM | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts confirming IS:5312(PN16). a ¦ Size80 mm NB | non return valve | size: 80 mm NB | type: wafer, fittings: matching flanges, nuts & bolts, standard: indian standard 5312(PN16) |  | 1.0 | Nos
I ¦ PAINTS CONTROL LAB I2 ¦ AUTOMATIC SPRINKLER SYSTEM | Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts confirming IS:5312(PN16). b ¦ Size40 mm NB | non return valve | size: 40 mm NB | type: wafer, fittings: matching flanges, nuts & bolts, standard: indian standard 5312(PN16) |  | 1.0 | Nos
I ¦ PAINTS CONTROL LAB I2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & fixing of paddle type Flow Switch | flow switch |  | type: paddle |  | 2.0 | Nos
I ¦ PAINTS CONTROL LAB I2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Fixing of Sprinkler Head Pendent type for K factor-80. Temp rating 68 deg C.UL/FM Approved. | sprinkler head pendent type | k factor: 80 | temperature rating: 68 deg C, certification: UL(underwriters laboratories), certification: FM(factory mutual) |  | 26.0 | Nos
I ¦ PAINTS CONTROL LAB I2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, installation of automatic 25 NB Air Release Valve | air release valve | size: 25 NB | feature: automatic |  | 1.0 | Nos
I ¦ PAINTS CONTROL LAB I2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends a ¦ Size 40NB | globe valve | size: 40 NB | material: bronze, standard: indian standard 778, end connection: screwed |  | 2.0 | Nos
I ¦ PAINTS CONTROL LAB I2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends b ¦ Size 25NB | globe valve | size: 25 NB | material: bronze, standard: indian standard 778, end connection: screwed |  | 2.0 | Nos
I ¦ PAINTS CONTROL LAB I2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply,Erection and testing of Installation Control Valve complete with trims & gong. a ¦ Size 100 mm NB | installation control valve | size: 100 mm NB | feature: complete with trims & gong |  | 1.0 | Nos
I ¦ PAINTS CONTROL LAB I2 ¦ AUTOMATIC SPRINKLER SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. a ¦ Size 100 mm NB | cs gate valve | size: 100 mm NB | material: cs(carbon steel), standard: api 600, class: 150, fittings: matching flanges, nuts & bolts |  | 1.0 | Nos
I ¦ PAINTS CONTROL LAB I3 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | analogue addressable multicriteria detector |  |  |  | 13.0 | Nos
I ¦ PAINTS CONTROL LAB I3 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Manual Call point | analogue addressable manual call point |  |  |  | 3.0 | Nos
I ¦ PAINTS CONTROL LAB I3 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of Hooter cum strobe | hooter cum strobe |  |  |  | 3.0 | Nos
I ¦ PAINTS CONTROL LAB I3 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of Telephone jack. | telephone jack |  |  |  | 2.0 | Nos
I ¦ PAINTS CONTROL LAB I3 ¦ FDA SYSTEM | Supply, erction, testing & commissioning of analogue addressable Control Module | analogue addressable control module |  |  |  | 2.0 | Nos
I ¦ PAINTS CONTROL LAB I3 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Isolator Module | analogue addressable isolator module |  |  |  | 2.0 | Nos
I ¦ PAINTS CONTROL LAB I3 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of analogue addressable Monitor module | analogue addressable monitor module |  |  |  | 2.0 | Nos
I ¦ PAINTS CONTROL LAB I3 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. a ¦ 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cabling | cable: 2C x 1.5 mm2 | feature: complete with lugs, laying and termination of both ends, type: loop cable |  | 125.0 | Mtr
I ¦ PAINTS CONTROL LAB I3 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. a ¦ 2C x 1.5 mm2 Armoured ( Power cable) | armoured cabling | cable: 2C x 1.5 mm2 | feature: complete with lugs, laying and termination of both ends, type: power cable |  | 50.0 | Mtr
I ¦ PAINTS CONTROL LAB I3 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. a ¦ 2C x 0.5 mm2 Armoured ( Telephone cable) | armoured cabling | cable: 2C x 0.5 mm2 | feature: complete with lugs, laying and termination of both ends, type: telephone cable |  | 20.0 | Mtr
I ¦ PAINTS CONTROL LAB I3 ¦ FDA SYSTEM | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable trays |  | feature: for laying all type of cables as indicated above including all necessary structural supports |  | 131.0 | Mtr
I ¦ PAINTS CONTROL LAB I4 ¦ PA SYSTEM | IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | ip based networkable touch screen paging station |  | feature: selection of zones, supervision of system status, setting of scheduled broadcasts, central exchange with stand by CPU, built-in monitoring loudspeaker, goose-neck microphone, LCD touchscreen display, audio input |  | 1.0 | Nos
I ¦ PAINTS CONTROL LAB I4 ¦ PA SYSTEM | 3 ¦ Rack Mounted 100 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | power amplifier | power: 100 watt | mounting: rack mounted, feature: battery back up, feature: wattage shall be as per requirement |  | 1.0 | Nos
I ¦ PAINTS CONTROL LAB I4 ¦ PA SYSTEM | 4 ¦ 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | xlpe cu cable | conductor: 2C, cross section: 1.5 mm2 | type: multi stranded, shielding: shielded, armor: armoured, insulation: xlpe, conductor material: copper, application: power & signal |  | 131.0 | Mtr
I ¦ PAINTS CONTROL LAB I4 ¦ PA SYSTEM | 5 ¦ DVD player with features to hook up to amplifiers of PA system for music in the common areas. | dvd player |  | feature: hook up to amplifiers of PA system, application: music in the common areas |  | 1.0 | Nos
I ¦ PAINTS CONTROL LAB I4 ¦ PA SYSTEM | 6 ¦ Paging Loudspeaker | loudspeaker |  | feature: paging |  | 1.0 | Nos