## Sheet1
section_context_for_this_product_block | full_product_description | core_product_name | size | feature_or_specifications | acronymed_core_product_name | quantity | unit
C ¦ RESIN PLANT, RISHRA; C1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Groove joints to be done for erection of pipes with proper couplings and fasteners. All escavations, pedestal supports, structural supports shall be of vendor's scope. 150 mm NB | ms black steel pipe | size: 150 mm NB | material: ms(mild steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint: groove joints with proper couplings and fasteners, scope: all excavations, pedestal supports, structural supports by vendor |  | 12.0 | Mtr
C ¦ RESIN PLANT, RISHRA; C1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Groove joints to be done for erection of pipes with proper couplings and fasteners. All escavations, pedestal supports, structural supports shall be of vendor's scope. 80 mm NB | ms black steel pipe | size: 80 mm NB | material: ms(mild steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint: groove joints with proper couplings and fasteners, scope: all excavations, pedestal supports, structural supports by vendor |  | 6.0 | Mtr
C ¦ RESIN PLANT, RISHRA; C1 ¦ HYDRANT SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Groove joints to be done for erection of pipes with proper couplings and fasteners. All escavations, pedestal supports, structural supports shall be of vendor's scope. 25 mm NB | ms black steel pipe | size: 25 mm NB | material: ms(mild steel), grade: heavy, thickness: 5.4mm, standard: indian standard 1239 part -1, fittings: elbows, tees, flanges, reduces clamps, ms support dash fasteners, painting: two coats of approved primer and two coats of approved paint, joint: groove joints with proper couplings and fasteners, scope: all excavations, pedestal supports, structural supports by vendor |  | 6.0 | Mtr
C ¦ RESIN PLANT, RISHRA; C1 ¦ HYDRANT SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, Class 150 with matching flanges, bolts, nuts and gaskets. Size 150 mm NB | gate valve | size: 150 mm NB | material: cs(carbon steel), standard: API 600, class: 150, accessories: matching flanges, bolts, nuts and gaskets |  | 1.0 | Nos
C ¦ RESIN PLANT, RISHRA; C1 ¦ HYDRANT SYSTEM | Supply, installation, testing and commissioning of CS Non return valve as per BS 1868, Class 150, with companion flanges,nuts & bolts and gaskets. Size 150 mm NB | non return valve | size: 150 mm NB | material: cs(carbon steel), standard: BS 1868, class: 150, accessories: companion flanges, nuts & bolts and gaskets |  | 1.0 | Nos
C ¦ RESIN PLANT, RISHRA; C1 ¦ HYDRANT SYSTEM | Supply & installation of SS oblique type single headed Landing valve with 80 mm inlet and 63 mm outlet SS instantaneous male coupling with rubber cap and chain conforming to IS : 5290 including matching flanges, gasket, nuts and bolts complete. | landing valve | inlet: 80 mm, outlet: 63 mm | material: ss(stainless steel), type: oblique, head: single, coupling: ss(stainless steel) instantaneous male, accessories: rubber cap and chain, standard: indian standard 5290, accessories: matching flanges, gasket, nuts and bolts |  | 3.0 | Nos
C ¦ RESIN PLANT, RISHRA; C1 ¦ HYDRANT SYSTEM | Supply,Installation of Butterfly valve as per BS :5155 (Wafer type) matching flanges complete with nuts & bolts.. Necessary fittings shall be provided by erection vendor. Size 80 mm NB | butterfly valve | size: 80 mm NB | standard: BS 5155, type: wafer, accessories: matching flanges, nuts & bolts, fittings: necessary fittings by erection vendor |  | 3.0 | Nos
C ¦ RESIN PLANT, RISHRA; C1 ¦ HYDRANT SYSTEM | Supply & installation of SS branch pipe with 20 mm nozzle conforming to IS : 903 complete | branch pipe | nozzle: 20 mm | material: ss(stainless steel), standard: indian standard 903 |  | 3.0 | Nos
C ¦ RESIN PLANT, RISHRA; C1 ¦ HYDRANT SYSTEM | Supply & installation of 63 mm dia rubberized reinforced rubber line hose pipe in 15 m length conforming to IS : 636 Type II ISI marked with gunmetal male and female instantaneous coupling conforming to IS 903 wounded with 18 SWG copper wire complete | hose pipe | diameter: 63 mm, length: 15 m | type: rubberized reinforced rubber line, standard: indian standard 636 type II ISI marked, coupling: gunmetal male and female instantaneous, coupling standard: indian standard 903, wire: 18 SWG copper wire |  | 6.0 | Nos
C ¦ RESIN PLANT, RISHRA; C1 ¦ HYDRANT SYSTEM | Supply & installation of MS Hose Box of fabricated from 16 SWG CRCA sheet double door with lockable arrangements to accommodate 2 RRL hose of 15 m length and one branch pipe painted white inside and red outside with one key. (750X600X250 mm) | hose box | dimensions: 750X600X250 mm | material: ms(mild steel), sheet: 16 SWG CRCA, door: double, lockable: yes, capacity: 2 RRL hose of 15 m length and one branch pipe, paint: white inside and red outside, accessories: one key |  | 3.0 | Nos
C ¦ RESIN PLANT, RISHRA; C1 ¦ HYDRANT SYSTEM | Supply & installation of swinging type hose reel drum fabricated from 14 SWG CRCA sheets painted with red colour stove paint 2 coats over 1 coat of primer with 30 m long 20 mm dia rubber hose pipe with with SS self closing shut – off nozzle of 5 mm outlet fixed on wall. | hose reel drum | hose length: 30 m, hose diameter: 20 mm, nozzle outlet: 5 mm | type: swinging, material: 14 SWG CRCA sheets, paint: red colour stove paint 2 coats over 1 coat of primer, hose: rubber, nozzle: ss(stainless steel) self closing shut-off, mounting: fixed on wall |  | 3.0 | Nos
C ¦ RESIN PLANT, RISHRA; C1 ¦ HYDRANT SYSTEM | Supply and installation of pressure gauge, 1/2 inch bottom entry, of suitable range with ball valves and other accessories. | pressure gauge | bottom entry: 1/2 inch | range: suitable, accessories: ball valves and other accessories |  | 1.0 | Nos
C ¦ RESIN PLANT, RISHRA; C1 ¦ HYDRANT SYSTEM | Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends, Size 25NB | globe valve | size: 25NB | material: bronze, standard: indian standard 778, end-type: screwed |  | 5.0 | Nos
C ¦ RESIN PLANT, RISHRA; C1 ¦ HYDRANT SYSTEM | Supply & installation of 250ltr portable foam tank filled with 3% ARFFF foam concentrate with foam making branch and pick up tube. | portable foam tank | tank capacity: 250ltr | foam concentrate: 3% ARFFF, feature: foam making branch and pick up tube |  | 1.0 | Nos
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection , testing & commissioning of Deluge valve, with dry pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 2 way Solenoid Valve, and other accessories etc. & manual release unit., 150 mm NB | deluge valve | size: 150 mm NB | feature: dry pilot trim assembly, feature: fitted with strainer, feature: drain valve, feature: pressure gauge, feature: pressure switch, feature: flame proof 2 way solenoid valve, feature: manual release unit |  | 1.0 | Nos
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection , testing & commissioning of Deluge valve, with dry pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 2 way Solenoid Valve, and other accessories etc. & manual release unit., 80 mm NB | deluge valve | size: 80 mm NB | feature: dry pilot trim assembly, feature: fitted with strainer, feature: drain valve, feature: pressure gauge, feature: pressure switch, feature: flame proof 2 way solenoid valve, feature: manual release unit |  | 2.0 | Nos
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, Class 150 with matching flanges complete with nuts, bolts and gaskets., 150 mm NB | gate valve | size: 150 mm NB | material: cs(carbon steel), standard: API 600, class: 150, end-type: matching flanges, feature: complete with nuts, bolts and gaskets |  | 3.0 | Nos
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, Class 150 with matching flanges complete with nuts, bolts and gaskets., 80 mm NB | gate valve | size: 80 mm NB | material: cs(carbon steel), standard: API 600, class: 150, end-type: matching flanges, feature: complete with nuts, bolts and gaskets |  | 6.0 | Nos
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing and commissioning of Y-Strainer., Size 150 mm NB | y-strainer | size: 150 mm NB |  |  | 1.0 | Nos
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply, installation, testing and commissioning of Y-Strainer., Size 80 mm NB | y-strainer | size: 80 mm NB |  |  | 2.0 | Nos
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply,installation,testing and commissioning of Foam Sprinkler nozzle with necessary threaded fittings as per drawing. The sprinkler shall be Open Aspiration, Pendent type, K-42 with standard spray angle.End connection 1/2" NPT/BSP.UL/FM Approved., Spray nozzle K factor -42 | foam sprinkler nozzle | k factor: 42, end connection: 1/2" NPT/BSP | feature: open aspiration, type: pendent, spray angle: standard, certification: UL(underwriters laboratories), certification: FM(factory mutual), feature: necessary threaded fittings as per drawing |  | 123.0 | Nos
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply,installation and commissioning of UL/FM approved Quartzoid Bulb Detector for K factor-80. Temp rating 68 deg C. | quartzoid bulb detector | k factor: 80 | certification: UL(underwriters laboratories), certification: FM(factory mutual), temperature rating: 68 deg C |  | 123.0 | Nos
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Capacity of 2100 ltr. | capacity | capacity: 2100 ltr. |  |  | 1.0 | Nos
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply of AR-AFFF(3%) foam concentrate(PFOS/PFAS free) having sp. Gravity 1.0±.02 g/mlat 20⁰C , PH 7.0-8.5 & viscosity 1200 ±300 cps. | ar-afff foam concentrate |  | concentration: 3%, pfos/pfas: free, specific gravity: 1.0±.02 g/ml at 20°C, ph: 7.0-8.5, viscosity: 1200 ±300 cps | ar-afff foam concentrate | 2100.0 | Ltr
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 150 NB | gi pipe | size: 150 NB | class: c class (heavy class), standard: indian standard 1239, fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, fixing: clamps to ms brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, location: above ground, specification: as per specifications | gi pipe | 32.0 | Mtr
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 100 NB | gi pipe | size: 100 NB | class: c class (heavy class), standard: indian standard 1239, fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, fixing: clamps to ms brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, location: above ground, specification: as per specifications | gi pipe | 16.0 | Mtr
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 80 NB | gi pipe | size: 80 NB | class: c class (heavy class), standard: indian standard 1239, fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, fixing: clamps to ms brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, location: above ground, specification: as per specifications | gi pipe | 92.0 | Mtr
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 65 NB | gi pipe | size: 65 NB | class: c class (heavy class), standard: indian standard 1239, fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, fixing: clamps to ms brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, location: above ground, specification: as per specifications | gi pipe | 36.0 | Mtr
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 50 NB | gi pipe | size: 50 NB | class: c class (heavy class), standard: indian standard 1239, fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, fixing: clamps to ms brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, location: above ground, specification: as per specifications | gi pipe | 46.0 | Mtr
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 40NB | gi pipe | size: 40NB | class: c class (heavy class), standard: indian standard 1239, fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, fixing: clamps to ms brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, location: above ground, specification: as per specifications | gi pipe | 129.0 | Mtr
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 25NB | gi pipe | size: 25NB | class: c class (heavy class), standard: indian standard 1239, fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, fixing: clamps to ms brackets/hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, location: above ground, specification: as per specifications | gi pipe | 952.0 | Mtr
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved red oxide primer and two coats of approved red enamel paint. Pipe joints shall be with grooved coupling. All escavation, pedestal supports, structural supports shall be of vendor's scope. 150 mm NB | ms black steel pipe | size: 150 mm NB, thickness: 5.4mm | grade: heavy, standard: indian standard 1239 part-1, fittings included: elbows, tees, flanges, reducers, clamps, ms support dash fasteners, painting: two coats approved red oxide primer, two coats approved red enamel paint, joint: grooved coupling, excavation: included, pedestal supports: included, structural supports: included, scope: vendor's | ms black steel pipe | 18.0 | Mtr
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved red oxide primer and two coats of approved red enamel paint. Pipe joints shall be with grooved coupling. All escavation, pedestal supports, structural supports shall be of vendor's scope. 100 mm NB | ms black steel pipe | size: 100 mm NB, thickness: 5.4mm | grade: heavy, standard: indian standard 1239 part-1, fittings included: elbows, tees, flanges, reducers, clamps, ms support dash fasteners, painting: two coats approved red oxide primer, two coats approved red enamel paint, joint: grooved coupling, excavation: included, pedestal supports: included, structural supports: included, scope: vendor's | ms black steel pipe | 12.0 | Mtr
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved red oxide primer and two coats of approved red enamel paint. Pipe joints shall be with grooved coupling. All escavation, pedestal supports, structural supports shall be of vendor's scope. 80 mm NB | ms black steel pipe | size: 80 mm NB, thickness: 5.4mm | grade: heavy, standard: indian standard 1239 part-1, fittings included: elbows, tees, flanges, reducers, clamps, ms support dash fasteners, painting: two coats approved red oxide primer, two coats approved red enamel paint, joint: grooved coupling, excavation: included, pedestal supports: included, structural supports: included, scope: vendor's | ms black steel pipe | 12.0 | Mtr
C ¦ RESIN PLANT, RISHRA; C2 ¦ FOAM WATER SPRAY SYSTEM | Supply, erection, testing & commissioning of Air Buffer tank complete with necessary components. The compressor shall be of capacity 15 M³/Hr( FAD), discharge pressure 10 bar, single stage, reciprocating type. | air buffer tank | compressor capacity: 15 M³/Hr (FAD) | discharge pressure: 10 bar, compressor type: single stage, reciprocating, components: necessary components included |  | 1.0 | Nos
C ¦ RESIN PLANT, RISHRA; C3 ¦ AUTOMATIC SPRINKLER SYSTEM | a ¦ Size 80 mm NB |  | size: 80 mm NB |  |  | 1.0 | Nos
C ¦ RESIN PLANT, RISHRA; C3 ¦ AUTOMATIC SPRINKLER SYSTEM | b ¦ Size 50 mm NB |  | size: 50 mm NB |  |  | 1.0 | Nos
C ¦ RESIN PLANT, RISHRA; C3 ¦ AUTOMATIC SPRINKLER SYSTEM | 3 ¦ Providing & fixing Non return valve (Wafer type) with matching flanges complete with nuts & bolts confirming to API 594. | non return valve |  | type: wafer, flanges: matching, accessories: nuts & bolts, standard: api 594
C ¦ RESIN PLANT, RISHRA; C3 ¦ AUTOMATIC SPRINKLER SYSTEM | a ¦ Size 80 mm NB | non return valve | size: 80 mm NB |  |  | 1.0 | Nos
C ¦ RESIN PLANT, RISHRA; C3 ¦ AUTOMATIC SPRINKLER SYSTEM | b ¦ Size 50 mm NB | non return valve | size: 50 mm NB |  |  | 1.0 | Nos
C ¦ RESIN PLANT, RISHRA; C3 ¦ AUTOMATIC SPRINKLER SYSTEM | 4 ¦ Supply & fixing of Paddle type Flow Switch | paddle type flow switch |  |  |  | 2.0 | Nos
C ¦ RESIN PLANT, RISHRA; C3 ¦ AUTOMATIC SPRINKLER SYSTEM | 5 ¦ Supply,Fixing of Sprinkler Head Pendent type for K factor-80. Temp rating 68 deg C.UL/FM Approved. | sprinkler head pendent type | k factor: 80 | temperature rating: 68 deg C, certification: ul(underwriters laboratories), certification: fm(factory mutual) |  | 37.0 | Nos
C ¦ RESIN PLANT, RISHRA; C3 ¦ AUTOMATIC SPRINKLER SYSTEM | 6 ¦ Supply, installation of automatic 25 NB Air Release Valve | air release valve | size: 25 NB | feature: automatic |  | 1.0 | Nos
C ¦ RESIN PLANT, RISHRA; C3 ¦ AUTOMATIC SPRINKLER SYSTEM | 7 ¦ Supply & installation of Bronze Globe Valves conforming to IS: 778 with screwed ends | globe valve |  | material: bronze, standard: indian standard 778, ends: screwed
C ¦ RESIN PLANT, RISHRA; C3 ¦ AUTOMATIC SPRINKLER SYSTEM | a ¦ Size 25NB | globe valve | size: 25NB |  |  | 5.0 | Nos
C ¦ RESIN PLANT, RISHRA; C3 ¦ AUTOMATIC SPRINKLER SYSTEM | b ¦ Size 40NB | globe valve | size: 40NB |  |  | 2.0 | Nos
C ¦ RESIN PLANT, RISHRA; C3 ¦ AUTOMATIC SPRINKLER SYSTEM | 8 ¦ Supply,Erection and testing of Installation Control Valve complete with trims & gong. | installation control valve |  | accessories: trims & gong
C ¦ RESIN PLANT, RISHRA; C3 ¦ AUTOMATIC SPRINKLER SYSTEM | a ¦ Size 80 mm NB | installation control valve | size: 80 mm NB |  |  | 1.0 | Nos
C ¦ RESIN PLANT, RISHRA; C3 ¦ AUTOMATIC SPRINKLER SYSTEM | 9 ¦ Supply, installation, testing & commissioning of CS Gate Valve as per API 600 with matching flanges complete with nuts,bolts and gaskets. | gate valve |  | material: cs(carbon steel), standard: api 600, flanges: matching, accessories: nuts, bolts and gaskets
C ¦ RESIN PLANT, RISHRA; C3 ¦ AUTOMATIC SPRINKLER SYSTEM | a ¦ Size 80 NB | gate valve | size: 80 NB |  |  | 1.0 | Nos
C ¦ RESIN PLANT, RISHRA; C4 ¦ FDA SYSTEM | 1 ¦ Supply, erection, testing & commissioning of analogue addressable Multicriteria Detector | analogue addressable multicriteria detector |  |  |  | 9.0 | Nos
C ¦ RESIN PLANT, RISHRA; C4 ¦ FDA SYSTEM | 2 ¦ Supply, erection, testing & commissioning of analogue addressable Heat Detector | analogue addressable heat detector |  |  |  | 2.0 | Nos
C ¦ RESIN PLANT, RISHRA; C4 ¦ FDA SYSTEM | 3 ¦ Supply, erection, testing & commissioning of IR Detector | ir detector |  |  | ir detector | 8.0 | Nos
C ¦ RESIN PLANT, RISHRA; C4 ¦ FDA SYSTEM | 4 ¦ Supply, erection, testing & commissioning of analogue addressable explosion proof Manual Call point | manual call point |  | type: analogue addressable, feature: explosion proof |  | 6.0 | Nos
C ¦ RESIN PLANT, RISHRA; C4 ¦ FDA SYSTEM | 5 ¦ Supply, erection, testing & commissioning of explosion proo Hooter cum strobe | hooter cum strobe |  | feature: explosion proof |  | 10.0 | Nos
C ¦ RESIN PLANT, RISHRA; C4 ¦ FDA SYSTEM | 6 ¦ Supply, erction, testing & commissioning of analogue addressable Control Module | control module |  | type: analogue addressable |  | 8.0 | Nos
C ¦ RESIN PLANT, RISHRA; C4 ¦ FDA SYSTEM | 7 ¦ Supply, erection, testing & commissioning of analogue addressable Isolator Module | isolator module |  | type: analogue addressable |  | 3.0 | Nos
C ¦ RESIN PLANT, RISHRA; C4 ¦ FDA SYSTEM | 8 ¦ Supply, erection, testing & commissioning of analogue addressable Monitor module | monitor module |  | type: analogue addressable |  | 12.0 | Nos
C ¦ RESIN PLANT, RISHRA; C4 ¦ FDA SYSTEM | 9 ¦ Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. a ¦ 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cabling | cable size: 2C x 1.5 mm2 | feature: loop cable, feature: armoured, feature: complete with lugs, feature: laying and termination of both ends |  | 389.0 | Mtr
C ¦ RESIN PLANT, RISHRA; C4 ¦ FDA SYSTEM | 10 ¦ Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. a ¦ 2C x 1.5 mm2 Armoured ( Power cable) | armoured cabling | cable size: 2C x 1.5 mm2 | feature: power cable, feature: armoured, feature: complete with lugs, feature: laying and termination of both ends |  | 297.0 | Mtr
C ¦ RESIN PLANT, RISHRA; C4 ¦ FDA SYSTEM | 11 ¦ Supply, erection, fabrication, testing and commission of VOC detector with range of 1 – 1000 ppm isobutylene equivalent.and following accessoriesa) DigiPID internal dust filter (Pack of 5) b) Waterproof Filter Assy, RAEGuard2 PID, Pack of 5 c) DigiPID Teflon UV electrode shield pack of 10 d) DigiPID Dust Cover e) Air Drying Pre Filter Kit f) DigiPID external water trap filter (Pack of 5) | voc detector | range: 1 – 1000 ppm isobutylene equivalent | accessories: DigiPID internal dust filter (Pack of 5), accessories: Waterproof Filter Assy, RAEGuard2 PID, Pack of 5, accessories: DigiPID Teflon UV electrode shield pack of 10, accessories: DigiPID Dust Cover, accessories: Air Drying Pre Filter Kit, accessories: DigiPID external water trap filter (Pack of 5) |  | 11.0 | Nos
C ¦ RESIN PLANT, RISHRA; C4 ¦ FDA SYSTEM | 12 ¦ Supply, installation, testing and commissioning of aspiration detector with CMOS imager combined with multiple photodiode for reliable very early warning in a wide range of environments with minimal nuisance alarms. The detector should have 4 pipe inlet and min 100m pipelength support per inlet.The detector should have Smart on-board two stage filter retains dust count and remaining filter life for predictable maintenance& coverage area of min 2000 Sq.Mtr | aspiration detector | pipe inlet: 4, pipelength support per inlet: min 100m, coverage area: min 2000 Sq.Mtr | imager: CMOS, feature: combined with multiple photodiode, feature: very early warning, feature: minimal nuisance alarms, filter: Smart on-board two stage filter retains dust count and remaining filter life for predictable maintenance |  | 4.0 | Nos
C ¦ RESIN PLANT, RISHRA; C4 ¦ FDA SYSTEM | 13 ¦ Supply,Installation,Testing & Commissioning of UL/VDS listed CPVC Pipe 25 mm Dia & Pipe Accessories for the Aspiration detection. | cpvc pipe | diameter: 25 mm | certification: UL(underwriters laboratories), certification: VDS, feature: listed, feature: pipe accessories for the aspiration detection |  | 304.0 | Mtr
C ¦ RESIN PLANT, RISHRA; C4 ¦ FDA SYSTEM | 14 ¦ Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable trays |  | feature: for laying all type of cables, feature: including all necessary structural supports |  | 389.0 | Mtr
C ¦ RESIN PLANT, RISHRA; C5 ¦ PA SYSTEM | 1 ¦ IP based Networkable touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Central exchage with Stand by CPU . Built-in monitoring loudspeaker . Goose-neck microphone . LCD touchscreen display . Audio input | ip based networkable touch screen paging station |  | feature: selection of zones, feature: supervision of system status, feature: setting of scheduled broadcasts, feature: central exchange with stand by CPU, feature: built-in monitoring loudspeaker, feature: goose-neck microphone, feature: LCD touchscreen display, feature: audio input |  | 1.0 | Nos
C ¦ RESIN PLANT, RISHRA; C5 ¦ PA SYSTEM | 3 ¦ 9 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | horn type of speaker | power: 9 W | feature: high efficiency, weather protection: IP 65 (weatherproof type), feature: suitable for outdoor area |  | 2.0 | Nos
C ¦ RESIN PLANT, RISHRA; C5 ¦ PA SYSTEM | 4 ¦ 15 W High Efficiency Horn type of Speaker with weather protection IP 65 (Weatherproof Type, Suitable for Outdoor Area) | horn type of speaker | power: 15 W | feature: high efficiency, weather protection: IP 65 (weatherproof type), feature: suitable for outdoor area |  | 6.0 | Nos
C ¦ RESIN PLANT, RISHRA; C5 ¦ PA SYSTEM | 5 ¦ Rack Mounted 200 watt Power Amplifier with battery back up (Wattage shall be as per requirement) | power amplifier | power: 200 watt | mounting: rack mounted, feature: battery back up, feature: wattage shall be as per requirement |  | 1.0 | Nos
C ¦ RESIN PLANT, RISHRA; C5 ¦ PA SYSTEM | 6 ¦ 2C x 1.5 mm2 multi stranded, shielded, Armoured, XLPE Cu Cable for Power & Signal | xlpe cu cable | core: 2C, cross section: 1.5 mm2 | feature: multi stranded, feature: shielded, feature: armoured, application: for power & signal |  | 260.0 | Mtr
C ¦ RESIN PLANT, RISHRA; C5 ¦ PA SYSTEM | 7 ¦ DVD player with features to hook up to amplifiers of PA system for music in the common areas. | dvd player |  | feature: features to hook up to amplifiers of PA system for music in the common areas |  | 1.0 | Nos
C ¦ RESIN PLANT, RISHRA; C5 ¦ PA SYSTEM | 8 ¦ Paging Loudspeaker | paging loudspeaker |  |  |  | 1.0 | Nos