## Sheet1
section_context_for_this_product_block | full_product_description | core_product_name | size | feature_or_specifications | acronymed_core_product_name | quantity | unit
M ¦ SOFA TANK M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, erection , testing & commissioning of Deluge valve with wet pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch, flame proof 3/2 way Solenoid Valve, air filter regulator etc. & manual release unit. The valve shall be electro-pneumatic type. | deluge valve |  | trim assembly: wet pilot, fitted with: strainer, fitted with: drain valve, fitted with: pressure gauge, fitted with: pressure switch, fitted with: flame proof 3/2 way solenoid valve, fitted with: air filter regulator, fitted with: manual release unit, type: electro-pneumatic
M ¦ SOFA TANK M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | 150 mm NB | deluge valve | size: 150 mm NB |  |  | 1.0 | Nos
M ¦ SOFA TANK M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. | gate valve |  | material: cs(carbon steel), standard: API 600, class: 150, flanges: matching, complete with: nuts & bolts
M ¦ SOFA TANK M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | 150 mm NB | gate valve | size: 150 mm NB |  |  | 3.0 | Nos
M ¦ SOFA TANK M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, installation, testing of Y- Stainer. | y-stainer
M ¦ SOFA TANK M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | 150 mm NB | y-stainer | size: 150 mm NB |  |  | 1.0 | Nos
M ¦ SOFA TANK M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply,installation and commissioning of UL/FM approved Medium Velocity Water Spray Nozzle | medium velocity water spray nozzle |  | certification: UL(underwriters laboratories), certification: FM(factory mutual)
M ¦ SOFA TANK M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | MVWS nozzle K factor 18, spray angle 100⁰ | medium velocity water spray nozzle | k factor: 18, spray angle: 100⁰ |  | mvws nozzle | 66.0 | Nos
M ¦ SOFA TANK M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply,installation and commissioning of UL/FM approved Quartzoid Bulb Detector for K factor-80. Temp rating 68 deg C | quartzoid bulb detector | k factor: 80, temperature rating: 68 deg C | certification: UL(underwriters laboratories), certification: FM(factory mutual) |  | 66.0 | Nos
M ¦ SOFA TANK M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications | gi "c" class pipes |  | class: heavy, standard: IS 1239, fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, fixing: clamps to MS brackets / hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, application: above ground pipes
M ¦ SOFA TANK M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | 150 NB | gi "c" class pipes | size: 150 NB |  |  | 24.0 | Mtr
M ¦ SOFA TANK M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | 100 NB | gi "c" class pipes | size: 100 NB |  |  | 24.0 | Mtr
M ¦ SOFA TANK M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | 80 NB | gi "c" class pipes | size: 80 NB |  |  | 30.0 | Mtr
M ¦ SOFA TANK M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | 65 NB | gi "c" class pipes | size: 65 NB |  |  | 60.0 | Mtr
M ¦ SOFA TANK M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, erection, fabrication, testing of MS black steel pipe Heavy grade of thickness 5.4mm conforming to IS : 1239 Part -1 including all fittings viz. Elbows, tees, flanges, etc. reduces clamps, MS support dash fasteners etc. including painting the pipe with two coats of approved primer and two coats of approved paint. Pipe joints shall be grooved with groove coupling. All related civil work, supports etc shall be of vendor's scope. | ms black steel pipe | thickness: 5.4mm | grade: heavy, standard: IS 1239 Part-1, fittings included: elbows, tees, flanges, reduces clamps, MS support dash fasteners, painting: two coats approved primer, painting: two coats approved paint, joints: grooved with groove coupling, civil work: vendor's scope
M ¦ SOFA TANK M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | 150 NB | ms black steel pipe | size: 150 NB |  |  | 36.0 | Mtr
M ¦ SOFA TANK M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | 25 NB | ms black steel pipe | size: 25 NB |  |  | 218.0 | Mtr
M ¦ SOFA TANK M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, erction, testing & commissioning of analogue addressable Control Module | analogue addressable control module |  |  |  | 1.0 | Nos
M ¦ SOFA TANK M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 150 NB | gi pipe | size: 150 NB | class: c class (heavy class), standard: indian standard 1239, fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, fixing: clamps to ms brackets / hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, application: above ground pipes |  | 66.0 | Mtr
M ¦ SOFA TANK M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, erection, testing and commissioning of GI "C" Class(Heavy Class) pipes conforming to IS 1239 with threaded or grooved fittings with including cutting pipes to correct lengths, providing fittings like elbow,tee,reducer and welding flanges to pipe, fixing with clamps to MS brackets / hangers, steel supports as per drawing. Rate shall be inclusive of Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all above ground pies. Rates to be inclusive of all complete as per specifications 100 NB | gi pipe | size: 100 NB | class: c class (heavy class), standard: indian standard 1239, fittings: threaded or grooved, fittings included: elbow, tee, reducer, welding flanges, fixing: clamps to ms brackets / hangers, steel supports, primer: zinc chromate, paint: 2 coats red enamel, requirement: fire authorities, application: above ground pipes |  | 140.0 | Mtr
M ¦ SOFA TANK M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, erection , testing & commissioning of Deluge valve with dry pilot trim assembly,fitted with strainer, drain valve, pressure gauge, Pressure Switch,dry pilot actuator, air filter regulator etc. & manual release unit. Size 150 NB | deluge valve | size: 150 NB | trim assembly: dry pilot, fitted with: strainer, drain valve, pressure gauge, pressure switch, dry pilot actuator, air filter regulator, manual release unit: included |  | 4.0 | Nos
M ¦ SOFA TANK M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Providing & fixing Cast Iron Y Strainer. Size 150 NB | y strainer | size: 150 NB | material: cast iron |  | 4.0 | Nos
M ¦ SOFA TANK M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply & fixing of SS-304 FOAM GENERATOR with Minimum flow 120lpm | foam generator | minimum flow: 120 lpm | material: ss-304 |  | 8.0 | Nos
M ¦ SOFA TANK M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, installation, testing & commissioning of CS Gate Valve as per API 600, class 150 with matching flanges complete with nuts & bolts. Size 150 NB | gate valve | size: 150 NB | material: cs(carbon steel), standard: api 600, class: 150, flanges: matching, included: nuts & bolts |  | 12.0 | Nos
M ¦ SOFA TANK M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, installation, testing and commissioning of Atmospheric Foam tank vertical type ,manufacturing as per ASME, section-VIII part- I. Tank shall be supplied along with all necessary valves, fittingss & instruments as per Technical data sheet attached with Tender documents. Capacity of 250 ltr. | atmospheric foam tank | capacity: 250 ltr. | type: vertical, standard: asme section-viii part-i, supplied with: all necessary valves, fittings & instruments, reference: technical data sheet attached with tender documents |  | 4.0 | Nos
M ¦ SOFA TANK M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply of AR-AFFF(3%) foam concentrate (PFOS/PFAS free) having sp. Gravity 1.0±.02 g/mlat 20⁰C , pH 7.0-8.5 & viscosity 1200 ±300 cps. | foam concentrate |  | type: ar-afff(3%), pfos/pfas: free, specific gravity: 1.0±.02 g/ml at 20⁰c, ph: 7.0-8.5, viscosity: 1200 ±300 cps | ar-afff(3%) | 1000.0 | Ltr
M ¦ SOFA TANK M1 ¦ MEDIUM VELOCITY WATER SPRAY SYSTEM | Supply, installation, testing and commissioning of Inline Inductor 150NB | inline inductor | size: 150NB |  |  | 4.0 | Nos
M ¦ SOFA TANK M3 ¦ FDA SYSTEM | Supply, erection, testing & commissioning of IR Detector | ir detector |  |  |  | 5.0 | Nos
M ¦ SOFA TANK M3 ¦ FDA SYSTEM | Providing & fixing ARMOURED CABLING complete with lugs, laying and termination of both ends. a ¦ 2C x 1.5 mm2 Armoured ( Loop cable) | armoured cabling | cable: 2C x 1.5 mm2 | feature: complete with lugs, laying and termination of both ends, type: armoured, type: loop cable |  | 120.0 | Mtr
M ¦ SOFA TANK M3 ¦ FDA SYSTEM | Supply, fabrication, erection & testing of GI CABLE TRAYS FOR LAYING ALL TYPE OF CABLES AS INDICATED ABOVE INCLUDING ALL NECESSARY STRUCTURAL SUPPORTS. | gi cable trays |  | material: gi(galvanized iron), feature: for laying all type of cables as indicated above including all necessary structural supports |  | 120.0 | Mtr