## Sheet1
0 | 1 | 2 | 3 | 4 | 5
Instrument earthing with CU earth plate | Earthing with CU earth plate 600mmX600mmX3mm thick, GI Pipe of 19mm dia, 2 meter length including accessories as required as per IS-3043. Following points to be considered with earth pit. |  | 6 | nos
Instrument earthing with CU earth plate | a. Masonary enclosure with cover plate having locking arrangement.
Instrument earthing with CU earth plate | b. watering pipe
Instrument earthing with CU earth plate | c. charcole, salt (approximately 15kg charcoal and 15kg salt for each pit ) Refer attached drawing for further consideration.
Earthing with GI pipe | 25mmX3mm CU strip for instrument panel earthing. | 25mmX3mm | 150 | m
Earthing with GI pipe | 16 ways earthing copper plate with accessories |  | 4 | nos
Earthing with GI pipe | Earthing with GI earth pipe 3 meter long, 100 mm diameter including accessories as required as per IS-3043. Following points to be considered with earth pit. a. Masonary enclosure with cover plate having locking arrangement. b. charcole, salt (approximately 15kg charcoal and 15kg salt for each pit) Refer attached drawing for further consideration. |  | 12 | nos
Earthing with GI pipe | 50mmX6mm GI strip for main grid, panel earthing etc. | 50mmX6mm | 250 | m
Earthing with GI pipe | 25mmX3mm GI strip for main grid, panel earthing etc. | 25mmX3mm | 525 | m
Earthing with GI pipe | 10Sqmm CU earthing wire. |  | 300 | m
Earthing with GI pipe | Conductor Material: Plain annealed high conductivity Flexible copper conductor as per Class 5 of IS 8130/84 latest.
Earthing with GI pipe | Insulation material: PVC Type 'D' with FR-LSH Propertes.
Earthing with GI pipe | Rated voltage: 1100 V
Earthing with GI pipe | FRLS properties:
Earthing with GI pipe | Oxygen Index Min. 29% as per ASTM D- 2863
Earthing with GI pipe | Temperature Index Min. 250 Deg.C as per ASTM D- 2863
Earthing with GI pipe | Smoke Density Rating Max. 60% as per ASTM D- 2843
Earthing with GI pipe | Acid Gas Generation Max. 20% as per IEC- 754- 1
Earthing with GI pipe | Max. conductor temp. under normal operating conditions 70deg C
Earthing with GI pipe | 16 ways earting GI plate with accessories |  | 12 | nos
Earthing with GI pipe | 50Sqmm, 30m length CU earthing wire with clip reel & accessories | 50Sqmm, 30m | 1 | nos
Lighting arrester | 25mm dia, 1800mm long GI tube having single prong at top with 85mm dia 3mm thick GI base plate | 25mm dia, 1800mm | 3 | nos
Cable Tray | 150 mm GI perforated cable tray with coupler plate and accessories | 150 mm | 45 | m
| 300 mm GI perforated cable tray with coupler plate and accessories | 300 mm | 120 | m
Conduit | 50mm dia double corrugated HDPE conduit | 50mm | 416 | m
| 100mm dia double corrugated HDPE conduit | 100mm | 260 | m
Siren | Hand operated siren range 500 m | 500 m | 1 | No
| Electrical siren range 500 m, Voltage: 230VAC | 500 m | 1 | No
MEDB | Panel Constructional details: Panel suitable for 415VAC,50Hz, 3Wire AC supply system fabricated in compartmentalised with CRCA sheet steel, thickness 2mm, treated with 7tank procees. Painting shall be powder coated and oven dried. Panel shall have withstand capacity of 25KA for 1 sec. Ingress protection shall be IP-42. It will have suitable MS base channel with powder coated. panel shall be fabricated in transportable section. The panel shall have a common CU earthbar of size 25mmX5mm at the rear with 2 nos earth stud. Stud type power terminal suitable for rated load to be considered. Connection to be done with PVC insulated CU conductor cable of required current rating. Paint shall be finalised during detail engineering.
MEDB | Dual Incomer with Bus-coupler: 4 Pole 100A microprocessor based O/C, S/C & E/F releases with extended door handle. SINGLE POINT EMERGENCY STOP SHALL BE PROVIDED. Out Going feeders: a) 8 nos 32A, 4 Pole microprocessor based MCCB power feeder with On,Off, Trip indication lamps. b) 4 nos 63A, 4 Pole microprocessor based MCCB power feeder with On,Off, Trip indication lamps. c) 1 no 16A, 4 Pole microprocessor based MCCB power feeder with On,Off, Trip indication lamps.
MEDB | 32A TPN+E CU Bus (10KA) shall be considered. d) 6A, DP MCB 2 Nos and 16A, DP MCB 6 Nos shall be considered in a separate feeder. |  | 1 | No
ILDB | NON FLAMEPROOF TYPE, |  | 1 | NO
OLDB | NON FLAMEPROOF TYPE, |  | 1 | NO
UPS -ACDB | NON FLAMEPROOF TYPE, |  | 1 | NO
Solar Panel | NON FLAMEPROOF TYPE, |  | 1 | NO
UPS & UPS Panel (2 X 6 KVA) | NON FLAMEPROOF TYPE, |  | 1 | NO
Cable | 4CX16Sqmm, AL conductor XLPE Insulated, FRLS, Voltage grade 1100V | 4CX16Sqmm | 136 | m
| 4CX4Sqmm, CU conductor XLPE Insulated, FRLS, Voltage grade 1100V | 4CX4Sqmm | 136 | m
Cable Gland | Flameproof cable gland for 4CX16Sqmm | 4CX16Sqmm | 10 | Nos
| Flameproof cable gland for 4CX4Sqmm | 4CX4Sqmm | 58 | Nos
Cable Lugs | Ring type AL Lugs 4CX16Sqmm power cable | 4CX16Sqmm | 40 | Nos
| Ring type CU Lugs 4CX4Sqmm power cable | 4CX4Sqmm | 232 | Nos
Electrical building internal lighting wiring | Primary wiring 12M | 12M | 10 | Point
| Secondary wiring 4M | 4M | 10 | Point
Electrical building internal lighting wiring | Primary wiring 12M | 12M | 22.1 | Point
| Secondary wiring 4M | 12M | 22.1 | Point
SOCKET | 6PIN 15/16 & 5/6 AMPS MODULAR SOCKET |  | 4 | Nos
| 15/16 Amp modular switch board |  | 5 | Nos
LED lamp | Fixture 2X40W wall/ceiling mount or equivalent light fixture |  | 5 | No
| FLP Fixture 2X40W wall/ceiling mount or equivalent light fixture |  | 1 | No
| Fixture 1X20W wall/ceiling mount or equivalent light fixture |  | 2 | No
Ceiling Fan | Ceiling fan of 1200mm | 1200mm | 2 | No
Exhaust fan | 450mm dia FLP exhaust fan with louvers | 450mm dia | 2 | No
| 300mm dia FLP exhaust fan with louvers | 300mm dia | 4 | No
Conduit | 25mm dia PVC conduit | 25mm dia | 100 | m
GENSET | 15KVA/12KW 3 PHASE MAHINDRA CPCB II compliant Gas Genset, Prime rated, radiator cooled, 15KVA equivalent electric alternator, microprocessor based controller, silencer, anti-vibration mountings, exhaust flexible connector, batteries with cable, acoustic enclosure and pressure converter valve. |  | 1 | No
Outdoor Light Fittings | FLP 110W LED for mounting on 7m hexagonal light pole suitable for hazardous Zone-2 area |  | 22 | Nos
Outdoor Light Fittings | 7 meter height hexagonal/octagonal street pole with suitable size of JB |  | 22 | Nos
Outdoor Light Fittings | Wiring 3CX2.5 Sqmm XLPE Insulated Cable |  | 220 | m
Site Misc materials | vitreous enamel caution boards suitable for 440 V as per IS 255 including fixing on the wall with all the required hardware etc. complete in English / Hindi/ Local Language. |  | 10 | Nos
Site Misc materials | Single Line Diagram complete with laminated A2 size colour print. |  | 2 | Set
Site Misc materials | shock treatment chart framed in good quality glass in English / Hindi / Local Language). |  | 10 | Nos
Site Misc materials | Insulating mat (2 or 2.5mm thick X 0.9 or 1Mtr w , 11 KV) as per IS15652/IEC61111 |  | 10 | Nos
Site Misc materials | Pairs of Rubber hand gloves IS Mark |  | 10 | Nos
Site Misc materials | Fiirst aid box with Snake serum |  | 2 | Nos