## Sheet1
section_context_for_this_product_block | full_product_description | core_product_name | size | feature_or_specifications | acronymed_core_product_name | quantity | unit | sheet_name
| Instrument earthing with CU earth plate ¦ Earthing with CU earth plate 600mmX600mmX3mm thick, GI Pipe of 19mm dia, 2 meter length including accessories as required as per IS-3043. Following points to be considered with earth pit. | earthing plate | plate size: 600mmX600mmX3mm, pipe diameter: 19mm, pipe length: 2 meter | material: copper, pipe material: gi(galvanized iron), standard: indian standard 3043 |  | 6 | nos | Sheet1
| Instrument earthing with CU earth plate ¦ a. Masonary enclosure with cover plate having locking arrangement. | earthing plate |  | feature: masonary enclosure with cover plate having locking arrangement |  |  |  | Sheet1
| Instrument earthing with CU earth plate ¦ b. watering pipe | earthing plate |  | feature: watering pipe |  |  |  | Sheet1
| Instrument earthing with CU earth plate ¦ c. charcole, salt (approximately 15kg charcoal and 15kg salt for each pit ) Refer attached drawing for further consideration. | earthing plate |  | feature: charcole, salt (approximately 15kg charcoal and 15kg salt for each pit) |  |  |  | Sheet1
| Earthing with GI pipe ¦ 25mmX3mm CU strip for instrument panel earthing. | earthing strip | strip size: 25mmX3mm | material: copper, application: instrument panel earthing |  | 150 | m | Sheet1
| Earthing with GI pipe ¦ 16 ways earthing copper plate with accessories | earthing plate |  | ways: 16, material: copper, with accessories |  | 4 | nos | Sheet1
| Earthing with GI pipe ¦ Earthing with GI earth pipe 3 meter long, 100 mm diameter including accessories as required as per IS-3043. Following points to be considered with earth pit. a. Masonary enclosure with cover plate having locking arrangement. b. charcole, salt (approximately 15kg charcoal and 15kg salt for each pit) Refer attached drawing for further consideration. | earthing pipe | pipe length: 3 meter, pipe diameter: 100 mm | material: gi(galvanized iron), standard: indian standard 3043, feature: masonary enclosure with cover plate having locking arrangement, feature: charcole, salt (approximately 15kg charcoal and 15kg salt for each pit) |  | 12 | nos | Sheet1
| Earthing with GI pipe ¦ 50mmX6mm GI strip for main grid, panel earthing etc. | earthing strip | strip size: 50mmX6mm | material: gi(galvanized iron), application: main grid, panel earthing etc. |  | 250 | m | Sheet1
| Earthing with GI pipe ¦ 25mmX3mm GI strip for main grid, panel earthing etc. | earthing strip | strip size: 25mmX3mm | material: gi(galvanized iron), application: main grid, panel earthing etc. |  | 525 | m | Sheet1
| Earthing with GI pipe ¦ 10Sqmm CU earthing wire. | earthing wire | wire size: 10Sqmm | material: copper |  | 300 | m | Sheet1
| Earthing with GI pipe ¦ Conductor Material: Plain annealed high conductivity Flexible copper conductor as per Class 5 of IS 8130/84 latest. | earthing wire |  | conductor material: plain annealed high conductivity flexible copper, standard: indian standard 8130/84 class 5 |  |  |  | Sheet1
| Earthing with GI pipe ¦ Insulation material: PVC Type 'D' with FR-LSH Propertes. | earthing wire |  | insulation material: pvc type 'd', feature: fr-lsh properties |  |  |  | Sheet1
| Earthing with GI pipe ¦ Rated voltage: 1100 V | earthing wire |  | rated voltage: 1100 v |  |  |  | Sheet1
| Earthing with GI pipe ¦ FRLS properties: | earthing wire |  | feature: frls properties |  |  |  | Sheet1
| Earthing with GI pipe ¦ Oxygen Index Min. 29% as per ASTM D- 2863 | earthing wire |  | oxygen index: min. 29%, standard: astm d-2863 |  |  |  | Sheet1
| Earthing with GI pipe ¦ Temperature Index Min. 250 Deg.C as per ASTM D- 2863 | earthing wire |  | temperature index: min. 250 deg.c, standard: astm d-2863 |  |  |  | Sheet1
| Earthing with GI pipe ¦ Smoke Density Rating Max. 60% as per ASTM D- 2843 | earthing wire |  | smoke density rating: max. 60%, standard: astm d-2843 |  |  |  | Sheet1
| Earthing with GI pipe ¦ Acid Gas Generation Max. 20% as per IEC- 754- 1 | earthing wire |  | acid gas generation: max. 20%, standard: iec-754-1 |  |  |  | Sheet1
| Earthing with GI pipe ¦ Max. conductor temp. under normal operating conditions 70deg C | earthing wire |  | max. conductor temp. under normal operating conditions: 70deg c |  |  |  | Sheet1
| Earthing with GI pipe ¦ 16 ways earting GI plate with accessories | earthing plate |  | ways: 16, material: gi(galvanized iron), with accessories |  | 12 | nos | Sheet1
| Earthing with GI pipe ¦ 50Sqmm, 30m length CU earthing wire with clip reel & accessories | earthing wire | wire size: 50Sqmm, wire length: 30m | material: copper, with clip reel & accessories |  | 1 | nos | Sheet1
| Lighting arrester ¦ 25mm dia, 1800mm long GI tube having single prong at top with 85mm dia 3mm thick GI base plate | lighting arrester | tube diameter: 25mm, tube length: 1800mm, base plate diameter: 85mm, base plate thickness: 3mm | tube material: gi(galvanized iron), base plate material: gi(galvanized iron), feature: single prong at top |  | 3 | nos | Sheet1
| Cable Tray ¦ 150 mm GI perforated cable tray with coupler plate and accessories | cable tray | tray width: 150 mm | material: gi(galvanized iron), type: perforated, with coupler plate and accessories |  | 45 | m | Sheet1
| nan ¦ 300 mm GI perforated cable tray with coupler plate and accessories | cable tray | tray width: 300 mm | material: gi(galvanized iron), type: perforated, with coupler plate and accessories |  | 120 | m | Sheet1
| Conduit ¦ 50mm dia double corrugated HDPE conduit | hdpe conduit | conduit diameter: 50mm | type: double corrugated, material: hdpe(high density polyethylene) |  | 416 | m | Sheet1
| nan ¦ 100mm dia double corrugated HDPE conduit | hdpe conduit | conduit diameter: 100mm | type: double corrugated, material: hdpe(high density polyethylene) |  | 260 | m | Sheet1
| Siren ¦ Hand operated siren range 500 m | siren | range: 500 m | type: hand operated |  | 1 | No | Sheet1
| nan ¦ Electrical siren range 500 m, Voltage: 230VAC | siren | range: 500 m | type: electrical, voltage: 230VAC |  | 1 | No | Sheet1
| MEDB ¦ Panel Constructional details: Panel suitable for 415VAC,50Hz, 3Wire AC supply system fabricated in compartmentalised with CRCA sheet steel, thickness 2mm, treated with 7tank procees. Painting shall be powder coated and oven dried. Panel shall have withstand capacity of 25KA for 1 sec. Ingress protection shall be IP-42. It will have suitable MS base channel with powder coated. panel shall be fabricated in transportable section. The panel shall have a common CU earthbar of size 25mmX5mm at the rear with 2 nos earth stud. Stud type power terminal suitable for rated load to be considered. Connection to be done with PVC insulated CU conductor cable of required current rating. Paint shall be finalised during detail engineering. | panel | earthbar size: 25mmX5mm, sheet thickness: 2mm | supply system: 415VAC, 50Hz, 3Wire AC, construction: compartmentalised, material: crca sheet steel, treatment: 7tank process, painting: powder coated and oven dried, withstand capacity: 25KA for 1 sec, ingress protection: IP-42, base channel: ms(mild steel) powder coated, fabrication: transportable section, earthbar material: copper, earth stud: 2 nos, terminal: stud type power terminal, connection: pvc insulated copper conductor cable, paint: to be finalised during detail engineering |  |  |  | Sheet1
| MEDB ¦ Dual Incomer with Bus-coupler: 4 Pole 100A microprocessor based O/C, S/C & E/F releases with extended door handle. SINGLE POINT EMERGENCY STOP SHALL BE PROVIDED. Out Going feeders: a) 8 nos 32A, 4 Pole microprocessor based MCCB power feeder with On,Off, Trip indication lamps. b) 4 nos 63A, 4 Pole microprocessor based MCCB power feeder with On,Off, Trip indication lamps. c) 1 no 16A, 4 Pole microprocessor based MCCB power feeder with On,Off, Trip indication lamps. | dual incomer with bus-coupler |  | pole: 4, current: 100A, control: microprocessor based O/C(over current), S/C(short circuit) & E/F(earth fault) releases, feature: extended door handle, feature: single point emergency stop, outgoing feeders: 8 nos 32A 4 Pole microprocessor based MCCB power feeder with On,Off, Trip indication lamps; 4 nos 63A 4 Pole microprocessor based MCCB power feeder with On,Off, Trip indication lamps; 1 no 16A 4 Pole microprocessor based MCCB power feeder with On,Off, Trip indication lamps |  |  |  | Sheet1
| MEDB ¦ 32A TPN+E CU Bus (10KA) shall be considered. d) 6A, DP MCB 2 Nos and 16A, DP MCB 6 Nos shall be considered in a separate feeder. | tpn+e cu bus | current: 32A | feature: 10KA, outgoing feeders: 6A DP MCB 2 Nos, 16A DP MCB 6 Nos in separate feeder |  | 1 | No | Sheet1
| ILDB ¦ NON FLAMEPROOF TYPE, | ildb |  | feature: non flameproof type |  | 1 | NO | Sheet1
| OLDB ¦ NON FLAMEPROOF TYPE, | oldb |  | feature: non flameproof type |  | 1 | NO | Sheet1
| UPS -ACDB ¦ NON FLAMEPROOF TYPE, | ups -acdb |  | feature: non flameproof type |  | 1 | NO | Sheet1
| Solar Panel ¦ NON FLAMEPROOF TYPE, | solar panel |  | feature: non flameproof type |  | 1 | NO | Sheet1
| UPS & UPS Panel (2 X 6 KVA) ¦ NON FLAMEPROOF TYPE, | ups & ups panel | capacity: 2 X 6 KVA | feature: non flameproof type |  | 1 | NO | Sheet1
| Cable ¦ 4CX16Sqmm, AL conductor XLPE Insulated, FRLS, Voltage grade 1100V | cable | size: 4CX16Sqmm | conductor: aluminium, insulation: XLPE, feature: FRLS, voltage grade: 1100V |  | 136 | m | Sheet1
| nan ¦ 4CX4Sqmm, CU conductor XLPE Insulated, FRLS, Voltage grade 1100V | cable | size: 4CX4Sqmm | conductor: copper, insulation: XLPE, feature: FRLS, voltage grade: 1100V |  | 136 | m | Sheet1
| Cable Gland ¦ Flameproof cable gland for 4CX16Sqmm | cable gland | size: 4CX16Sqmm | feature: flameproof |  | 10 | Nos | Sheet1
| nan ¦ Flameproof cable gland for 4CX4Sqmm | cable gland | size: 4CX4Sqmm | feature: flameproof |  | 58 | Nos | Sheet1
| Cable Lugs ¦ Ring type AL Lugs 4CX16Sqmm power cable | cable lugs | size: 4CX16Sqmm | type: ring, material: aluminium, application: power cable |  | 40 | Nos | Sheet1
| nan ¦ Ring type CU Lugs 4CX4Sqmm power cable | cable lugs | size: 4CX4Sqmm | type: ring, material: copper, application: power cable |  | 232 | Nos | Sheet1
| Electrical building internal lighting wiring ¦ Primary wiring 12M | electrical building internal lighting wiring | length: 12M | type: primary wiring |  | 10 | Point | Sheet1
| nan ¦ Secondary wiring 4M | electrical building internal lighting wiring | length: 4M | type: secondary wiring |  | 10 | Point | Sheet1
| Electrical building internal lighting wiring ¦ Primary wiring 12M | electrical building internal lighting wiring | length: 12M | type: primary wiring |  | 22.1 | Point | Sheet1
| nan ¦ Secondary wiring 4M | electrical building internal lighting wiring | length: 12M | type: secondary wiring |  | 22.1 | Point | Sheet1
| SOCKET ¦ 6PIN 15/16 & 5/6 AMPS MODULAR SOCKET | modular socket |  | pin: 6, current: 15/16 & 5/6 amps |  | 4 | Nos | Sheet1
| nan ¦ 15/16 Amp modular switch board | modular switch board |  | current: 15/16 amp |  | 5 | Nos | Sheet1
| LED lamp ¦ Fixture 2X40W wall/ceiling mount or equivalent light fixture | led lamp |  | fixture: 2X40W wall/ceiling mount or equivalent light fixture |  | 5 | No | Sheet1
| nan ¦ FLP Fixture 2X40W wall/ceiling mount or equivalent light fixture | flp fixture |  | fixture: 2X40W wall/ceiling mount or equivalent light fixture |  | 1 | No | Sheet1
| nan ¦ Fixture 1X20W wall/ceiling mount or equivalent light fixture | fixture |  | fixture: 1X20W wall/ceiling mount or equivalent light fixture |  | 2 | No | Sheet1
| Ceiling Fan ¦ Ceiling fan of 1200mm | ceiling fan | diameter: 1200mm |  |  | 2 | No | Sheet1
| Exhaust fan ¦ 450mm dia FLP exhaust fan with louvers | flp exhaust fan | diameter: 450mm | feature: with louvers |  | 2 | No | Sheet1
| nan ¦ 300mm dia FLP exhaust fan with louvers | flp exhaust fan | diameter: 300mm | feature: with louvers |  | 4 | No | Sheet1
| Conduit ¦ 25mm dia PVC conduit | pvc conduit | diameter: 25mm |  |  | 100 | m | Sheet1
| GENSET ¦ 15KVA/12KW 3 PHASE MAHINDRA CPCB II compliant Gas Genset, Prime rated, radiator cooled, 15KVA equivalent electric alternator, microprocessor based controller, silencer, anti-vibration mountings, exhaust flexible connector, batteries with cable, acoustic enclosure and pressure converter valve. | gas genset | capacity: 15KVA/12KW, phase: 3 | manufacturer: mahindra, compliance: CPCB II, rating: prime rated, cooling: radiator cooled, alternator: 15KVA equivalent electric, controller: microprocessor based, accessories: silencer, anti-vibration mountings, exhaust flexible connector, batteries with cable, acoustic enclosure, pressure converter valve |  | 1 | No | Sheet1
| Outdoor Light Fittings ¦ FLP 110W LED for mounting on 7m hexagonal light pole suitable for hazardous Zone-2 area | flp led light fitting | power: 110W, mounting height: 7m | feature: suitable for hazardous Zone-2 area, mounting: hexagonal light pole |  | 22 | Nos | Sheet1
| Outdoor Light Fittings ¦ 7 meter height hexagonal/octagonal street pole with suitable size of JB | street pole | height: 7 meter | shape: hexagonal/octagonal, accessory: suitable size of JB |  | 22 | Nos | Sheet1
| Outdoor Light Fittings ¦ Wiring 3CX2.5 Sqmm XLPE Insulated Cable | wiring cable | size: 3CX2.5 Sqmm | insulation: XLPE |  | 220 | m | Sheet1
Site Misc materials | Site Misc materials ¦ Single Line Diagram complete with laminated A2 size colour print. | single line diagram | print size: a2 | finish: laminated, color: colour print |  | 2 | Set | Sheet1
Site Misc materials | Site Misc materials ¦ shock treatment chart framed in good quality glass in English / Hindi / Local Language). | shock treatment chart |  | frame: good quality glass, language: english/hindi/local language |  | 10 | Nos | Sheet1
Site Misc materials | Site Misc materials ¦ Insulating mat (2 or 2.5mm thick X 0.9 or 1Mtr w , 11 KV) as per IS15652/IEC61111 | insulating mat | thickness: 2 or 2.5mm, width: 0.9 or 1mtr | voltage: 11 kv, standard: is15652(indian standard 15652), standard: iec61111(international electrotechnical commission 61111) |  | 10 | Nos | Sheet1
Site Misc materials | Site Misc materials ¦ Pairs of Rubber hand gloves IS Mark | rubber hand gloves |  | certification: is mark(indian standard mark) |  | 10 | Nos | Sheet1
Site Misc materials | Site Misc materials ¦ Fiirst aid box with Snake serum | first aid box |  | accessory: snake serum |  | 2 | Nos | Sheet1